## Calculator
This is a calculator to help you calculate the Flow Rate and Steam Consumption per hour with SuperKlean 8000 Series Steam & Cold Water Mixing Unit. Please use the left button if you are using Imperial/British Unit. Please use the right buttion if you are using Metric Unit.
Trouble running the calculator? Follow the instructions in this Microsoft Support article. Please make sure to close and reopen this file after completing the steps listed under "Unblock a single file"
The Flow Rate and Steam Consumption Calculator is only available on the desktop version of Microsoft Excel
Imperial Unit
Metric Unit

## Sheet2 (hidden)
Imperial Unit |  | Metric Unit
Input Data |  | Input Data
Cold Water Temp (°F) | 40 | Cold Water Temp (°C) | 10
Required Hot Water Temp (°F) | 160 | Required Hot Water Temp (°C) | 80
Cold Water Pressure (psi) | 50 | Cold Water Pressure (bar) | 5
Steam Pressure (psi) | 70 | Steam Pressure (bar) | 6
Result |  | Result
Hot Water Flow Rate (gal/min) | 7.2222 | Hot Water Flow Rate (l/min) | 30.4671
Steam Consumption (pound/h) | 480.9611 | Steam Consumption (kg/h) | 259.6521

## Worksheet (hidden)
Temperature Rise °F | 120 |  |  | Temperature Rise °C | 70
|  |  |  | Temperature Rise °F | 126
Steam Property | 2095.9 |  |  | Steam Property | 2064.92
Bar/psi constant | 14.5038 |  |  | Gallon/liter constant | 3.7854
| Cold psi | Steam psi | Termperature Rise °F |  | Cold bar | Steam bar | Termperature Rise °F
| 50 | 70 | 120 |  | 5 | 6 | 126
Flow Rate | 7.2222 |  |  | Flow Rate | 8.0486
| Flow Rate |  |  |  | Flow Rate
TR 0 | 13.4 |  |  | TR 0 | 13.8
TR 55 | 11.7056 |  |  | TR 55 | 13.25
TR 100 | 7.9333 |  |  | TR 100 | 9.2
TR 135 | 6.6889 |  |  | TR 135 | 7.65

## Data Sheet_b (hidden)
Cold | Steam | TR | Flow | Cold | Steam | TR | Flow
30 | 45 | 0 | 13.1 | 2 | 3 | 55 | 10
30 | 46 | 0 | 13.1 | 2 | 3.1 | 55 | 10.09
30 | 47 | 0 | 13.1 | 2 | 3.2 | 55 | 10.18
30 | 48 | 0 | 13.1 | 2 | 3.3 | 55 | 10.27
30 | 49 | 0 | 13.1 | 2 | 3.4 | 55 | 10.36
30 | 50 | 0 | 13.1 | 2 | 3.5 | 55 | 10.45
30 | 51 | 0 | 13.1 | 2 | 3.6 | 55 | 10.54
30 | 52 | 0 | 13.1 | 2 | 3.7 | 55 | 10.63
30 | 53 | 0 | 13.1 | 2 | 3.8 | 55 | 10.72
30 | 54 | 0 | 13.1 | 2 | 3.9 | 55 | 10.81
30 | 55 | 0 | 13.1 | 2 | 4 | 55 | 10.9
30 | 56 | 0 | 13.1 | 2 | 4.1 | 55 | 10.99
30 | 57 | 0 | 13.1 | 2 | 4.2 | 55 | 11.08
30 | 58 | 0 | 13.1 | 2 | 4.3 | 55 | 11.17
30 | 59 | 0 | 13.1 | 2 | 4.4 | 55 | 11.26
30 | 60 | 0 | 13.1 | 2 | 4.5 | 55 | 11.35
30 | 61 | 0 | 13.1 | 2 | 4.6 | 55 | 11.44
30 | 62 | 0 | 13.1 | 2 | 4.7 | 55 | 11.53
30 | 63 | 0 | 13.1 | 2 | 4.8 | 55 | 11.62
30 | 64 | 0 | 13.1 | 2 | 4.9 | 55 | 11.71
30 | 65 | 0 | 13.1 | 2 | 5 | 55 | 11.8
30 | 66 | 0 | 13.1 | 2 | 5.1 | 55 | 11.86
30 | 67 | 0 | 13.1 | 2 | 5.2 | 55 | 11.92
30 | 68 | 0 | 13.1 | 2 | 5.3 | 55 | 11.98
30 | 69 | 0 | 13.1 | 2 | 5.4 | 55 | 12.04
30 | 70 | 0 | 13.1 | 2 | 5.5 | 55 | 12.1
30 | 71 | 0 | 13.1 | 2 | 5.6 | 55 | 12.16
30 | 72 | 0 | 13.1 | 2 | 5.7 | 55 | 12.22
30 | 73 | 0 | 13.1 | 2 | 5.8 | 55 | 12.28
30 | 74 | 0 | 13.1 | 2 | 5.9 | 55 | 12.34
30 | 75 | 0 | 13.1 | 2 | 6 | 55 | 12.4
30 | 76 | 0 | 13.1 | 2 | 6.1 | 55 | 12.46
30 | 77 | 0 | 13.1 | 2 | 6.2 | 55 | 12.52
30 | 78 | 0 | 13.1 | 2 | 6.3 | 55 | 12.58
30 | 79 | 0 | 13.1 | 2 | 6.4 | 55 | 12.64
30 | 80 | 0 | 13.1 | 2 | 6.5 | 55 | 12.7
30 | 81 | 0 | 13.1 | 2 | 6.6 | 55 | 12.76
30 | 82 | 0 | 13.1 | 2 | 6.7 | 55 | 12.82
30 | 83 | 0 | 13.1 | 2 | 6.8 | 55 | 12.88
30 | 84 | 0 | 13.1 | 2 | 6.9 | 55 | 12.94
30 | 85 | 0 | 13.1 | 2 | 7 | 55 | 13
30 | 86 | 0 | 13.1 | 2 | 7.1 | 55 | 13.055
30 | 87 | 0 | 13.1 | 2 | 7.2 | 55 | 13.11
30 | 88 | 0 | 13.1 | 2 | 7.3 | 55 | 13.165
30 | 89 | 0 | 13.1 | 2 | 7.4 | 55 | 13.22
30 | 90 | 0 | 13.1 | 2 | 7.5 | 55 | 13.275
30 | 91 | 0 | 13.1 | 2 | 7.6 | 55 | 13.33
30 | 92 | 0 | 13.1 | 2 | 7.7 | 55 | 13.385
30 | 93 | 0 | 13.1 | 2 | 7.8 | 55 | 13.44
30 | 94 | 0 | 13.1 | 2 | 7.9 | 55 | 13.495
30 | 95 | 0 | 13.1 | 2 | 8 | 55 | 13.55
30 | 96 | 0 | 13.1 | 2 | 8.1 | 55 | 13.605
30 | 97 | 0 | 13.1 | 2 | 8.2 | 55 | 13.66
30 | 98 | 0 | 13.1 | 2 | 8.3 | 55 | 13.715
30 | 99 | 0 | 13.1 | 2 | 8.4 | 55 | 13.77
30 | 100 | 0 | 13.1 | 2 | 8.5 | 55 | 13.825
30 | 101 | 0 | 13.1 | 2 | 8.6 | 55 | 13.88
30 | 102 | 0 | 13.1 | 2 | 8.7 | 55 | 13.935
30 | 103 | 0 | 13.1 | 2 | 8.8 | 55 | 13.99
30 | 104 | 0 | 13.1 | 2 | 8.9 | 55 | 14.045
30 | 105 | 0 | 13.1 | 2 | 9 | 55 | 14.1
30 | 106 | 0 | 13.1 | 2 | 9.1 | 55 | 14.21
30 | 107 | 0 | 13.1 | 2 | 9.2 | 55 | 14.32
30 | 108 | 0 | 13.1 | 2 | 9.3 | 55 | 14.43
30 | 109 | 0 | 13.1 | 2 | 9.4 | 55 | 14.54
30 | 110 | 0 | 13.1 | 2 | 9.5 | 55 | 14.65
30 | 111 | 0 | 13.1 | 2 | 9.6 | 55 | 14.76
30 | 112 | 0 | 13.1 | 2 | 9.7 | 55 | 14.87
30 | 113 | 0 | 13.1 | 2 | 9.8 | 55 | 14.98
30 | 114 | 0 | 13.1 | 2 | 9.9 | 55 | 15.09
30 | 115 | 0 | 13.1 | 2 | 10 | 55 | 15.2
30 | 116 | 0 | 13.1 | 2.1 | 3 | 55 | 10
30 | 117 | 0 | 13.1 | 2.1 | 3.1 | 55 | 10.091
30 | 118 | 0 | 13.1 | 2.1 | 3.2 | 55 | 10.182
30 | 119 | 0 | 13.1 | 2.1 | 3.3 | 55 | 10.273
30 | 120 | 0 | 13.1 | 2.1 | 3.4 | 55 | 10.364
30 | 121 | 0 | 13.1 | 2.1 | 3.5 | 55 | 10.455
30 | 122 | 0 | 13.1 | 2.1 | 3.6 | 55 | 10.546
30 | 123 | 0 | 13.1 | 2.1 | 3.7 | 55 | 10.637
30 | 124 | 0 | 13.1 | 2.1 | 3.8 | 55 | 10.728
30 | 125 | 0 | 13.1 | 2.1 | 3.9 | 55 | 10.819
30 | 126 | 0 | 13.1 | 2.1 | 4 | 55 | 10.91
30 | 127 | 0 | 13.1 | 2.1 | 4.1 | 55 | 11.001
30 | 128 | 0 | 13.1 | 2.1 | 4.2 | 55 | 11.092
30 | 129 | 0 | 13.1 | 2.1 | 4.3 | 55 | 11.183
30 | 130 | 0 | 13.1 | 2.1 | 4.4 | 55 | 11.274
30 | 131 | 0 | 13.1 | 2.1 | 4.5 | 55 | 11.365
30 | 132 | 0 | 13.1 | 2.1 | 4.6 | 55 | 11.456
30 | 133 | 0 | 13.1 | 2.1 | 4.7 | 55 | 11.547
30 | 134 | 0 | 13.1 | 2.1 | 4.8 | 55 | 11.638
30 | 135 | 0 | 13.1 | 2.1 | 4.9 | 55 | 11.729
30 | 136 | 0 | 13.1 | 2.1 | 5 | 55 | 11.82
30 | 137 | 0 | 13.1 | 2.1 | 5.1 | 55 | 11.88
30 | 138 | 0 | 13.1 | 2.1 | 5.2 | 55 | 11.94
30 | 139 | 0 | 13.1 | 2.1 | 5.3 | 55 | 12
30 | 140 | 0 | 13.1 | 2.1 | 5.4 | 55 | 12.06
30 | 141 | 0 | 13.1 | 2.1 | 5.5 | 55 | 12.12
30 | 142 | 0 | 13.1 | 2.1 | 5.6 | 55 | 12.18
30 | 143 | 0 | 13.1 | 2.1 | 5.7 | 55 | 12.24
30 | 144 | 0 | 13.1 | 2.1 | 5.8 | 55 | 12.3
30 | 145 | 0 | 13.1 | 2.1 | 5.9 | 55 | 12.36
30 | 146 | 0 | 13.1 | 2.1 | 6 | 55 | 12.42
30 | 147 | 0 | 13.1 | 2.1 | 6.1 | 55 | 12.48
30 | 148 | 0 | 13.1 | 2.1 | 6.2 | 55 | 12.54
30 | 149 | 0 | 13.1 | 2.1 | 6.3 | 55 | 12.6
30 | 150 | 0 | 13.1 | 2.1 | 6.4 | 55 | 12.66
31 | 45 | 0 | 13.1133 | 2.1 | 6.5 | 55 | 12.72
31 | 46 | 0 | 13.1133 | 2.1 | 6.6 | 55 | 12.78
31 | 47 | 0 | 13.1133 | 2.1 | 6.7 | 55 | 12.84
31 | 48 | 0 | 13.1133 | 2.1 | 6.8 | 55 | 12.9
31 | 49 | 0 | 13.1133 | 2.1 | 6.9 | 55 | 12.96
31 | 50 | 0 | 13.1133 | 2.1 | 7 | 55 | 13.02
31 | 51 | 0 | 13.1133 | 2.1 | 7.1 | 55 | 13.0745
31 | 52 | 0 | 13.1133 | 2.1 | 7.2 | 55 | 13.129
31 | 53 | 0 | 13.1133 | 2.1 | 7.3 | 55 | 13.1835
31 | 54 | 0 | 13.1133 | 2.1 | 7.4 | 55 | 13.238
31 | 55 | 0 | 13.1133 | 2.1 | 7.5 | 55 | 13.2925
31 | 56 | 0 | 13.1133 | 2.1 | 7.6 | 55 | 13.347
31 | 57 | 0 | 13.1133 | 2.1 | 7.7 | 55 | 13.4015
31 | 58 | 0 | 13.1133 | 2.1 | 7.8 | 55 | 13.456
31 | 59 | 0 | 13.1133 | 2.1 | 7.9 | 55 | 13.5105
31 | 60 | 0 | 13.1133 | 2.1 | 8 | 55 | 13.565
31 | 61 | 0 | 13.1133 | 2.1 | 8.1 | 55 | 13.6195
31 | 62 | 0 | 13.1133 | 2.1 | 8.2 | 55 | 13.674
31 | 63 | 0 | 13.1133 | 2.1 | 8.3 | 55 | 13.7285
31 | 64 | 0 | 13.1133 | 2.1 | 8.4 | 55 | 13.783
31 | 65 | 0 | 13.1133 | 2.1 | 8.5 | 55 | 13.8375
31 | 66 | 0 | 13.1133 | 2.1 | 8.6 | 55 | 13.892
31 | 67 | 0 | 13.1133 | 2.1 | 8.7 | 55 | 13.9465
31 | 68 | 0 | 13.1133 | 2.1 | 8.8 | 55 | 14.001
31 | 69 | 0 | 13.1133 | 2.1 | 8.9 | 55 | 14.0555
31 | 70 | 0 | 13.1133 | 2.1 | 9 | 55 | 14.11
31 | 71 | 0 | 13.1133 | 2.1 | 9.1 | 55 | 14.22
31 | 72 | 0 | 13.1133 | 2.1 | 9.2 | 55 | 14.33
31 | 73 | 0 | 13.1133 | 2.1 | 9.3 | 55 | 14.44
31 | 74 | 0 | 13.1133 | 2.1 | 9.4 | 55 | 14.55
31 | 75 | 0 | 13.1133 | 2.1 | 9.5 | 55 | 14.66
31 | 76 | 0 | 13.1133 | 2.1 | 9.6 | 55 | 14.77
31 | 77 | 0 | 13.1133 | 2.1 | 9.7 | 55 | 14.88
31 | 78 | 0 | 13.1133 | 2.1 | 9.8 | 55 | 14.99
31 | 79 | 0 | 13.1133 | 2.1 | 9.9 | 55 | 15.1
31 | 80 | 0 | 13.1133 | 2.1 | 10 | 55 | 15.21
31 | 81 | 0 | 13.1133 | 2.2 | 3 | 55 | 10
31 | 82 | 0 | 13.1133 | 2.2 | 3.1 | 55 | 10.092
31 | 83 | 0 | 13.1133 | 2.2 | 3.2 | 55 | 10.184
31 | 84 | 0 | 13.1133 | 2.2 | 3.3 | 55 | 10.276
31 | 85 | 0 | 13.1133 | 2.2 | 3.4 | 55 | 10.368
31 | 86 | 0 | 13.1133 | 2.2 | 3.5 | 55 | 10.46
31 | 87 | 0 | 13.1133 | 2.2 | 3.6 | 55 | 10.552
31 | 88 | 0 | 13.1133 | 2.2 | 3.7 | 55 | 10.644
31 | 89 | 0 | 13.1133 | 2.2 | 3.8 | 55 | 10.736
31 | 90 | 0 | 13.1133 | 2.2 | 3.9 | 55 | 10.828
31 | 91 | 0 | 13.1133 | 2.2 | 4 | 55 | 10.92
31 | 92 | 0 | 13.1133 | 2.2 | 4.1 | 55 | 11.012
31 | 93 | 0 | 13.1133 | 2.2 | 4.2 | 55 | 11.104
31 | 94 | 0 | 13.1133 | 2.2 | 4.3 | 55 | 11.196
31 | 95 | 0 | 13.1133 | 2.2 | 4.4 | 55 | 11.288
31 | 96 | 0 | 13.1133 | 2.2 | 4.5 | 55 | 11.38
31 | 97 | 0 | 13.1133 | 2.2 | 4.6 | 55 | 11.472
31 | 98 | 0 | 13.1133 | 2.2 | 4.7 | 55 | 11.564
31 | 99 | 0 | 13.1133 | 2.2 | 4.8 | 55 | 11.656
31 | 100 | 0 | 13.1133 | 2.2 | 4.9 | 55 | 11.748
31 | 101 | 0 | 13.1133 | 2.2 | 5 | 55 | 11.84
31 | 102 | 0 | 13.1133 | 2.2 | 5.1 | 55 | 11.9
31 | 103 | 0 | 13.1133 | 2.2 | 5.2 | 55 | 11.96
31 | 104 | 0 | 13.1133 | 2.2 | 5.3 | 55 | 12.02
31 | 105 | 0 | 13.1133 | 2.2 | 5.4 | 55 | 12.08
31 | 106 | 0 | 13.1133 | 2.2 | 5.5 | 55 | 12.14
31 | 107 | 0 | 13.1133 | 2.2 | 5.6 | 55 | 12.2
31 | 108 | 0 | 13.1133 | 2.2 | 5.7 | 55 | 12.26
31 | 109 | 0 | 13.1133 | 2.2 | 5.8 | 55 | 12.32
31 | 110 | 0 | 13.1133 | 2.2 | 5.9 | 55 | 12.38
31 | 111 | 0 | 13.1133 | 2.2 | 6 | 55 | 12.44
31 | 112 | 0 | 13.1133 | 2.2 | 6.1 | 55 | 12.5
31 | 113 | 0 | 13.1133 | 2.2 | 6.2 | 55 | 12.56
31 | 114 | 0 | 13.1133 | 2.2 | 6.3 | 55 | 12.62
31 | 115 | 0 | 13.1133 | 2.2 | 6.4 | 55 | 12.68
31 | 116 | 0 | 13.1133 | 2.2 | 6.5 | 55 | 12.74
31 | 117 | 0 | 13.1133 | 2.2 | 6.6 | 55 | 12.8
31 | 118 | 0 | 13.1133 | 2.2 | 6.7 | 55 | 12.86
31 | 119 | 0 | 13.1133 | 2.2 | 6.8 | 55 | 12.92
31 | 120 | 0 | 13.1133 | 2.2 | 6.9 | 55 | 12.98
31 | 121 | 0 | 13.1133 | 2.2 | 7 | 55 | 13.04
31 | 122 | 0 | 13.1133 | 2.2 | 7.1 | 55 | 13.094
31 | 123 | 0 | 13.1133 | 2.2 | 7.2 | 55 | 13.148
31 | 124 | 0 | 13.1133 | 2.2 | 7.3 | 55 | 13.202
31 | 125 | 0 | 13.1133 | 2.2 | 7.4 | 55 | 13.256
31 | 126 | 0 | 13.1133 | 2.2 | 7.5 | 55 | 13.31
31 | 127 | 0 | 13.1133 | 2.2 | 7.6 | 55 | 13.364
31 | 128 | 0 | 13.1133 | 2.2 | 7.7 | 55 | 13.418
31 | 129 | 0 | 13.1133 | 2.2 | 7.8 | 55 | 13.472
31 | 130 | 0 | 13.1133 | 2.2 | 7.9 | 55 | 13.526
31 | 131 | 0 | 13.1133 | 2.2 | 8 | 55 | 13.58
31 | 132 | 0 | 13.1133 | 2.2 | 8.1 | 55 | 13.634
31 | 133 | 0 | 13.1133 | 2.2 | 8.2 | 55 | 13.688
31 | 134 | 0 | 13.1133 | 2.2 | 8.3 | 55 | 13.742
31 | 135 | 0 | 13.1133 | 2.2 | 8.4 | 55 | 13.796
31 | 136 | 0 | 13.1133 | 2.2 | 8.5 | 55 | 13.85
31 | 137 | 0 | 13.1133 | 2.2 | 8.6 | 55 | 13.904
31 | 138 | 0 | 13.1133 | 2.2 | 8.7 | 55 | 13.958
31 | 139 | 0 | 13.1133 | 2.2 | 8.8 | 55 | 14.012
31 | 140 | 0 | 13.1133 | 2.2 | 8.9 | 55 | 14.066
31 | 141 | 0 | 13.1133 | 2.2 | 9 | 55 | 14.12
31 | 142 | 0 | 13.1133 | 2.2 | 9.1 | 55 | 14.23
31 | 143 | 0 | 13.1133 | 2.2 | 9.2 | 55 | 14.34
31 | 144 | 0 | 13.1133 | 2.2 | 9.3 | 55 | 14.45
31 | 145 | 0 | 13.1133 | 2.2 | 9.4 | 55 | 14.56
31 | 146 | 0 | 13.1133 | 2.2 | 9.5 | 55 | 14.67
31 | 147 | 0 | 13.1133 | 2.2 | 9.6 | 55 | 14.78
31 | 148 | 0 | 13.1133 | 2.2 | 9.7 | 55 | 14.89
31 | 149 | 0 | 13.1133 | 2.2 | 9.8 | 55 | 15
31 | 150 | 0 | 13.1133 | 2.2 | 9.9 | 55 | 15.11
32 | 45 | 0 | 13.1267 | 2.2 | 10 | 55 | 15.22
32 | 46 | 0 | 13.1267 | 2.3 | 3 | 55 | 10
32 | 47 | 0 | 13.1267 | 2.3 | 3.1 | 55 | 10.093
32 | 48 | 0 | 13.1267 | 2.3 | 3.2 | 55 | 10.186
32 | 49 | 0 | 13.1267 | 2.3 | 3.3 | 55 | 10.279
32 | 50 | 0 | 13.1267 | 2.3 | 3.4 | 55 | 10.372
32 | 51 | 0 | 13.1267 | 2.3 | 3.5 | 55 | 10.465
32 | 52 | 0 | 13.1267 | 2.3 | 3.6 | 55 | 10.558
32 | 53 | 0 | 13.1267 | 2.3 | 3.7 | 55 | 10.651
32 | 54 | 0 | 13.1267 | 2.3 | 3.8 | 55 | 10.744
32 | 55 | 0 | 13.1267 | 2.3 | 3.9 | 55 | 10.837
32 | 56 | 0 | 13.1267 | 2.3 | 4 | 55 | 10.93
32 | 57 | 0 | 13.1267 | 2.3 | 4.1 | 55 | 11.023
32 | 58 | 0 | 13.1267 | 2.3 | 4.2 | 55 | 11.116
32 | 59 | 0 | 13.1267 | 2.3 | 4.3 | 55 | 11.209
32 | 60 | 0 | 13.1267 | 2.3 | 4.4 | 55 | 11.302
32 | 61 | 0 | 13.1267 | 2.3 | 4.5 | 55 | 11.395
32 | 62 | 0 | 13.1267 | 2.3 | 4.6 | 55 | 11.488
32 | 63 | 0 | 13.1267 | 2.3 | 4.7 | 55 | 11.581
32 | 64 | 0 | 13.1267 | 2.3 | 4.8 | 55 | 11.674
32 | 65 | 0 | 13.1267 | 2.3 | 4.9 | 55 | 11.767
32 | 66 | 0 | 13.1267 | 2.3 | 5 | 55 | 11.86
32 | 67 | 0 | 13.1267 | 2.3 | 5.1 | 55 | 11.92
32 | 68 | 0 | 13.1267 | 2.3 | 5.2 | 55 | 11.98
32 | 69 | 0 | 13.1267 | 2.3 | 5.3 | 55 | 12.04
32 | 70 | 0 | 13.1267 | 2.3 | 5.4 | 55 | 12.1
32 | 71 | 0 | 13.1267 | 2.3 | 5.5 | 55 | 12.16
32 | 72 | 0 | 13.1267 | 2.3 | 5.6 | 55 | 12.22
32 | 73 | 0 | 13.1267 | 2.3 | 5.7 | 55 | 12.28
32 | 74 | 0 | 13.1267 | 2.3 | 5.8 | 55 | 12.34
32 | 75 | 0 | 13.1267 | 2.3 | 5.9 | 55 | 12.4
32 | 76 | 0 | 13.1267 | 2.3 | 6 | 55 | 12.46
32 | 77 | 0 | 13.1267 | 2.3 | 6.1 | 55 | 12.52
32 | 78 | 0 | 13.1267 | 2.3 | 6.2 | 55 | 12.58
32 | 79 | 0 | 13.1267 | 2.3 | 6.3 | 55 | 12.64
32 | 80 | 0 | 13.1267 | 2.3 | 6.4 | 55 | 12.7
32 | 81 | 0 | 13.1267 | 2.3 | 6.5 | 55 | 12.76
32 | 82 | 0 | 13.1267 | 2.3 | 6.6 | 55 | 12.82
32 | 83 | 0 | 13.1267 | 2.3 | 6.7 | 55 | 12.88
32 | 84 | 0 | 13.1267 | 2.3 | 6.8 | 55 | 12.94
32 | 85 | 0 | 13.1267 | 2.3 | 6.9 | 55 | 13
32 | 86 | 0 | 13.1267 | 2.3 | 7 | 55 | 13.06
32 | 87 | 0 | 13.1267 | 2.3 | 7.1 | 55 | 13.1135
32 | 88 | 0 | 13.1267 | 2.3 | 7.2 | 55 | 13.167
32 | 89 | 0 | 13.1267 | 2.3 | 7.3 | 55 | 13.2205
32 | 90 | 0 | 13.1267 | 2.3 | 7.4 | 55 | 13.274
32 | 91 | 0 | 13.1267 | 2.3 | 7.5 | 55 | 13.3275
32 | 92 | 0 | 13.1267 | 2.3 | 7.6 | 55 | 13.381
32 | 93 | 0 | 13.1267 | 2.3 | 7.7 | 55 | 13.4345
32 | 94 | 0 | 13.1267 | 2.3 | 7.8 | 55 | 13.488
32 | 95 | 0 | 13.1267 | 2.3 | 7.9 | 55 | 13.5415
32 | 96 | 0 | 13.1267 | 2.3 | 8 | 55 | 13.595
32 | 97 | 0 | 13.1267 | 2.3 | 8.1 | 55 | 13.6485
32 | 98 | 0 | 13.1267 | 2.3 | 8.2 | 55 | 13.702
32 | 99 | 0 | 13.1267 | 2.3 | 8.3 | 55 | 13.7555
32 | 100 | 0 | 13.1267 | 2.3 | 8.4 | 55 | 13.809
32 | 101 | 0 | 13.1267 | 2.3 | 8.5 | 55 | 13.8625
32 | 102 | 0 | 13.1267 | 2.3 | 8.6 | 55 | 13.916
32 | 103 | 0 | 13.1267 | 2.3 | 8.7 | 55 | 13.9695
32 | 104 | 0 | 13.1267 | 2.3 | 8.8 | 55 | 14.023
32 | 105 | 0 | 13.1267 | 2.3 | 8.9 | 55 | 14.0765
32 | 106 | 0 | 13.1267 | 2.3 | 9 | 55 | 14.13
32 | 107 | 0 | 13.1267 | 2.3 | 9.1 | 55 | 14.24
32 | 108 | 0 | 13.1267 | 2.3 | 9.2 | 55 | 14.35
32 | 109 | 0 | 13.1267 | 2.3 | 9.3 | 55 | 14.46
32 | 110 | 0 | 13.1267 | 2.3 | 9.4 | 55 | 14.57
32 | 111 | 0 | 13.1267 | 2.3 | 9.5 | 55 | 14.68
32 | 112 | 0 | 13.1267 | 2.3 | 9.6 | 55 | 14.79
32 | 113 | 0 | 13.1267 | 2.3 | 9.7 | 55 | 14.9
32 | 114 | 0 | 13.1267 | 2.3 | 9.8 | 55 | 15.01
32 | 115 | 0 | 13.1267 | 2.3 | 9.9 | 55 | 15.12
32 | 116 | 0 | 13.1267 | 2.3 | 10 | 55 | 15.23
32 | 117 | 0 | 13.1267 | 2.4 | 3 | 55 | 10
32 | 118 | 0 | 13.1267 | 2.4 | 3.1 | 55 | 10.094
32 | 119 | 0 | 13.1267 | 2.4 | 3.2 | 55 | 10.188
32 | 120 | 0 | 13.1267 | 2.4 | 3.3 | 55 | 10.282
32 | 121 | 0 | 13.1267 | 2.4 | 3.4 | 55 | 10.376
32 | 122 | 0 | 13.1267 | 2.4 | 3.5 | 55 | 10.47
32 | 123 | 0 | 13.1267 | 2.4 | 3.6 | 55 | 10.564
32 | 124 | 0 | 13.1267 | 2.4 | 3.7 | 55 | 10.658
32 | 125 | 0 | 13.1267 | 2.4 | 3.8 | 55 | 10.752
32 | 126 | 0 | 13.1267 | 2.4 | 3.9 | 55 | 10.846
32 | 127 | 0 | 13.1267 | 2.4 | 4 | 55 | 10.94
32 | 128 | 0 | 13.1267 | 2.4 | 4.1 | 55 | 11.034
32 | 129 | 0 | 13.1267 | 2.4 | 4.2 | 55 | 11.128
32 | 130 | 0 | 13.1267 | 2.4 | 4.3 | 55 | 11.222
32 | 131 | 0 | 13.1267 | 2.4 | 4.4 | 55 | 11.316
32 | 132 | 0 | 13.1267 | 2.4 | 4.5 | 55 | 11.41
32 | 133 | 0 | 13.1267 | 2.4 | 4.6 | 55 | 11.504
32 | 134 | 0 | 13.1267 | 2.4 | 4.7 | 55 | 11.598
32 | 135 | 0 | 13.1267 | 2.4 | 4.8 | 55 | 11.692
32 | 136 | 0 | 13.1267 | 2.4 | 4.9 | 55 | 11.786
32 | 137 | 0 | 13.1267 | 2.4 | 5 | 55 | 11.88
32 | 138 | 0 | 13.1267 | 2.4 | 5.1 | 55 | 11.94
32 | 139 | 0 | 13.1267 | 2.4 | 5.2 | 55 | 12
32 | 140 | 0 | 13.1267 | 2.4 | 5.3 | 55 | 12.06
32 | 141 | 0 | 13.1267 | 2.4 | 5.4 | 55 | 12.12
32 | 142 | 0 | 13.1267 | 2.4 | 5.5 | 55 | 12.18
32 | 143 | 0 | 13.1267 | 2.4 | 5.6 | 55 | 12.24
32 | 144 | 0 | 13.1267 | 2.4 | 5.7 | 55 | 12.3
32 | 145 | 0 | 13.1267 | 2.4 | 5.8 | 55 | 12.36
32 | 146 | 0 | 13.1267 | 2.4 | 5.9 | 55 | 12.42
32 | 147 | 0 | 13.1267 | 2.4 | 6 | 55 | 12.48
32 | 148 | 0 | 13.1267 | 2.4 | 6.1 | 55 | 12.54
32 | 149 | 0 | 13.1267 | 2.4 | 6.2 | 55 | 12.6
32 | 150 | 0 | 13.1267 | 2.4 | 6.3 | 55 | 12.66
33 | 45 | 0 | 13.14 | 2.4 | 6.4 | 55 | 12.72
33 | 46 | 0 | 13.14 | 2.4 | 6.5 | 55 | 12.78
33 | 47 | 0 | 13.14 | 2.4 | 6.6 | 55 | 12.84
33 | 48 | 0 | 13.14 | 2.4 | 6.7 | 55 | 12.9
33 | 49 | 0 | 13.14 | 2.4 | 6.8 | 55 | 12.96
33 | 50 | 0 | 13.14 | 2.4 | 6.9 | 55 | 13.02
33 | 51 | 0 | 13.14 | 2.4 | 7 | 55 | 13.08
33 | 52 | 0 | 13.14 | 2.4 | 7.1 | 55 | 13.133
33 | 53 | 0 | 13.14 | 2.4 | 7.2 | 55 | 13.186
33 | 54 | 0 | 13.14 | 2.4 | 7.3 | 55 | 13.239
33 | 55 | 0 | 13.14 | 2.4 | 7.4 | 55 | 13.292
33 | 56 | 0 | 13.14 | 2.4 | 7.5 | 55 | 13.345
33 | 57 | 0 | 13.14 | 2.4 | 7.6 | 55 | 13.398
33 | 58 | 0 | 13.14 | 2.4 | 7.7 | 55 | 13.451
33 | 59 | 0 | 13.14 | 2.4 | 7.8 | 55 | 13.504
33 | 60 | 0 | 13.14 | 2.4 | 7.9 | 55 | 13.557
33 | 61 | 0 | 13.14 | 2.4 | 8 | 55 | 13.61
33 | 62 | 0 | 13.14 | 2.4 | 8.1 | 55 | 13.663
33 | 63 | 0 | 13.14 | 2.4 | 8.2 | 55 | 13.716
33 | 64 | 0 | 13.14 | 2.4 | 8.3 | 55 | 13.769
33 | 65 | 0 | 13.14 | 2.4 | 8.4 | 55 | 13.822
33 | 66 | 0 | 13.14 | 2.4 | 8.5 | 55 | 13.875
33 | 67 | 0 | 13.14 | 2.4 | 8.6 | 55 | 13.928
33 | 68 | 0 | 13.14 | 2.4 | 8.7 | 55 | 13.981
33 | 69 | 0 | 13.14 | 2.4 | 8.8 | 55 | 14.034
33 | 70 | 0 | 13.14 | 2.4 | 8.9 | 55 | 14.087
33 | 71 | 0 | 13.14 | 2.4 | 9 | 55 | 14.14
33 | 72 | 0 | 13.14 | 2.4 | 9.1 | 55 | 14.25
33 | 73 | 0 | 13.14 | 2.4 | 9.2 | 55 | 14.36
33 | 74 | 0 | 13.14 | 2.4 | 9.3 | 55 | 14.47
33 | 75 | 0 | 13.14 | 2.4 | 9.4 | 55 | 14.58
33 | 76 | 0 | 13.14 | 2.4 | 9.5 | 55 | 14.69
33 | 77 | 0 | 13.14 | 2.4 | 9.6 | 55 | 14.8
33 | 78 | 0 | 13.14 | 2.4 | 9.7 | 55 | 14.91
33 | 79 | 0 | 13.14 | 2.4 | 9.8 | 55 | 15.02
33 | 80 | 0 | 13.14 | 2.4 | 9.9 | 55 | 15.13
33 | 81 | 0 | 13.14 | 2.4 | 10 | 55 | 15.24
33 | 82 | 0 | 13.14 | 2.5 | 3 | 55 | 10
33 | 83 | 0 | 13.14 | 2.5 | 3.1 | 55 | 10.095
33 | 84 | 0 | 13.14 | 2.5 | 3.2 | 55 | 10.19
33 | 85 | 0 | 13.14 | 2.5 | 3.3 | 55 | 10.285
33 | 86 | 0 | 13.14 | 2.5 | 3.4 | 55 | 10.38
33 | 87 | 0 | 13.14 | 2.5 | 3.5 | 55 | 10.475
33 | 88 | 0 | 13.14 | 2.5 | 3.6 | 55 | 10.57
33 | 89 | 0 | 13.14 | 2.5 | 3.7 | 55 | 10.665
33 | 90 | 0 | 13.14 | 2.5 | 3.8 | 55 | 10.76
33 | 91 | 0 | 13.14 | 2.5 | 3.9 | 55 | 10.855
33 | 92 | 0 | 13.14 | 2.5 | 4 | 55 | 10.95
33 | 93 | 0 | 13.14 | 2.5 | 4.1 | 55 | 11.045
33 | 94 | 0 | 13.14 | 2.5 | 4.2 | 55 | 11.14
33 | 95 | 0 | 13.14 | 2.5 | 4.3 | 55 | 11.235
33 | 96 | 0 | 13.14 | 2.5 | 4.4 | 55 | 11.33
33 | 97 | 0 | 13.14 | 2.5 | 4.5 | 55 | 11.425
33 | 98 | 0 | 13.14 | 2.5 | 4.6 | 55 | 11.52
33 | 99 | 0 | 13.14 | 2.5 | 4.7 | 55 | 11.615
33 | 100 | 0 | 13.14 | 2.5 | 4.8 | 55 | 11.71
33 | 101 | 0 | 13.14 | 2.5 | 4.9 | 55 | 11.805
33 | 102 | 0 | 13.14 | 2.5 | 5 | 55 | 11.9
33 | 103 | 0 | 13.14 | 2.5 | 5.1 | 55 | 11.96
33 | 104 | 0 | 13.14 | 2.5 | 5.2 | 55 | 12.02
33 | 105 | 0 | 13.14 | 2.5 | 5.3 | 55 | 12.08
33 | 106 | 0 | 13.14 | 2.5 | 5.4 | 55 | 12.14
33 | 107 | 0 | 13.14 | 2.5 | 5.5 | 55 | 12.2
33 | 108 | 0 | 13.14 | 2.5 | 5.6 | 55 | 12.26
33 | 109 | 0 | 13.14 | 2.5 | 5.7 | 55 | 12.32
33 | 110 | 0 | 13.14 | 2.5 | 5.8 | 55 | 12.38
33 | 111 | 0 | 13.14 | 2.5 | 5.9 | 55 | 12.44
33 | 112 | 0 | 13.14 | 2.5 | 6 | 55 | 12.5
33 | 113 | 0 | 13.14 | 2.5 | 6.1 | 55 | 12.56
33 | 114 | 0 | 13.14 | 2.5 | 6.2 | 55 | 12.62
33 | 115 | 0 | 13.14 | 2.5 | 6.3 | 55 | 12.68
33 | 116 | 0 | 13.14 | 2.5 | 6.4 | 55 | 12.74
33 | 117 | 0 | 13.14 | 2.5 | 6.5 | 55 | 12.8
33 | 118 | 0 | 13.14 | 2.5 | 6.6 | 55 | 12.86
33 | 119 | 0 | 13.14 | 2.5 | 6.7 | 55 | 12.92
33 | 120 | 0 | 13.14 | 2.5 | 6.8 | 55 | 12.98
33 | 121 | 0 | 13.14 | 2.5 | 6.9 | 55 | 13.04
33 | 122 | 0 | 13.14 | 2.5 | 7 | 55 | 13.1
33 | 123 | 0 | 13.14 | 2.5 | 7.1 | 55 | 13.1525
33 | 124 | 0 | 13.14 | 2.5 | 7.2 | 55 | 13.205
33 | 125 | 0 | 13.14 | 2.5 | 7.3 | 55 | 13.2575
33 | 126 | 0 | 13.14 | 2.5 | 7.4 | 55 | 13.31
33 | 127 | 0 | 13.14 | 2.5 | 7.5 | 55 | 13.3625
33 | 128 | 0 | 13.14 | 2.5 | 7.6 | 55 | 13.415
33 | 129 | 0 | 13.14 | 2.5 | 7.7 | 55 | 13.4675
33 | 130 | 0 | 13.14 | 2.5 | 7.8 | 55 | 13.52
33 | 131 | 0 | 13.14 | 2.5 | 7.9 | 55 | 13.5725
33 | 132 | 0 | 13.14 | 2.5 | 8 | 55 | 13.625
33 | 133 | 0 | 13.14 | 2.5 | 8.1 | 55 | 13.6775
33 | 134 | 0 | 13.14 | 2.5 | 8.2 | 55 | 13.73
33 | 135 | 0 | 13.14 | 2.5 | 8.3 | 55 | 13.7825
33 | 136 | 0 | 13.14 | 2.5 | 8.4 | 55 | 13.835
33 | 137 | 0 | 13.14 | 2.5 | 8.5 | 55 | 13.8875
33 | 138 | 0 | 13.14 | 2.5 | 8.6 | 55 | 13.94
33 | 139 | 0 | 13.14 | 2.5 | 8.7 | 55 | 13.9925
33 | 140 | 0 | 13.14 | 2.5 | 8.8 | 55 | 14.045
33 | 141 | 0 | 13.14 | 2.5 | 8.9 | 55 | 14.0975
33 | 142 | 0 | 13.14 | 2.5 | 9 | 55 | 14.15
33 | 143 | 0 | 13.14 | 2.5 | 9.1 | 55 | 14.26
33 | 144 | 0 | 13.14 | 2.5 | 9.2 | 55 | 14.37
33 | 145 | 0 | 13.14 | 2.5 | 9.3 | 55 | 14.48
33 | 146 | 0 | 13.14 | 2.5 | 9.4 | 55 | 14.59
33 | 147 | 0 | 13.14 | 2.5 | 9.5 | 55 | 14.7
33 | 148 | 0 | 13.14 | 2.5 | 9.6 | 55 | 14.81
33 | 149 | 0 | 13.14 | 2.5 | 9.7 | 55 | 14.92
33 | 150 | 0 | 13.14 | 2.5 | 9.8 | 55 | 15.03
34 | 45 | 0 | 13.1533 | 2.5 | 9.9 | 55 | 15.14
34 | 46 | 0 | 13.1533 | 2.5 | 10 | 55 | 15.25
34 | 47 | 0 | 13.1533 | 2.6 | 3 | 55 | 10
34 | 48 | 0 | 13.1533 | 2.6 | 3.1 | 55 | 10.096
34 | 49 | 0 | 13.1533 | 2.6 | 3.2 | 55 | 10.192
34 | 50 | 0 | 13.1533 | 2.6 | 3.3 | 55 | 10.288
34 | 51 | 0 | 13.1533 | 2.6 | 3.4 | 55 | 10.384
34 | 52 | 0 | 13.1533 | 2.6 | 3.5 | 55 | 10.48
34 | 53 | 0 | 13.1533 | 2.6 | 3.6 | 55 | 10.576
34 | 54 | 0 | 13.1533 | 2.6 | 3.7 | 55 | 10.672
34 | 55 | 0 | 13.1533 | 2.6 | 3.8 | 55 | 10.768
34 | 56 | 0 | 13.1533 | 2.6 | 3.9 | 55 | 10.864
34 | 57 | 0 | 13.1533 | 2.6 | 4 | 55 | 10.96
34 | 58 | 0 | 13.1533 | 2.6 | 4.1 | 55 | 11.056
34 | 59 | 0 | 13.1533 | 2.6 | 4.2 | 55 | 11.152
34 | 60 | 0 | 13.1533 | 2.6 | 4.3 | 55 | 11.248
34 | 61 | 0 | 13.1533 | 2.6 | 4.4 | 55 | 11.344
34 | 62 | 0 | 13.1533 | 2.6 | 4.5 | 55 | 11.44
34 | 63 | 0 | 13.1533 | 2.6 | 4.6 | 55 | 11.536
34 | 64 | 0 | 13.1533 | 2.6 | 4.7 | 55 | 11.632
34 | 65 | 0 | 13.1533 | 2.6 | 4.8 | 55 | 11.728
34 | 66 | 0 | 13.1533 | 2.6 | 4.9 | 55 | 11.824
34 | 67 | 0 | 13.1533 | 2.6 | 5 | 55 | 11.92
34 | 68 | 0 | 13.1533 | 2.6 | 5.1 | 55 | 11.98
34 | 69 | 0 | 13.1533 | 2.6 | 5.2 | 55 | 12.04
34 | 70 | 0 | 13.1533 | 2.6 | 5.3 | 55 | 12.1
34 | 71 | 0 | 13.1533 | 2.6 | 5.4 | 55 | 12.16
34 | 72 | 0 | 13.1533 | 2.6 | 5.5 | 55 | 12.22
34 | 73 | 0 | 13.1533 | 2.6 | 5.6 | 55 | 12.28
34 | 74 | 0 | 13.1533 | 2.6 | 5.7 | 55 | 12.34
34 | 75 | 0 | 13.1533 | 2.6 | 5.8 | 55 | 12.4
34 | 76 | 0 | 13.1533 | 2.6 | 5.9 | 55 | 12.46
34 | 77 | 0 | 13.1533 | 2.6 | 6 | 55 | 12.52
34 | 78 | 0 | 13.1533 | 2.6 | 6.1 | 55 | 12.58
34 | 79 | 0 | 13.1533 | 2.6 | 6.2 | 55 | 12.64
34 | 80 | 0 | 13.1533 | 2.6 | 6.3 | 55 | 12.7
34 | 81 | 0 | 13.1533 | 2.6 | 6.4 | 55 | 12.76
34 | 82 | 0 | 13.1533 | 2.6 | 6.5 | 55 | 12.82
34 | 83 | 0 | 13.1533 | 2.6 | 6.6 | 55 | 12.88
34 | 84 | 0 | 13.1533 | 2.6 | 6.7 | 55 | 12.94
34 | 85 | 0 | 13.1533 | 2.6 | 6.8 | 55 | 13
34 | 86 | 0 | 13.1533 | 2.6 | 6.9 | 55 | 13.06
34 | 87 | 0 | 13.1533 | 2.6 | 7 | 55 | 13.12
34 | 88 | 0 | 13.1533 | 2.6 | 7.1 | 55 | 13.172
34 | 89 | 0 | 13.1533 | 2.6 | 7.2 | 55 | 13.224
34 | 90 | 0 | 13.1533 | 2.6 | 7.3 | 55 | 13.276
34 | 91 | 0 | 13.1533 | 2.6 | 7.4 | 55 | 13.328
34 | 92 | 0 | 13.1533 | 2.6 | 7.5 | 55 | 13.38
34 | 93 | 0 | 13.1533 | 2.6 | 7.6 | 55 | 13.432
34 | 94 | 0 | 13.1533 | 2.6 | 7.7 | 55 | 13.484
34 | 95 | 0 | 13.1533 | 2.6 | 7.8 | 55 | 13.536
34 | 96 | 0 | 13.1533 | 2.6 | 7.9 | 55 | 13.588
34 | 97 | 0 | 13.1533 | 2.6 | 8 | 55 | 13.64
34 | 98 | 0 | 13.1533 | 2.6 | 8.1 | 55 | 13.692
34 | 99 | 0 | 13.1533 | 2.6 | 8.2 | 55 | 13.744
34 | 100 | 0 | 13.1533 | 2.6 | 8.3 | 55 | 13.796
34 | 101 | 0 | 13.1533 | 2.6 | 8.4 | 55 | 13.848
34 | 102 | 0 | 13.1533 | 2.6 | 8.5 | 55 | 13.9
34 | 103 | 0 | 13.1533 | 2.6 | 8.6 | 55 | 13.952
34 | 104 | 0 | 13.1533 | 2.6 | 8.7 | 55 | 14.004
34 | 105 | 0 | 13.1533 | 2.6 | 8.8 | 55 | 14.056
34 | 106 | 0 | 13.1533 | 2.6 | 8.9 | 55 | 14.108
34 | 107 | 0 | 13.1533 | 2.6 | 9 | 55 | 14.16
34 | 108 | 0 | 13.1533 | 2.6 | 9.1 | 55 | 14.27
34 | 109 | 0 | 13.1533 | 2.6 | 9.2 | 55 | 14.38
34 | 110 | 0 | 13.1533 | 2.6 | 9.3 | 55 | 14.49
34 | 111 | 0 | 13.1533 | 2.6 | 9.4 | 55 | 14.6
34 | 112 | 0 | 13.1533 | 2.6 | 9.5 | 55 | 14.71
34 | 113 | 0 | 13.1533 | 2.6 | 9.6 | 55 | 14.82
34 | 114 | 0 | 13.1533 | 2.6 | 9.7 | 55 | 14.93
34 | 115 | 0 | 13.1533 | 2.6 | 9.8 | 55 | 15.04
34 | 116 | 0 | 13.1533 | 2.6 | 9.9 | 55 | 15.15
34 | 117 | 0 | 13.1533 | 2.6 | 10 | 55 | 15.26
34 | 118 | 0 | 13.1533 | 2.7 | 3 | 55 | 10
34 | 119 | 0 | 13.1533 | 2.7 | 3.1 | 55 | 10.097
34 | 120 | 0 | 13.1533 | 2.7 | 3.2 | 55 | 10.194
34 | 121 | 0 | 13.1533 | 2.7 | 3.3 | 55 | 10.291
34 | 122 | 0 | 13.1533 | 2.7 | 3.4 | 55 | 10.388
34 | 123 | 0 | 13.1533 | 2.7 | 3.5 | 55 | 10.485
34 | 124 | 0 | 13.1533 | 2.7 | 3.6 | 55 | 10.582
34 | 125 | 0 | 13.1533 | 2.7 | 3.7 | 55 | 10.679
34 | 126 | 0 | 13.1533 | 2.7 | 3.8 | 55 | 10.776
34 | 127 | 0 | 13.1533 | 2.7 | 3.9 | 55 | 10.873
34 | 128 | 0 | 13.1533 | 2.7 | 4 | 55 | 10.97
34 | 129 | 0 | 13.1533 | 2.7 | 4.1 | 55 | 11.067
34 | 130 | 0 | 13.1533 | 2.7 | 4.2 | 55 | 11.164
34 | 131 | 0 | 13.1533 | 2.7 | 4.3 | 55 | 11.261
34 | 132 | 0 | 13.1533 | 2.7 | 4.4 | 55 | 11.358
34 | 133 | 0 | 13.1533 | 2.7 | 4.5 | 55 | 11.455
34 | 134 | 0 | 13.1533 | 2.7 | 4.6 | 55 | 11.552
34 | 135 | 0 | 13.1533 | 2.7 | 4.7 | 55 | 11.649
34 | 136 | 0 | 13.1533 | 2.7 | 4.8 | 55 | 11.746
34 | 137 | 0 | 13.1533 | 2.7 | 4.9 | 55 | 11.843
34 | 138 | 0 | 13.1533 | 2.7 | 5 | 55 | 11.94
34 | 139 | 0 | 13.1533 | 2.7 | 5.1 | 55 | 12
34 | 140 | 0 | 13.1533 | 2.7 | 5.2 | 55 | 12.06
34 | 141 | 0 | 13.1533 | 2.7 | 5.3 | 55 | 12.12
34 | 142 | 0 | 13.1533 | 2.7 | 5.4 | 55 | 12.18
34 | 143 | 0 | 13.1533 | 2.7 | 5.5 | 55 | 12.24
34 | 144 | 0 | 13.1533 | 2.7 | 5.6 | 55 | 12.3
34 | 145 | 0 | 13.1533 | 2.7 | 5.7 | 55 | 12.36
34 | 146 | 0 | 13.1533 | 2.7 | 5.8 | 55 | 12.42
34 | 147 | 0 | 13.1533 | 2.7 | 5.9 | 55 | 12.48
34 | 148 | 0 | 13.1533 | 2.7 | 6 | 55 | 12.54
34 | 149 | 0 | 13.1533 | 2.7 | 6.1 | 55 | 12.6
34 | 150 | 0 | 13.1533 | 2.7 | 6.2 | 55 | 12.66
35 | 45 | 0 | 13.1667 | 2.7 | 6.3 | 55 | 12.72
35 | 46 | 0 | 13.1667 | 2.7 | 6.4 | 55 | 12.78
35 | 47 | 0 | 13.1667 | 2.7 | 6.5 | 55 | 12.84
35 | 48 | 0 | 13.1667 | 2.7 | 6.6 | 55 | 12.9
35 | 49 | 0 | 13.1667 | 2.7 | 6.7 | 55 | 12.96
35 | 50 | 0 | 13.1667 | 2.7 | 6.8 | 55 | 13.02
35 | 51 | 0 | 13.1667 | 2.7 | 6.9 | 55 | 13.08
35 | 52 | 0 | 13.1667 | 2.7 | 7 | 55 | 13.14
35 | 53 | 0 | 13.1667 | 2.7 | 7.1 | 55 | 13.1915
35 | 54 | 0 | 13.1667 | 2.7 | 7.2 | 55 | 13.243
35 | 55 | 0 | 13.1667 | 2.7 | 7.3 | 55 | 13.2945
35 | 56 | 0 | 13.1667 | 2.7 | 7.4 | 55 | 13.346
35 | 57 | 0 | 13.1667 | 2.7 | 7.5 | 55 | 13.3975
35 | 58 | 0 | 13.1667 | 2.7 | 7.6 | 55 | 13.449
35 | 59 | 0 | 13.1667 | 2.7 | 7.7 | 55 | 13.5005
35 | 60 | 0 | 13.1667 | 2.7 | 7.8 | 55 | 13.552
35 | 61 | 0 | 13.1667 | 2.7 | 7.9 | 55 | 13.6035
35 | 62 | 0 | 13.1667 | 2.7 | 8 | 55 | 13.655
35 | 63 | 0 | 13.1667 | 2.7 | 8.1 | 55 | 13.7065
35 | 64 | 0 | 13.1667 | 2.7 | 8.2 | 55 | 13.758
35 | 65 | 0 | 13.1667 | 2.7 | 8.3 | 55 | 13.8095
35 | 66 | 0 | 13.1667 | 2.7 | 8.4 | 55 | 13.861
35 | 67 | 0 | 13.1667 | 2.7 | 8.5 | 55 | 13.9125
35 | 68 | 0 | 13.1667 | 2.7 | 8.6 | 55 | 13.964
35 | 69 | 0 | 13.1667 | 2.7 | 8.7 | 55 | 14.0155
35 | 70 | 0 | 13.1667 | 2.7 | 8.8 | 55 | 14.067
35 | 71 | 0 | 13.1667 | 2.7 | 8.9 | 55 | 14.1185
35 | 72 | 0 | 13.1667 | 2.7 | 9 | 55 | 14.17
35 | 73 | 0 | 13.1667 | 2.7 | 9.1 | 55 | 14.28
35 | 74 | 0 | 13.1667 | 2.7 | 9.2 | 55 | 14.39
35 | 75 | 0 | 13.1667 | 2.7 | 9.3 | 55 | 14.5
35 | 76 | 0 | 13.1667 | 2.7 | 9.4 | 55 | 14.61
35 | 77 | 0 | 13.1667 | 2.7 | 9.5 | 55 | 14.72
35 | 78 | 0 | 13.1667 | 2.7 | 9.6 | 55 | 14.83
35 | 79 | 0 | 13.1667 | 2.7 | 9.7 | 55 | 14.94
35 | 80 | 0 | 13.1667 | 2.7 | 9.8 | 55 | 15.05
35 | 81 | 0 | 13.1667 | 2.7 | 9.9 | 55 | 15.16
35 | 82 | 0 | 13.1667 | 2.7 | 10 | 55 | 15.27
35 | 83 | 0 | 13.1667 | 2.8 | 3 | 55 | 10
35 | 84 | 0 | 13.1667 | 2.8 | 3.1 | 55 | 10.098
35 | 85 | 0 | 13.1667 | 2.8 | 3.2 | 55 | 10.196
35 | 86 | 0 | 13.1667 | 2.8 | 3.3 | 55 | 10.294
35 | 87 | 0 | 13.1667 | 2.8 | 3.4 | 55 | 10.392
35 | 88 | 0 | 13.1667 | 2.8 | 3.5 | 55 | 10.49
35 | 89 | 0 | 13.1667 | 2.8 | 3.6 | 55 | 10.588
35 | 90 | 0 | 13.1667 | 2.8 | 3.7 | 55 | 10.686
35 | 91 | 0 | 13.1667 | 2.8 | 3.8 | 55 | 10.784
35 | 92 | 0 | 13.1667 | 2.8 | 3.9 | 55 | 10.882
35 | 93 | 0 | 13.1667 | 2.8 | 4 | 55 | 10.98
35 | 94 | 0 | 13.1667 | 2.8 | 4.1 | 55 | 11.078
35 | 95 | 0 | 13.1667 | 2.8 | 4.2 | 55 | 11.176
35 | 96 | 0 | 13.1667 | 2.8 | 4.3 | 55 | 11.274
35 | 97 | 0 | 13.1667 | 2.8 | 4.4 | 55 | 11.372
35 | 98 | 0 | 13.1667 | 2.8 | 4.5 | 55 | 11.47
35 | 99 | 0 | 13.1667 | 2.8 | 4.6 | 55 | 11.568
35 | 100 | 0 | 13.1667 | 2.8 | 4.7 | 55 | 11.666
35 | 101 | 0 | 13.1667 | 2.8 | 4.8 | 55 | 11.764
35 | 102 | 0 | 13.1667 | 2.8 | 4.9 | 55 | 11.862
35 | 103 | 0 | 13.1667 | 2.8 | 5 | 55 | 11.96
35 | 104 | 0 | 13.1667 | 2.8 | 5.1 | 55 | 12.02
35 | 105 | 0 | 13.1667 | 2.8 | 5.2 | 55 | 12.08
35 | 106 | 0 | 13.1667 | 2.8 | 5.3 | 55 | 12.14
35 | 107 | 0 | 13.1667 | 2.8 | 5.4 | 55 | 12.2
35 | 108 | 0 | 13.1667 | 2.8 | 5.5 | 55 | 12.26
35 | 109 | 0 | 13.1667 | 2.8 | 5.6 | 55 | 12.32
35 | 110 | 0 | 13.1667 | 2.8 | 5.7 | 55 | 12.38
35 | 111 | 0 | 13.1667 | 2.8 | 5.8 | 55 | 12.44
35 | 112 | 0 | 13.1667 | 2.8 | 5.9 | 55 | 12.5
35 | 113 | 0 | 13.1667 | 2.8 | 6 | 55 | 12.56
35 | 114 | 0 | 13.1667 | 2.8 | 6.1 | 55 | 12.62
35 | 115 | 0 | 13.1667 | 2.8 | 6.2 | 55 | 12.68
35 | 116 | 0 | 13.1667 | 2.8 | 6.3 | 55 | 12.74
35 | 117 | 0 | 13.1667 | 2.8 | 6.4 | 55 | 12.8
35 | 118 | 0 | 13.1667 | 2.8 | 6.5 | 55 | 12.86
35 | 119 | 0 | 13.1667 | 2.8 | 6.6 | 55 | 12.92
35 | 120 | 0 | 13.1667 | 2.8 | 6.7 | 55 | 12.98
35 | 121 | 0 | 13.1667 | 2.8 | 6.8 | 55 | 13.04
35 | 122 | 0 | 13.1667 | 2.8 | 6.9 | 55 | 13.1
35 | 123 | 0 | 13.1667 | 2.8 | 7 | 55 | 13.16
35 | 124 | 0 | 13.1667 | 2.8 | 7.1 | 55 | 13.211
35 | 125 | 0 | 13.1667 | 2.8 | 7.2 | 55 | 13.262
35 | 126 | 0 | 13.1667 | 2.8 | 7.3 | 55 | 13.313
35 | 127 | 0 | 13.1667 | 2.8 | 7.4 | 55 | 13.364
35 | 128 | 0 | 13.1667 | 2.8 | 7.5 | 55 | 13.415
35 | 129 | 0 | 13.1667 | 2.8 | 7.6 | 55 | 13.466
35 | 130 | 0 | 13.1667 | 2.8 | 7.7 | 55 | 13.517
35 | 131 | 0 | 13.1667 | 2.8 | 7.8 | 55 | 13.568
35 | 132 | 0 | 13.1667 | 2.8 | 7.9 | 55 | 13.619
35 | 133 | 0 | 13.1667 | 2.8 | 8 | 55 | 13.67
35 | 134 | 0 | 13.1667 | 2.8 | 8.1 | 55 | 13.721
35 | 135 | 0 | 13.1667 | 2.8 | 8.2 | 55 | 13.772
35 | 136 | 0 | 13.1667 | 2.8 | 8.3 | 55 | 13.823
35 | 137 | 0 | 13.1667 | 2.8 | 8.4 | 55 | 13.874
35 | 138 | 0 | 13.1667 | 2.8 | 8.5 | 55 | 13.925
35 | 139 | 0 | 13.1667 | 2.8 | 8.6 | 55 | 13.976
35 | 140 | 0 | 13.1667 | 2.8 | 8.7 | 55 | 14.027
35 | 141 | 0 | 13.1667 | 2.8 | 8.8 | 55 | 14.078
35 | 142 | 0 | 13.1667 | 2.8 | 8.9 | 55 | 14.129
35 | 143 | 0 | 13.1667 | 2.8 | 9 | 55 | 14.18
35 | 144 | 0 | 13.1667 | 2.8 | 9.1 | 55 | 14.29
35 | 145 | 0 | 13.1667 | 2.8 | 9.2 | 55 | 14.4
35 | 146 | 0 | 13.1667 | 2.8 | 9.3 | 55 | 14.51
35 | 147 | 0 | 13.1667 | 2.8 | 9.4 | 55 | 14.62
35 | 148 | 0 | 13.1667 | 2.8 | 9.5 | 55 | 14.73
35 | 149 | 0 | 13.1667 | 2.8 | 9.6 | 55 | 14.84
35 | 150 | 0 | 13.1667 | 2.8 | 9.7 | 55 | 14.95
36 | 45 | 0 | 13.18 | 2.8 | 9.8 | 55 | 15.06
36 | 46 | 0 | 13.18 | 2.8 | 9.9 | 55 | 15.17
36 | 47 | 0 | 13.18 | 2.8 | 10 | 55 | 15.28
36 | 48 | 0 | 13.18 | 2.9 | 3 | 55 | 10
36 | 49 | 0 | 13.18 | 2.9 | 3.1 | 55 | 10.099
36 | 50 | 0 | 13.18 | 2.9 | 3.2 | 55 | 10.198
36 | 51 | 0 | 13.18 | 2.9 | 3.3 | 55 | 10.297
36 | 52 | 0 | 13.18 | 2.9 | 3.4 | 55 | 10.396
36 | 53 | 0 | 13.18 | 2.9 | 3.5 | 55 | 10.495
36 | 54 | 0 | 13.18 | 2.9 | 3.6 | 55 | 10.594
36 | 55 | 0 | 13.18 | 2.9 | 3.7 | 55 | 10.693
36 | 56 | 0 | 13.18 | 2.9 | 3.8 | 55 | 10.792
36 | 57 | 0 | 13.18 | 2.9 | 3.9 | 55 | 10.891
36 | 58 | 0 | 13.18 | 2.9 | 4 | 55 | 10.99
36 | 59 | 0 | 13.18 | 2.9 | 4.1 | 55 | 11.089
36 | 60 | 0 | 13.18 | 2.9 | 4.2 | 55 | 11.188
36 | 61 | 0 | 13.18 | 2.9 | 4.3 | 55 | 11.287
36 | 62 | 0 | 13.18 | 2.9 | 4.4 | 55 | 11.386
36 | 63 | 0 | 13.18 | 2.9 | 4.5 | 55 | 11.485
36 | 64 | 0 | 13.18 | 2.9 | 4.6 | 55 | 11.584
36 | 65 | 0 | 13.18 | 2.9 | 4.7 | 55 | 11.683
36 | 66 | 0 | 13.18 | 2.9 | 4.8 | 55 | 11.782
36 | 67 | 0 | 13.18 | 2.9 | 4.9 | 55 | 11.881
36 | 68 | 0 | 13.18 | 2.9 | 5 | 55 | 11.98
36 | 69 | 0 | 13.18 | 2.9 | 5.1 | 55 | 12.04
36 | 70 | 0 | 13.18 | 2.9 | 5.2 | 55 | 12.1
36 | 71 | 0 | 13.18 | 2.9 | 5.3 | 55 | 12.16
36 | 72 | 0 | 13.18 | 2.9 | 5.4 | 55 | 12.22
36 | 73 | 0 | 13.18 | 2.9 | 5.5 | 55 | 12.28
36 | 74 | 0 | 13.18 | 2.9 | 5.6 | 55 | 12.34
36 | 75 | 0 | 13.18 | 2.9 | 5.7 | 55 | 12.4
36 | 76 | 0 | 13.18 | 2.9 | 5.8 | 55 | 12.46
36 | 77 | 0 | 13.18 | 2.9 | 5.9 | 55 | 12.52
36 | 78 | 0 | 13.18 | 2.9 | 6 | 55 | 12.58
36 | 79 | 0 | 13.18 | 2.9 | 6.1 | 55 | 12.64
36 | 80 | 0 | 13.18 | 2.9 | 6.2 | 55 | 12.7
36 | 81 | 0 | 13.18 | 2.9 | 6.3 | 55 | 12.76
36 | 82 | 0 | 13.18 | 2.9 | 6.4 | 55 | 12.82
36 | 83 | 0 | 13.18 | 2.9 | 6.5 | 55 | 12.88
36 | 84 | 0 | 13.18 | 2.9 | 6.6 | 55 | 12.94
36 | 85 | 0 | 13.18 | 2.9 | 6.7 | 55 | 13
36 | 86 | 0 | 13.18 | 2.9 | 6.8 | 55 | 13.06
36 | 87 | 0 | 13.18 | 2.9 | 6.9 | 55 | 13.12
36 | 88 | 0 | 13.18 | 2.9 | 7 | 55 | 13.18
36 | 89 | 0 | 13.18 | 2.9 | 7.1 | 55 | 13.2305
36 | 90 | 0 | 13.18 | 2.9 | 7.2 | 55 | 13.281
36 | 91 | 0 | 13.18 | 2.9 | 7.3 | 55 | 13.3315
36 | 92 | 0 | 13.18 | 2.9 | 7.4 | 55 | 13.382
36 | 93 | 0 | 13.18 | 2.9 | 7.5 | 55 | 13.4325
36 | 94 | 0 | 13.18 | 2.9 | 7.6 | 55 | 13.483
36 | 95 | 0 | 13.18 | 2.9 | 7.7 | 55 | 13.5335
36 | 96 | 0 | 13.18 | 2.9 | 7.8 | 55 | 13.584
36 | 97 | 0 | 13.18 | 2.9 | 7.9 | 55 | 13.6345
36 | 98 | 0 | 13.18 | 2.9 | 8 | 55 | 13.685
36 | 99 | 0 | 13.18 | 2.9 | 8.1 | 55 | 13.7355
36 | 100 | 0 | 13.18 | 2.9 | 8.2 | 55 | 13.786
36 | 101 | 0 | 13.18 | 2.9 | 8.3 | 55 | 13.8365
36 | 102 | 0 | 13.18 | 2.9 | 8.4 | 55 | 13.887
36 | 103 | 0 | 13.18 | 2.9 | 8.5 | 55 | 13.9375
36 | 104 | 0 | 13.18 | 2.9 | 8.6 | 55 | 13.988
36 | 105 | 0 | 13.18 | 2.9 | 8.7 | 55 | 14.0385
36 | 106 | 0 | 13.18 | 2.9 | 8.8 | 55 | 14.089
36 | 107 | 0 | 13.18 | 2.9 | 8.9 | 55 | 14.1395
36 | 108 | 0 | 13.18 | 2.9 | 9 | 55 | 14.19
36 | 109 | 0 | 13.18 | 2.9 | 9.1 | 55 | 14.3
36 | 110 | 0 | 13.18 | 2.9 | 9.2 | 55 | 14.41
36 | 111 | 0 | 13.18 | 2.9 | 9.3 | 55 | 14.52
36 | 112 | 0 | 13.18 | 2.9 | 9.4 | 55 | 14.63
36 | 113 | 0 | 13.18 | 2.9 | 9.5 | 55 | 14.74
36 | 114 | 0 | 13.18 | 2.9 | 9.6 | 55 | 14.85
36 | 115 | 0 | 13.18 | 2.9 | 9.7 | 55 | 14.96
36 | 116 | 0 | 13.18 | 2.9 | 9.8 | 55 | 15.07
36 | 117 | 0 | 13.18 | 2.9 | 9.9 | 55 | 15.18
36 | 118 | 0 | 13.18 | 2.9 | 10 | 55 | 15.29
36 | 119 | 0 | 13.18 | 3 | 3 | 55 | 10
36 | 120 | 0 | 13.18 | 3 | 3.1 | 55 | 10.1
36 | 121 | 0 | 13.18 | 3 | 3.2 | 55 | 10.2
36 | 122 | 0 | 13.18 | 3 | 3.3 | 55 | 10.3
36 | 123 | 0 | 13.18 | 3 | 3.4 | 55 | 10.4
36 | 124 | 0 | 13.18 | 3 | 3.5 | 55 | 10.5
36 | 125 | 0 | 13.18 | 3 | 3.6 | 55 | 10.6
36 | 126 | 0 | 13.18 | 3 | 3.7 | 55 | 10.7
36 | 127 | 0 | 13.18 | 3 | 3.8 | 55 | 10.8
36 | 128 | 0 | 13.18 | 3 | 3.9 | 55 | 10.9
36 | 129 | 0 | 13.18 | 3 | 4 | 55 | 11
36 | 130 | 0 | 13.18 | 3 | 4.1 | 55 | 11.1
36 | 131 | 0 | 13.18 | 3 | 4.2 | 55 | 11.2
36 | 132 | 0 | 13.18 | 3 | 4.3 | 55 | 11.3
36 | 133 | 0 | 13.18 | 3 | 4.4 | 55 | 11.4
36 | 134 | 0 | 13.18 | 3 | 4.5 | 55 | 11.5
36 | 135 | 0 | 13.18 | 3 | 4.6 | 55 | 11.6
36 | 136 | 0 | 13.18 | 3 | 4.7 | 55 | 11.7
36 | 137 | 0 | 13.18 | 3 | 4.8 | 55 | 11.8
36 | 138 | 0 | 13.18 | 3 | 4.9 | 55 | 11.9
36 | 139 | 0 | 13.18 | 3 | 5 | 55 | 12
36 | 140 | 0 | 13.18 | 3 | 5.1 | 55 | 12.06
36 | 141 | 0 | 13.18 | 3 | 5.2 | 55 | 12.12
36 | 142 | 0 | 13.18 | 3 | 5.3 | 55 | 12.18
36 | 143 | 0 | 13.18 | 3 | 5.4 | 55 | 12.24
36 | 144 | 0 | 13.18 | 3 | 5.5 | 55 | 12.3
36 | 145 | 0 | 13.18 | 3 | 5.6 | 55 | 12.36
36 | 146 | 0 | 13.18 | 3 | 5.7 | 55 | 12.42
36 | 147 | 0 | 13.18 | 3 | 5.8 | 55 | 12.48
36 | 148 | 0 | 13.18 | 3 | 5.9 | 55 | 12.54
36 | 149 | 0 | 13.18 | 3 | 6 | 55 | 12.6
36 | 150 | 0 | 13.18 | 3 | 6.1 | 55 | 12.66
37 | 45 | 0 | 13.1933 | 3 | 6.2 | 55 | 12.72
37 | 46 | 0 | 13.1933 | 3 | 6.3 | 55 | 12.78
37 | 47 | 0 | 13.1933 | 3 | 6.4 | 55 | 12.84
37 | 48 | 0 | 13.1933 | 3 | 6.5 | 55 | 12.9
37 | 49 | 0 | 13.1933 | 3 | 6.6 | 55 | 12.96
37 | 50 | 0 | 13.1933 | 3 | 6.7 | 55 | 13.02
37 | 51 | 0 | 13.1933 | 3 | 6.8 | 55 | 13.08
37 | 52 | 0 | 13.1933 | 3 | 6.9 | 55 | 13.14
37 | 53 | 0 | 13.1933 | 3 | 7 | 55 | 13.2
37 | 54 | 0 | 13.1933 | 3 | 7.1 | 55 | 13.25
37 | 55 | 0 | 13.1933 | 3 | 7.2 | 55 | 13.3
37 | 56 | 0 | 13.1933 | 3 | 7.3 | 55 | 13.35
37 | 57 | 0 | 13.1933 | 3 | 7.4 | 55 | 13.4
37 | 58 | 0 | 13.1933 | 3 | 7.5 | 55 | 13.45
37 | 59 | 0 | 13.1933 | 3 | 7.6 | 55 | 13.5
37 | 60 | 0 | 13.1933 | 3 | 7.7 | 55 | 13.55
37 | 61 | 0 | 13.1933 | 3 | 7.8 | 55 | 13.6
37 | 62 | 0 | 13.1933 | 3 | 7.9 | 55 | 13.65
37 | 63 | 0 | 13.1933 | 3 | 8 | 55 | 13.7
37 | 64 | 0 | 13.1933 | 3 | 8.1 | 55 | 13.75
37 | 65 | 0 | 13.1933 | 3 | 8.2 | 55 | 13.8
37 | 66 | 0 | 13.1933 | 3 | 8.3 | 55 | 13.85
37 | 67 | 0 | 13.1933 | 3 | 8.4 | 55 | 13.9
37 | 68 | 0 | 13.1933 | 3 | 8.5 | 55 | 13.95
37 | 69 | 0 | 13.1933 | 3 | 8.6 | 55 | 14
37 | 70 | 0 | 13.1933 | 3 | 8.7 | 55 | 14.05
37 | 71 | 0 | 13.1933 | 3 | 8.8 | 55 | 14.1
37 | 72 | 0 | 13.1933 | 3 | 8.9 | 55 | 14.15
37 | 73 | 0 | 13.1933 | 3 | 9 | 55 | 14.2
37 | 74 | 0 | 13.1933 | 3 | 9.1 | 55 | 14.31
37 | 75 | 0 | 13.1933 | 3 | 9.2 | 55 | 14.42
37 | 76 | 0 | 13.1933 | 3 | 9.3 | 55 | 14.53
37 | 77 | 0 | 13.1933 | 3 | 9.4 | 55 | 14.64
37 | 78 | 0 | 13.1933 | 3 | 9.5 | 55 | 14.75
37 | 79 | 0 | 13.1933 | 3 | 9.6 | 55 | 14.86
37 | 80 | 0 | 13.1933 | 3 | 9.7 | 55 | 14.97
37 | 81 | 0 | 13.1933 | 3 | 9.8 | 55 | 15.08
37 | 82 | 0 | 13.1933 | 3 | 9.9 | 55 | 15.19
37 | 83 | 0 | 13.1933 | 3 | 10 | 55 | 15.3
37 | 84 | 0 | 13.1933 | 3.1 | 3 | 55 | 10.02
37 | 85 | 0 | 13.1933 | 3.1 | 3.1 | 55 | 10.1195
37 | 86 | 0 | 13.1933 | 3.1 | 3.2 | 55 | 10.219
37 | 87 | 0 | 13.1933 | 3.1 | 3.3 | 55 | 10.3185
37 | 88 | 0 | 13.1933 | 3.1 | 3.4 | 55 | 10.418
37 | 89 | 0 | 13.1933 | 3.1 | 3.5 | 55 | 10.5175
37 | 90 | 0 | 13.1933 | 3.1 | 3.6 | 55 | 10.617
37 | 91 | 0 | 13.1933 | 3.1 | 3.7 | 55 | 10.7165
37 | 92 | 0 | 13.1933 | 3.1 | 3.8 | 55 | 10.816
37 | 93 | 0 | 13.1933 | 3.1 | 3.9 | 55 | 10.9155
37 | 94 | 0 | 13.1933 | 3.1 | 4 | 55 | 11.015
37 | 95 | 0 | 13.1933 | 3.1 | 4.1 | 55 | 11.1145
37 | 96 | 0 | 13.1933 | 3.1 | 4.2 | 55 | 11.214
37 | 97 | 0 | 13.1933 | 3.1 | 4.3 | 55 | 11.3135
37 | 98 | 0 | 13.1933 | 3.1 | 4.4 | 55 | 11.413
37 | 99 | 0 | 13.1933 | 3.1 | 4.5 | 55 | 11.5125
37 | 100 | 0 | 13.1933 | 3.1 | 4.6 | 55 | 11.612
37 | 101 | 0 | 13.1933 | 3.1 | 4.7 | 55 | 11.7115
37 | 102 | 0 | 13.1933 | 3.1 | 4.8 | 55 | 11.811
37 | 103 | 0 | 13.1933 | 3.1 | 4.9 | 55 | 11.9105
37 | 104 | 0 | 13.1933 | 3.1 | 5 | 55 | 12.01
37 | 105 | 0 | 13.1933 | 3.1 | 5.1 | 55 | 12.0735
37 | 106 | 0 | 13.1933 | 3.1 | 5.2 | 55 | 12.137
37 | 107 | 0 | 13.1933 | 3.1 | 5.3 | 55 | 12.2005
37 | 108 | 0 | 13.1933 | 3.1 | 5.4 | 55 | 12.264
37 | 109 | 0 | 13.1933 | 3.1 | 5.5 | 55 | 12.3275
37 | 110 | 0 | 13.1933 | 3.1 | 5.6 | 55 | 12.391
37 | 111 | 0 | 13.1933 | 3.1 | 5.7 | 55 | 12.4545
37 | 112 | 0 | 13.1933 | 3.1 | 5.8 | 55 | 12.518
37 | 113 | 0 | 13.1933 | 3.1 | 5.9 | 55 | 12.5815
37 | 114 | 0 | 13.1933 | 3.1 | 6 | 55 | 12.645
37 | 115 | 0 | 13.1933 | 3.1 | 6.1 | 55 | 12.7085
37 | 116 | 0 | 13.1933 | 3.1 | 6.2 | 55 | 12.772
37 | 117 | 0 | 13.1933 | 3.1 | 6.3 | 55 | 12.8355
37 | 118 | 0 | 13.1933 | 3.1 | 6.4 | 55 | 12.899
37 | 119 | 0 | 13.1933 | 3.1 | 6.5 | 55 | 12.9625
37 | 120 | 0 | 13.1933 | 3.1 | 6.6 | 55 | 13.026
37 | 121 | 0 | 13.1933 | 3.1 | 6.7 | 55 | 13.0895
37 | 122 | 0 | 13.1933 | 3.1 | 6.8 | 55 | 13.153
37 | 123 | 0 | 13.1933 | 3.1 | 6.9 | 55 | 13.2165
37 | 124 | 0 | 13.1933 | 3.1 | 7 | 55 | 13.28
37 | 125 | 0 | 13.1933 | 3.1 | 7.1 | 55 | 13.3265
37 | 126 | 0 | 13.1933 | 3.1 | 7.2 | 55 | 13.373
37 | 127 | 0 | 13.1933 | 3.1 | 7.3 | 55 | 13.4195
37 | 128 | 0 | 13.1933 | 3.1 | 7.4 | 55 | 13.466
37 | 129 | 0 | 13.1933 | 3.1 | 7.5 | 55 | 13.5125
37 | 130 | 0 | 13.1933 | 3.1 | 7.6 | 55 | 13.559
37 | 131 | 0 | 13.1933 | 3.1 | 7.7 | 55 | 13.6055
37 | 132 | 0 | 13.1933 | 3.1 | 7.8 | 55 | 13.652
37 | 133 | 0 | 13.1933 | 3.1 | 7.9 | 55 | 13.6985
37 | 134 | 0 | 13.1933 | 3.1 | 8 | 55 | 13.745
37 | 135 | 0 | 13.1933 | 3.1 | 8.1 | 55 | 13.7915
37 | 136 | 0 | 13.1933 | 3.1 | 8.2 | 55 | 13.838
37 | 137 | 0 | 13.1933 | 3.1 | 8.3 | 55 | 13.8845
37 | 138 | 0 | 13.1933 | 3.1 | 8.4 | 55 | 13.931
37 | 139 | 0 | 13.1933 | 3.1 | 8.5 | 55 | 13.9775
37 | 140 | 0 | 13.1933 | 3.1 | 8.6 | 55 | 14.024
37 | 141 | 0 | 13.1933 | 3.1 | 8.7 | 55 | 14.0705
37 | 142 | 0 | 13.1933 | 3.1 | 8.8 | 55 | 14.117
37 | 143 | 0 | 13.1933 | 3.1 | 8.9 | 55 | 14.1635
37 | 144 | 0 | 13.1933 | 3.1 | 9 | 55 | 14.21
37 | 145 | 0 | 13.1933 | 3.1 | 9.1 | 55 | 14.322
37 | 146 | 0 | 13.1933 | 3.1 | 9.2 | 55 | 14.434
37 | 147 | 0 | 13.1933 | 3.1 | 9.3 | 55 | 14.546
37 | 148 | 0 | 13.1933 | 3.1 | 9.4 | 55 | 14.658
37 | 149 | 0 | 13.1933 | 3.1 | 9.5 | 55 | 14.77
37 | 150 | 0 | 13.1933 | 3.1 | 9.6 | 55 | 14.882
38 | 45 | 0 | 13.2067 | 3.1 | 9.7 | 55 | 14.994
38 | 46 | 0 | 13.2067 | 3.1 | 9.8 | 55 | 15.106
38 | 47 | 0 | 13.2067 | 3.1 | 9.9 | 55 | 15.218
38 | 48 | 0 | 13.2067 | 3.1 | 10 | 55 | 15.33
38 | 49 | 0 | 13.2067 | 3.2 | 3 | 55 | 10.04
38 | 50 | 0 | 13.2067 | 3.2 | 3.1 | 55 | 10.139
38 | 51 | 0 | 13.2067 | 3.2 | 3.2 | 55 | 10.238
38 | 52 | 0 | 13.2067 | 3.2 | 3.3 | 55 | 10.337
38 | 53 | 0 | 13.2067 | 3.2 | 3.4 | 55 | 10.436
38 | 54 | 0 | 13.2067 | 3.2 | 3.5 | 55 | 10.535
38 | 55 | 0 | 13.2067 | 3.2 | 3.6 | 55 | 10.634
38 | 56 | 0 | 13.2067 | 3.2 | 3.7 | 55 | 10.733
38 | 57 | 0 | 13.2067 | 3.2 | 3.8 | 55 | 10.832
38 | 58 | 0 | 13.2067 | 3.2 | 3.9 | 55 | 10.931
38 | 59 | 0 | 13.2067 | 3.2 | 4 | 55 | 11.03
38 | 60 | 0 | 13.2067 | 3.2 | 4.1 | 55 | 11.129
38 | 61 | 0 | 13.2067 | 3.2 | 4.2 | 55 | 11.228
38 | 62 | 0 | 13.2067 | 3.2 | 4.3 | 55 | 11.327
38 | 63 | 0 | 13.2067 | 3.2 | 4.4 | 55 | 11.426
38 | 64 | 0 | 13.2067 | 3.2 | 4.5 | 55 | 11.525
38 | 65 | 0 | 13.2067 | 3.2 | 4.6 | 55 | 11.624
38 | 66 | 0 | 13.2067 | 3.2 | 4.7 | 55 | 11.723
38 | 67 | 0 | 13.2067 | 3.2 | 4.8 | 55 | 11.822
38 | 68 | 0 | 13.2067 | 3.2 | 4.9 | 55 | 11.921
38 | 69 | 0 | 13.2067 | 3.2 | 5 | 55 | 12.02
38 | 70 | 0 | 13.2067 | 3.2 | 5.1 | 55 | 12.087
38 | 71 | 0 | 13.2067 | 3.2 | 5.2 | 55 | 12.154
38 | 72 | 0 | 13.2067 | 3.2 | 5.3 | 55 | 12.221
38 | 73 | 0 | 13.2067 | 3.2 | 5.4 | 55 | 12.288
38 | 74 | 0 | 13.2067 | 3.2 | 5.5 | 55 | 12.355
38 | 75 | 0 | 13.2067 | 3.2 | 5.6 | 55 | 12.422
38 | 76 | 0 | 13.2067 | 3.2 | 5.7 | 55 | 12.489
38 | 77 | 0 | 13.2067 | 3.2 | 5.8 | 55 | 12.556
38 | 78 | 0 | 13.2067 | 3.2 | 5.9 | 55 | 12.623
38 | 79 | 0 | 13.2067 | 3.2 | 6 | 55 | 12.69
38 | 80 | 0 | 13.2067 | 3.2 | 6.1 | 55 | 12.757
38 | 81 | 0 | 13.2067 | 3.2 | 6.2 | 55 | 12.824
38 | 82 | 0 | 13.2067 | 3.2 | 6.3 | 55 | 12.891
38 | 83 | 0 | 13.2067 | 3.2 | 6.4 | 55 | 12.958
38 | 84 | 0 | 13.2067 | 3.2 | 6.5 | 55 | 13.025
38 | 85 | 0 | 13.2067 | 3.2 | 6.6 | 55 | 13.092
38 | 86 | 0 | 13.2067 | 3.2 | 6.7 | 55 | 13.159
38 | 87 | 0 | 13.2067 | 3.2 | 6.8 | 55 | 13.226
38 | 88 | 0 | 13.2067 | 3.2 | 6.9 | 55 | 13.293
38 | 89 | 0 | 13.2067 | 3.2 | 7 | 55 | 13.36
38 | 90 | 0 | 13.2067 | 3.2 | 7.1 | 55 | 13.403
38 | 91 | 0 | 13.2067 | 3.2 | 7.2 | 55 | 13.446
38 | 92 | 0 | 13.2067 | 3.2 | 7.3 | 55 | 13.489
38 | 93 | 0 | 13.2067 | 3.2 | 7.4 | 55 | 13.532
38 | 94 | 0 | 13.2067 | 3.2 | 7.5 | 55 | 13.575
38 | 95 | 0 | 13.2067 | 3.2 | 7.6 | 55 | 13.618
38 | 96 | 0 | 13.2067 | 3.2 | 7.7 | 55 | 13.661
38 | 97 | 0 | 13.2067 | 3.2 | 7.8 | 55 | 13.704
38 | 98 | 0 | 13.2067 | 3.2 | 7.9 | 55 | 13.747
38 | 99 | 0 | 13.2067 | 3.2 | 8 | 55 | 13.79
38 | 100 | 0 | 13.2067 | 3.2 | 8.1 | 55 | 13.833
38 | 101 | 0 | 13.2067 | 3.2 | 8.2 | 55 | 13.876
38 | 102 | 0 | 13.2067 | 3.2 | 8.3 | 55 | 13.919
38 | 103 | 0 | 13.2067 | 3.2 | 8.4 | 55 | 13.962
38 | 104 | 0 | 13.2067 | 3.2 | 8.5 | 55 | 14.005
38 | 105 | 0 | 13.2067 | 3.2 | 8.6 | 55 | 14.048
38 | 106 | 0 | 13.2067 | 3.2 | 8.7 | 55 | 14.091
38 | 107 | 0 | 13.2067 | 3.2 | 8.8 | 55 | 14.134
38 | 108 | 0 | 13.2067 | 3.2 | 8.9 | 55 | 14.177
38 | 109 | 0 | 13.2067 | 3.2 | 9 | 55 | 14.22
38 | 110 | 0 | 13.2067 | 3.2 | 9.1 | 55 | 14.334
38 | 111 | 0 | 13.2067 | 3.2 | 9.2 | 55 | 14.448
38 | 112 | 0 | 13.2067 | 3.2 | 9.3 | 55 | 14.562
38 | 113 | 0 | 13.2067 | 3.2 | 9.4 | 55 | 14.676
38 | 114 | 0 | 13.2067 | 3.2 | 9.5 | 55 | 14.79
38 | 115 | 0 | 13.2067 | 3.2 | 9.6 | 55 | 14.904
38 | 116 | 0 | 13.2067 | 3.2 | 9.7 | 55 | 15.018
38 | 117 | 0 | 13.2067 | 3.2 | 9.8 | 55 | 15.132
38 | 118 | 0 | 13.2067 | 3.2 | 9.9 | 55 | 15.246
38 | 119 | 0 | 13.2067 | 3.2 | 10 | 55 | 15.36
38 | 120 | 0 | 13.2067 | 3.3 | 3 | 55 | 10.06
38 | 121 | 0 | 13.2067 | 3.3 | 3.1 | 55 | 10.1585
38 | 122 | 0 | 13.2067 | 3.3 | 3.2 | 55 | 10.257
38 | 123 | 0 | 13.2067 | 3.3 | 3.3 | 55 | 10.3555
38 | 124 | 0 | 13.2067 | 3.3 | 3.4 | 55 | 10.454
38 | 125 | 0 | 13.2067 | 3.3 | 3.5 | 55 | 10.5525
38 | 126 | 0 | 13.2067 | 3.3 | 3.6 | 55 | 10.651
38 | 127 | 0 | 13.2067 | 3.3 | 3.7 | 55 | 10.7495
38 | 128 | 0 | 13.2067 | 3.3 | 3.8 | 55 | 10.848
38 | 129 | 0 | 13.2067 | 3.3 | 3.9 | 55 | 10.9465
38 | 130 | 0 | 13.2067 | 3.3 | 4 | 55 | 11.045
38 | 131 | 0 | 13.2067 | 3.3 | 4.1 | 55 | 11.1435
38 | 132 | 0 | 13.2067 | 3.3 | 4.2 | 55 | 11.242
38 | 133 | 0 | 13.2067 | 3.3 | 4.3 | 55 | 11.3405
38 | 134 | 0 | 13.2067 | 3.3 | 4.4 | 55 | 11.439
38 | 135 | 0 | 13.2067 | 3.3 | 4.5 | 55 | 11.5375
38 | 136 | 0 | 13.2067 | 3.3 | 4.6 | 55 | 11.636
38 | 137 | 0 | 13.2067 | 3.3 | 4.7 | 55 | 11.7345
38 | 138 | 0 | 13.2067 | 3.3 | 4.8 | 55 | 11.833
38 | 139 | 0 | 13.2067 | 3.3 | 4.9 | 55 | 11.9315
38 | 140 | 0 | 13.2067 | 3.3 | 5 | 55 | 12.03
38 | 141 | 0 | 13.2067 | 3.3 | 5.1 | 55 | 12.1005
38 | 142 | 0 | 13.2067 | 3.3 | 5.2 | 55 | 12.171
38 | 143 | 0 | 13.2067 | 3.3 | 5.3 | 55 | 12.2415
38 | 144 | 0 | 13.2067 | 3.3 | 5.4 | 55 | 12.312
38 | 145 | 0 | 13.2067 | 3.3 | 5.5 | 55 | 12.3825
38 | 146 | 0 | 13.2067 | 3.3 | 5.6 | 55 | 12.453
38 | 147 | 0 | 13.2067 | 3.3 | 5.7 | 55 | 12.5235
38 | 148 | 0 | 13.2067 | 3.3 | 5.8 | 55 | 12.594
38 | 149 | 0 | 13.2067 | 3.3 | 5.9 | 55 | 12.6645
38 | 150 | 0 | 13.2067 | 3.3 | 6 | 55 | 12.735
39 | 45 | 0 | 13.22 | 3.3 | 6.1 | 55 | 12.8055
39 | 46 | 0 | 13.22 | 3.3 | 6.2 | 55 | 12.876
39 | 47 | 0 | 13.22 | 3.3 | 6.3 | 55 | 12.9465
39 | 48 | 0 | 13.22 | 3.3 | 6.4 | 55 | 13.017
39 | 49 | 0 | 13.22 | 3.3 | 6.5 | 55 | 13.0875
39 | 50 | 0 | 13.22 | 3.3 | 6.6 | 55 | 13.158
39 | 51 | 0 | 13.22 | 3.3 | 6.7 | 55 | 13.2285
39 | 52 | 0 | 13.22 | 3.3 | 6.8 | 55 | 13.299
39 | 53 | 0 | 13.22 | 3.3 | 6.9 | 55 | 13.3695
39 | 54 | 0 | 13.22 | 3.3 | 7 | 55 | 13.44
39 | 55 | 0 | 13.22 | 3.3 | 7.1 | 55 | 13.4795
39 | 56 | 0 | 13.22 | 3.3 | 7.2 | 55 | 13.519
39 | 57 | 0 | 13.22 | 3.3 | 7.3 | 55 | 13.5585
39 | 58 | 0 | 13.22 | 3.3 | 7.4 | 55 | 13.598
39 | 59 | 0 | 13.22 | 3.3 | 7.5 | 55 | 13.6375
39 | 60 | 0 | 13.22 | 3.3 | 7.6 | 55 | 13.677
39 | 61 | 0 | 13.22 | 3.3 | 7.7 | 55 | 13.7165
39 | 62 | 0 | 13.22 | 3.3 | 7.8 | 55 | 13.756
39 | 63 | 0 | 13.22 | 3.3 | 7.9 | 55 | 13.7955
39 | 64 | 0 | 13.22 | 3.3 | 8 | 55 | 13.835
39 | 65 | 0 | 13.22 | 3.3 | 8.1 | 55 | 13.8745
39 | 66 | 0 | 13.22 | 3.3 | 8.2 | 55 | 13.914
39 | 67 | 0 | 13.22 | 3.3 | 8.3 | 55 | 13.9535
39 | 68 | 0 | 13.22 | 3.3 | 8.4 | 55 | 13.993
39 | 69 | 0 | 13.22 | 3.3 | 8.5 | 55 | 14.0325
39 | 70 | 0 | 13.22 | 3.3 | 8.6 | 55 | 14.072
39 | 71 | 0 | 13.22 | 3.3 | 8.7 | 55 | 14.1115
39 | 72 | 0 | 13.22 | 3.3 | 8.8 | 55 | 14.151
39 | 73 | 0 | 13.22 | 3.3 | 8.9 | 55 | 14.1905
39 | 74 | 0 | 13.22 | 3.3 | 9 | 55 | 14.23
39 | 75 | 0 | 13.22 | 3.3 | 9.1 | 55 | 14.346
39 | 76 | 0 | 13.22 | 3.3 | 9.2 | 55 | 14.462
39 | 77 | 0 | 13.22 | 3.3 | 9.3 | 55 | 14.578
39 | 78 | 0 | 13.22 | 3.3 | 9.4 | 55 | 14.694
39 | 79 | 0 | 13.22 | 3.3 | 9.5 | 55 | 14.81
39 | 80 | 0 | 13.22 | 3.3 | 9.6 | 55 | 14.926
39 | 81 | 0 | 13.22 | 3.3 | 9.7 | 55 | 15.042
39 | 82 | 0 | 13.22 | 3.3 | 9.8 | 55 | 15.158
39 | 83 | 0 | 13.22 | 3.3 | 9.9 | 55 | 15.274
39 | 84 | 0 | 13.22 | 3.3 | 10 | 55 | 15.39
39 | 85 | 0 | 13.22 | 3.4 | 3 | 55 | 10.08
39 | 86 | 0 | 13.22 | 3.4 | 3.1 | 55 | 10.178
39 | 87 | 0 | 13.22 | 3.4 | 3.2 | 55 | 10.276
39 | 88 | 0 | 13.22 | 3.4 | 3.3 | 55 | 10.374
39 | 89 | 0 | 13.22 | 3.4 | 3.4 | 55 | 10.472
39 | 90 | 0 | 13.22 | 3.4 | 3.5 | 55 | 10.57
39 | 91 | 0 | 13.22 | 3.4 | 3.6 | 55 | 10.668
39 | 92 | 0 | 13.22 | 3.4 | 3.7 | 55 | 10.766
39 | 93 | 0 | 13.22 | 3.4 | 3.8 | 55 | 10.864
39 | 94 | 0 | 13.22 | 3.4 | 3.9 | 55 | 10.962
39 | 95 | 0 | 13.22 | 3.4 | 4 | 55 | 11.06
39 | 96 | 0 | 13.22 | 3.4 | 4.1 | 55 | 11.158
39 | 97 | 0 | 13.22 | 3.4 | 4.2 | 55 | 11.256
39 | 98 | 0 | 13.22 | 3.4 | 4.3 | 55 | 11.354
39 | 99 | 0 | 13.22 | 3.4 | 4.4 | 55 | 11.452
39 | 100 | 0 | 13.22 | 3.4 | 4.5 | 55 | 11.55
39 | 101 | 0 | 13.22 | 3.4 | 4.6 | 55 | 11.648
39 | 102 | 0 | 13.22 | 3.4 | 4.7 | 55 | 11.746
39 | 103 | 0 | 13.22 | 3.4 | 4.8 | 55 | 11.844
39 | 104 | 0 | 13.22 | 3.4 | 4.9 | 55 | 11.942
39 | 105 | 0 | 13.22 | 3.4 | 5 | 55 | 12.04
39 | 106 | 0 | 13.22 | 3.4 | 5.1 | 55 | 12.114
39 | 107 | 0 | 13.22 | 3.4 | 5.2 | 55 | 12.188
39 | 108 | 0 | 13.22 | 3.4 | 5.3 | 55 | 12.262
39 | 109 | 0 | 13.22 | 3.4 | 5.4 | 55 | 12.336
39 | 110 | 0 | 13.22 | 3.4 | 5.5 | 55 | 12.41
39 | 111 | 0 | 13.22 | 3.4 | 5.6 | 55 | 12.484
39 | 112 | 0 | 13.22 | 3.4 | 5.7 | 55 | 12.558
39 | 113 | 0 | 13.22 | 3.4 | 5.8 | 55 | 12.632
39 | 114 | 0 | 13.22 | 3.4 | 5.9 | 55 | 12.706
39 | 115 | 0 | 13.22 | 3.4 | 6 | 55 | 12.78
39 | 116 | 0 | 13.22 | 3.4 | 6.1 | 55 | 12.854
39 | 117 | 0 | 13.22 | 3.4 | 6.2 | 55 | 12.928
39 | 118 | 0 | 13.22 | 3.4 | 6.3 | 55 | 13.002
39 | 119 | 0 | 13.22 | 3.4 | 6.4 | 55 | 13.076
39 | 120 | 0 | 13.22 | 3.4 | 6.5 | 55 | 13.15
39 | 121 | 0 | 13.22 | 3.4 | 6.6 | 55 | 13.224
39 | 122 | 0 | 13.22 | 3.4 | 6.7 | 55 | 13.298
39 | 123 | 0 | 13.22 | 3.4 | 6.8 | 55 | 13.372
39 | 124 | 0 | 13.22 | 3.4 | 6.9 | 55 | 13.446
39 | 125 | 0 | 13.22 | 3.4 | 7 | 55 | 13.52
39 | 126 | 0 | 13.22 | 3.4 | 7.1 | 55 | 13.556
39 | 127 | 0 | 13.22 | 3.4 | 7.2 | 55 | 13.592
39 | 128 | 0 | 13.22 | 3.4 | 7.3 | 55 | 13.628
39 | 129 | 0 | 13.22 | 3.4 | 7.4 | 55 | 13.664
39 | 130 | 0 | 13.22 | 3.4 | 7.5 | 55 | 13.7
39 | 131 | 0 | 13.22 | 3.4 | 7.6 | 55 | 13.736
39 | 132 | 0 | 13.22 | 3.4 | 7.7 | 55 | 13.772
39 | 133 | 0 | 13.22 | 3.4 | 7.8 | 55 | 13.808
39 | 134 | 0 | 13.22 | 3.4 | 7.9 | 55 | 13.844
39 | 135 | 0 | 13.22 | 3.4 | 8 | 55 | 13.88
39 | 136 | 0 | 13.22 | 3.4 | 8.1 | 55 | 13.916
39 | 137 | 0 | 13.22 | 3.4 | 8.2 | 55 | 13.952
39 | 138 | 0 | 13.22 | 3.4 | 8.3 | 55 | 13.988
39 | 139 | 0 | 13.22 | 3.4 | 8.4 | 55 | 14.024
39 | 140 | 0 | 13.22 | 3.4 | 8.5 | 55 | 14.06
39 | 141 | 0 | 13.22 | 3.4 | 8.6 | 55 | 14.096
39 | 142 | 0 | 13.22 | 3.4 | 8.7 | 55 | 14.132
39 | 143 | 0 | 13.22 | 3.4 | 8.8 | 55 | 14.168
39 | 144 | 0 | 13.22 | 3.4 | 8.9 | 55 | 14.204
39 | 145 | 0 | 13.22 | 3.4 | 9 | 55 | 14.24
39 | 146 | 0 | 13.22 | 3.4 | 9.1 | 55 | 14.358
39 | 147 | 0 | 13.22 | 3.4 | 9.2 | 55 | 14.476
39 | 148 | 0 | 13.22 | 3.4 | 9.3 | 55 | 14.594
39 | 149 | 0 | 13.22 | 3.4 | 9.4 | 55 | 14.712
39 | 150 | 0 | 13.22 | 3.4 | 9.5 | 55 | 14.83
40 | 45 | 0 | 13.2333 | 3.4 | 9.6 | 55 | 14.948
40 | 46 | 0 | 13.2333 | 3.4 | 9.7 | 55 | 15.066
40 | 47 | 0 | 13.2333 | 3.4 | 9.8 | 55 | 15.184
40 | 48 | 0 | 13.2333 | 3.4 | 9.9 | 55 | 15.302
40 | 49 | 0 | 13.2333 | 3.4 | 10 | 55 | 15.42
40 | 50 | 0 | 13.2333 | 3.5 | 3 | 55 | 10.1
40 | 51 | 0 | 13.2333 | 3.5 | 3.1 | 55 | 10.1975
40 | 52 | 0 | 13.2333 | 3.5 | 3.2 | 55 | 10.295
40 | 53 | 0 | 13.2333 | 3.5 | 3.3 | 55 | 10.3925
40 | 54 | 0 | 13.2333 | 3.5 | 3.4 | 55 | 10.49
40 | 55 | 0 | 13.2333 | 3.5 | 3.5 | 55 | 10.5875
40 | 56 | 0 | 13.2333 | 3.5 | 3.6 | 55 | 10.685
40 | 57 | 0 | 13.2333 | 3.5 | 3.7 | 55 | 10.7825
40 | 58 | 0 | 13.2333 | 3.5 | 3.8 | 55 | 10.88
40 | 59 | 0 | 13.2333 | 3.5 | 3.9 | 55 | 10.9775
40 | 60 | 0 | 13.2333 | 3.5 | 4 | 55 | 11.075
40 | 61 | 0 | 13.2333 | 3.5 | 4.1 | 55 | 11.1725
40 | 62 | 0 | 13.2333 | 3.5 | 4.2 | 55 | 11.27
40 | 63 | 0 | 13.2333 | 3.5 | 4.3 | 55 | 11.3675
40 | 64 | 0 | 13.2333 | 3.5 | 4.4 | 55 | 11.465
40 | 65 | 0 | 13.2333 | 3.5 | 4.5 | 55 | 11.5625
40 | 66 | 0 | 13.2333 | 3.5 | 4.6 | 55 | 11.66
40 | 67 | 0 | 13.2333 | 3.5 | 4.7 | 55 | 11.7575
40 | 68 | 0 | 13.2333 | 3.5 | 4.8 | 55 | 11.855
40 | 69 | 0 | 13.2333 | 3.5 | 4.9 | 55 | 11.9525
40 | 70 | 0 | 13.2333 | 3.5 | 5 | 55 | 12.05
40 | 71 | 0 | 13.2333 | 3.5 | 5.1 | 55 | 12.1275
40 | 72 | 0 | 13.2333 | 3.5 | 5.2 | 55 | 12.205
40 | 73 | 0 | 13.2333 | 3.5 | 5.3 | 55 | 12.2825
40 | 74 | 0 | 13.2333 | 3.5 | 5.4 | 55 | 12.36
40 | 75 | 0 | 13.2333 | 3.5 | 5.5 | 55 | 12.4375
40 | 76 | 0 | 13.2333 | 3.5 | 5.6 | 55 | 12.515
40 | 77 | 0 | 13.2333 | 3.5 | 5.7 | 55 | 12.5925
40 | 78 | 0 | 13.2333 | 3.5 | 5.8 | 55 | 12.67
40 | 79 | 0 | 13.2333 | 3.5 | 5.9 | 55 | 12.7475
40 | 80 | 0 | 13.2333 | 3.5 | 6 | 55 | 12.825
40 | 81 | 0 | 13.2333 | 3.5 | 6.1 | 55 | 12.9025
40 | 82 | 0 | 13.2333 | 3.5 | 6.2 | 55 | 12.98
40 | 83 | 0 | 13.2333 | 3.5 | 6.3 | 55 | 13.0575
40 | 84 | 0 | 13.2333 | 3.5 | 6.4 | 55 | 13.135
40 | 85 | 0 | 13.2333 | 3.5 | 6.5 | 55 | 13.2125
40 | 86 | 0 | 13.2333 | 3.5 | 6.6 | 55 | 13.29
40 | 87 | 0 | 13.2333 | 3.5 | 6.7 | 55 | 13.3675
40 | 88 | 0 | 13.2333 | 3.5 | 6.8 | 55 | 13.445
40 | 89 | 0 | 13.2333 | 3.5 | 6.9 | 55 | 13.5225
40 | 90 | 0 | 13.2333 | 3.5 | 7 | 55 | 13.6
40 | 91 | 0 | 13.2333 | 3.5 | 7.1 | 55 | 13.6325
40 | 92 | 0 | 13.2333 | 3.5 | 7.2 | 55 | 13.665
40 | 93 | 0 | 13.2333 | 3.5 | 7.3 | 55 | 13.6975
40 | 94 | 0 | 13.2333 | 3.5 | 7.4 | 55 | 13.73
40 | 95 | 0 | 13.2333 | 3.5 | 7.5 | 55 | 13.7625
40 | 96 | 0 | 13.2333 | 3.5 | 7.6 | 55 | 13.795
40 | 97 | 0 | 13.2333 | 3.5 | 7.7 | 55 | 13.8275
40 | 98 | 0 | 13.2333 | 3.5 | 7.8 | 55 | 13.86
40 | 99 | 0 | 13.2333 | 3.5 | 7.9 | 55 | 13.8925
40 | 100 | 0 | 13.2333 | 3.5 | 8 | 55 | 13.925
40 | 101 | 0 | 13.2333 | 3.5 | 8.1 | 55 | 13.9575
40 | 102 | 0 | 13.2333 | 3.5 | 8.2 | 55 | 13.99
40 | 103 | 0 | 13.2333 | 3.5 | 8.3 | 55 | 14.0225
40 | 104 | 0 | 13.2333 | 3.5 | 8.4 | 55 | 14.055
40 | 105 | 0 | 13.2333 | 3.5 | 8.5 | 55 | 14.0875
40 | 106 | 0 | 13.2333 | 3.5 | 8.6 | 55 | 14.12
40 | 107 | 0 | 13.2333 | 3.5 | 8.7 | 55 | 14.1525
40 | 108 | 0 | 13.2333 | 3.5 | 8.8 | 55 | 14.185
40 | 109 | 0 | 13.2333 | 3.5 | 8.9 | 55 | 14.2175
40 | 110 | 0 | 13.2333 | 3.5 | 9 | 55 | 14.25
40 | 111 | 0 | 13.2333 | 3.5 | 9.1 | 55 | 14.37
40 | 112 | 0 | 13.2333 | 3.5 | 9.2 | 55 | 14.49
40 | 113 | 0 | 13.2333 | 3.5 | 9.3 | 55 | 14.61
40 | 114 | 0 | 13.2333 | 3.5 | 9.4 | 55 | 14.73
40 | 115 | 0 | 13.2333 | 3.5 | 9.5 | 55 | 14.85
40 | 116 | 0 | 13.2333 | 3.5 | 9.6 | 55 | 14.97
40 | 117 | 0 | 13.2333 | 3.5 | 9.7 | 55 | 15.09
40 | 118 | 0 | 13.2333 | 3.5 | 9.8 | 55 | 15.21
40 | 119 | 0 | 13.2333 | 3.5 | 9.9 | 55 | 15.33
40 | 120 | 0 | 13.2333 | 3.5 | 10 | 55 | 15.45
40 | 121 | 0 | 13.2333 | 3.6 | 3 | 55 | 10.12
40 | 122 | 0 | 13.2333 | 3.6 | 3.1 | 55 | 10.217
40 | 123 | 0 | 13.2333 | 3.6 | 3.2 | 55 | 10.314
40 | 124 | 0 | 13.2333 | 3.6 | 3.3 | 55 | 10.411
40 | 125 | 0 | 13.2333 | 3.6 | 3.4 | 55 | 10.508
40 | 126 | 0 | 13.2333 | 3.6 | 3.5 | 55 | 10.605
40 | 127 | 0 | 13.2333 | 3.6 | 3.6 | 55 | 10.702
40 | 128 | 0 | 13.2333 | 3.6 | 3.7 | 55 | 10.799
40 | 129 | 0 | 13.2333 | 3.6 | 3.8 | 55 | 10.896
40 | 130 | 0 | 13.2333 | 3.6 | 3.9 | 55 | 10.993
40 | 131 | 0 | 13.2333 | 3.6 | 4 | 55 | 11.09
40 | 132 | 0 | 13.2333 | 3.6 | 4.1 | 55 | 11.187
40 | 133 | 0 | 13.2333 | 3.6 | 4.2 | 55 | 11.284
40 | 134 | 0 | 13.2333 | 3.6 | 4.3 | 55 | 11.381
40 | 135 | 0 | 13.2333 | 3.6 | 4.4 | 55 | 11.478
40 | 136 | 0 | 13.2333 | 3.6 | 4.5 | 55 | 11.575
40 | 137 | 0 | 13.2333 | 3.6 | 4.6 | 55 | 11.672
40 | 138 | 0 | 13.2333 | 3.6 | 4.7 | 55 | 11.769
40 | 139 | 0 | 13.2333 | 3.6 | 4.8 | 55 | 11.866
40 | 140 | 0 | 13.2333 | 3.6 | 4.9 | 55 | 11.963
40 | 141 | 0 | 13.2333 | 3.6 | 5 | 55 | 12.06
40 | 142 | 0 | 13.2333 | 3.6 | 5.1 | 55 | 12.141
40 | 143 | 0 | 13.2333 | 3.6 | 5.2 | 55 | 12.222
40 | 144 | 0 | 13.2333 | 3.6 | 5.3 | 55 | 12.303
40 | 145 | 0 | 13.2333 | 3.6 | 5.4 | 55 | 12.384
40 | 146 | 0 | 13.2333 | 3.6 | 5.5 | 55 | 12.465
40 | 147 | 0 | 13.2333 | 3.6 | 5.6 | 55 | 12.546
40 | 148 | 0 | 13.2333 | 3.6 | 5.7 | 55 | 12.627
40 | 149 | 0 | 13.2333 | 3.6 | 5.8 | 55 | 12.708
40 | 150 | 0 | 13.2333 | 3.6 | 5.9 | 55 | 12.789
41 | 45 | 0 | 13.2467 | 3.6 | 6 | 55 | 12.87
41 | 46 | 0 | 13.2467 | 3.6 | 6.1 | 55 | 12.951
41 | 47 | 0 | 13.2467 | 3.6 | 6.2 | 55 | 13.032
41 | 48 | 0 | 13.2467 | 3.6 | 6.3 | 55 | 13.113
41 | 49 | 0 | 13.2467 | 3.6 | 6.4 | 55 | 13.194
41 | 50 | 0 | 13.2467 | 3.6 | 6.5 | 55 | 13.275
41 | 51 | 0 | 13.2467 | 3.6 | 6.6 | 55 | 13.356
41 | 52 | 0 | 13.2467 | 3.6 | 6.7 | 55 | 13.437
41 | 53 | 0 | 13.2467 | 3.6 | 6.8 | 55 | 13.518
41 | 54 | 0 | 13.2467 | 3.6 | 6.9 | 55 | 13.599
41 | 55 | 0 | 13.2467 | 3.6 | 7 | 55 | 13.68
41 | 56 | 0 | 13.2467 | 3.6 | 7.1 | 55 | 13.709
41 | 57 | 0 | 13.2467 | 3.6 | 7.2 | 55 | 13.738
41 | 58 | 0 | 13.2467 | 3.6 | 7.3 | 55 | 13.767
41 | 59 | 0 | 13.2467 | 3.6 | 7.4 | 55 | 13.796
41 | 60 | 0 | 13.2467 | 3.6 | 7.5 | 55 | 13.825
41 | 61 | 0 | 13.2467 | 3.6 | 7.6 | 55 | 13.854
41 | 62 | 0 | 13.2467 | 3.6 | 7.7 | 55 | 13.883
41 | 63 | 0 | 13.2467 | 3.6 | 7.8 | 55 | 13.912
41 | 64 | 0 | 13.2467 | 3.6 | 7.9 | 55 | 13.941
41 | 65 | 0 | 13.2467 | 3.6 | 8 | 55 | 13.97
41 | 66 | 0 | 13.2467 | 3.6 | 8.1 | 55 | 13.999
41 | 67 | 0 | 13.2467 | 3.6 | 8.2 | 55 | 14.028
41 | 68 | 0 | 13.2467 | 3.6 | 8.3 | 55 | 14.057
41 | 69 | 0 | 13.2467 | 3.6 | 8.4 | 55 | 14.086
41 | 70 | 0 | 13.2467 | 3.6 | 8.5 | 55 | 14.115
41 | 71 | 0 | 13.2467 | 3.6 | 8.6 | 55 | 14.144
41 | 72 | 0 | 13.2467 | 3.6 | 8.7 | 55 | 14.173
41 | 73 | 0 | 13.2467 | 3.6 | 8.8 | 55 | 14.202
41 | 74 | 0 | 13.2467 | 3.6 | 8.9 | 55 | 14.231
41 | 75 | 0 | 13.2467 | 3.6 | 9 | 55 | 14.26
41 | 76 | 0 | 13.2467 | 3.6 | 9.1 | 55 | 14.382
41 | 77 | 0 | 13.2467 | 3.6 | 9.2 | 55 | 14.504
41 | 78 | 0 | 13.2467 | 3.6 | 9.3 | 55 | 14.626
41 | 79 | 0 | 13.2467 | 3.6 | 9.4 | 55 | 14.748
41 | 80 | 0 | 13.2467 | 3.6 | 9.5 | 55 | 14.87
41 | 81 | 0 | 13.2467 | 3.6 | 9.6 | 55 | 14.992
41 | 82 | 0 | 13.2467 | 3.6 | 9.7 | 55 | 15.114
41 | 83 | 0 | 13.2467 | 3.6 | 9.8 | 55 | 15.236
41 | 84 | 0 | 13.2467 | 3.6 | 9.9 | 55 | 15.358
41 | 85 | 0 | 13.2467 | 3.6 | 10 | 55 | 15.48
41 | 86 | 0 | 13.2467 | 3.7 | 3 | 55 | 10.14
41 | 87 | 0 | 13.2467 | 3.7 | 3.1 | 55 | 10.2365
41 | 88 | 0 | 13.2467 | 3.7 | 3.2 | 55 | 10.333
41 | 89 | 0 | 13.2467 | 3.7 | 3.3 | 55 | 10.4295
41 | 90 | 0 | 13.2467 | 3.7 | 3.4 | 55 | 10.526
41 | 91 | 0 | 13.2467 | 3.7 | 3.5 | 55 | 10.6225
41 | 92 | 0 | 13.2467 | 3.7 | 3.6 | 55 | 10.719
41 | 93 | 0 | 13.2467 | 3.7 | 3.7 | 55 | 10.8155
41 | 94 | 0 | 13.2467 | 3.7 | 3.8 | 55 | 10.912
41 | 95 | 0 | 13.2467 | 3.7 | 3.9 | 55 | 11.0085
41 | 96 | 0 | 13.2467 | 3.7 | 4 | 55 | 11.105
41 | 97 | 0 | 13.2467 | 3.7 | 4.1 | 55 | 11.2015
41 | 98 | 0 | 13.2467 | 3.7 | 4.2 | 55 | 11.298
41 | 99 | 0 | 13.2467 | 3.7 | 4.3 | 55 | 11.3945
41 | 100 | 0 | 13.2467 | 3.7 | 4.4 | 55 | 11.491
41 | 101 | 0 | 13.2467 | 3.7 | 4.5 | 55 | 11.5875
41 | 102 | 0 | 13.2467 | 3.7 | 4.6 | 55 | 11.684
41 | 103 | 0 | 13.2467 | 3.7 | 4.7 | 55 | 11.7805
41 | 104 | 0 | 13.2467 | 3.7 | 4.8 | 55 | 11.877
41 | 105 | 0 | 13.2467 | 3.7 | 4.9 | 55 | 11.9735
41 | 106 | 0 | 13.2467 | 3.7 | 5 | 55 | 12.07
41 | 107 | 0 | 13.2467 | 3.7 | 5.1 | 55 | 12.1545
41 | 108 | 0 | 13.2467 | 3.7 | 5.2 | 55 | 12.239
41 | 109 | 0 | 13.2467 | 3.7 | 5.3 | 55 | 12.3235
41 | 110 | 0 | 13.2467 | 3.7 | 5.4 | 55 | 12.408
41 | 111 | 0 | 13.2467 | 3.7 | 5.5 | 55 | 12.4925
41 | 112 | 0 | 13.2467 | 3.7 | 5.6 | 55 | 12.577
41 | 113 | 0 | 13.2467 | 3.7 | 5.7 | 55 | 12.6615
41 | 114 | 0 | 13.2467 | 3.7 | 5.8 | 55 | 12.746
41 | 115 | 0 | 13.2467 | 3.7 | 5.9 | 55 | 12.8305
41 | 116 | 0 | 13.2467 | 3.7 | 6 | 55 | 12.915
41 | 117 | 0 | 13.2467 | 3.7 | 6.1 | 55 | 12.9995
41 | 118 | 0 | 13.2467 | 3.7 | 6.2 | 55 | 13.084
41 | 119 | 0 | 13.2467 | 3.7 | 6.3 | 55 | 13.1685
41 | 120 | 0 | 13.2467 | 3.7 | 6.4 | 55 | 13.253
41 | 121 | 0 | 13.2467 | 3.7 | 6.5 | 55 | 13.3375
41 | 122 | 0 | 13.2467 | 3.7 | 6.6 | 55 | 13.422
41 | 123 | 0 | 13.2467 | 3.7 | 6.7 | 55 | 13.5065
41 | 124 | 0 | 13.2467 | 3.7 | 6.8 | 55 | 13.591
41 | 125 | 0 | 13.2467 | 3.7 | 6.9 | 55 | 13.6755
41 | 126 | 0 | 13.2467 | 3.7 | 7 | 55 | 13.76
41 | 127 | 0 | 13.2467 | 3.7 | 7.1 | 55 | 13.7855
41 | 128 | 0 | 13.2467 | 3.7 | 7.2 | 55 | 13.811
41 | 129 | 0 | 13.2467 | 3.7 | 7.3 | 55 | 13.8365
41 | 130 | 0 | 13.2467 | 3.7 | 7.4 | 55 | 13.862
41 | 131 | 0 | 13.2467 | 3.7 | 7.5 | 55 | 13.8875
41 | 132 | 0 | 13.2467 | 3.7 | 7.6 | 55 | 13.913
41 | 133 | 0 | 13.2467 | 3.7 | 7.7 | 55 | 13.9385
41 | 134 | 0 | 13.2467 | 3.7 | 7.8 | 55 | 13.964
41 | 135 | 0 | 13.2467 | 3.7 | 7.9 | 55 | 13.9895
41 | 136 | 0 | 13.2467 | 3.7 | 8 | 55 | 14.015
41 | 137 | 0 | 13.2467 | 3.7 | 8.1 | 55 | 14.0405
41 | 138 | 0 | 13.2467 | 3.7 | 8.2 | 55 | 14.066
41 | 139 | 0 | 13.2467 | 3.7 | 8.3 | 55 | 14.0915
41 | 140 | 0 | 13.2467 | 3.7 | 8.4 | 55 | 14.117
41 | 141 | 0 | 13.2467 | 3.7 | 8.5 | 55 | 14.1425
41 | 142 | 0 | 13.2467 | 3.7 | 8.6 | 55 | 14.168
41 | 143 | 0 | 13.2467 | 3.7 | 8.7 | 55 | 14.1935
41 | 144 | 0 | 13.2467 | 3.7 | 8.8 | 55 | 14.219
41 | 145 | 0 | 13.2467 | 3.7 | 8.9 | 55 | 14.2445
41 | 146 | 0 | 13.2467 | 3.7 | 9 | 55 | 14.27
41 | 147 | 0 | 13.2467 | 3.7 | 9.1 | 55 | 14.394
41 | 148 | 0 | 13.2467 | 3.7 | 9.2 | 55 | 14.518
41 | 149 | 0 | 13.2467 | 3.7 | 9.3 | 55 | 14.642
41 | 150 | 0 | 13.2467 | 3.7 | 9.4 | 55 | 14.766
42 | 45 | 0 | 13.26 | 3.7 | 9.5 | 55 | 14.89
42 | 46 | 0 | 13.26 | 3.7 | 9.6 | 55 | 15.014
42 | 47 | 0 | 13.26 | 3.7 | 9.7 | 55 | 15.138
42 | 48 | 0 | 13.26 | 3.7 | 9.8 | 55 | 15.262
42 | 49 | 0 | 13.26 | 3.7 | 9.9 | 55 | 15.386
42 | 50 | 0 | 13.26 | 3.7 | 10 | 55 | 15.51
42 | 51 | 0 | 13.26 | 3.8 | 3 | 55 | 10.16
42 | 52 | 0 | 13.26 | 3.8 | 3.1 | 55 | 10.256
42 | 53 | 0 | 13.26 | 3.8 | 3.2 | 55 | 10.352
42 | 54 | 0 | 13.26 | 3.8 | 3.3 | 55 | 10.448
42 | 55 | 0 | 13.26 | 3.8 | 3.4 | 55 | 10.544
42 | 56 | 0 | 13.26 | 3.8 | 3.5 | 55 | 10.64
42 | 57 | 0 | 13.26 | 3.8 | 3.6 | 55 | 10.736
42 | 58 | 0 | 13.26 | 3.8 | 3.7 | 55 | 10.832
42 | 59 | 0 | 13.26 | 3.8 | 3.8 | 55 | 10.928
42 | 60 | 0 | 13.26 | 3.8 | 3.9 | 55 | 11.024
42 | 61 | 0 | 13.26 | 3.8 | 4 | 55 | 11.12
42 | 62 | 0 | 13.26 | 3.8 | 4.1 | 55 | 11.216
42 | 63 | 0 | 13.26 | 3.8 | 4.2 | 55 | 11.312
42 | 64 | 0 | 13.26 | 3.8 | 4.3 | 55 | 11.408
42 | 65 | 0 | 13.26 | 3.8 | 4.4 | 55 | 11.504
42 | 66 | 0 | 13.26 | 3.8 | 4.5 | 55 | 11.6
42 | 67 | 0 | 13.26 | 3.8 | 4.6 | 55 | 11.696
42 | 68 | 0 | 13.26 | 3.8 | 4.7 | 55 | 11.792
42 | 69 | 0 | 13.26 | 3.8 | 4.8 | 55 | 11.888
42 | 70 | 0 | 13.26 | 3.8 | 4.9 | 55 | 11.984
42 | 71 | 0 | 13.26 | 3.8 | 5 | 55 | 12.08
42 | 72 | 0 | 13.26 | 3.8 | 5.1 | 55 | 12.168
42 | 73 | 0 | 13.26 | 3.8 | 5.2 | 55 | 12.256
42 | 74 | 0 | 13.26 | 3.8 | 5.3 | 55 | 12.344
42 | 75 | 0 | 13.26 | 3.8 | 5.4 | 55 | 12.432
42 | 76 | 0 | 13.26 | 3.8 | 5.5 | 55 | 12.52
42 | 77 | 0 | 13.26 | 3.8 | 5.6 | 55 | 12.608
42 | 78 | 0 | 13.26 | 3.8 | 5.7 | 55 | 12.696
42 | 79 | 0 | 13.26 | 3.8 | 5.8 | 55 | 12.784
42 | 80 | 0 | 13.26 | 3.8 | 5.9 | 55 | 12.872
42 | 81 | 0 | 13.26 | 3.8 | 6 | 55 | 12.96
42 | 82 | 0 | 13.26 | 3.8 | 6.1 | 55 | 13.048
42 | 83 | 0 | 13.26 | 3.8 | 6.2 | 55 | 13.136
42 | 84 | 0 | 13.26 | 3.8 | 6.3 | 55 | 13.224
42 | 85 | 0 | 13.26 | 3.8 | 6.4 | 55 | 13.312
42 | 86 | 0 | 13.26 | 3.8 | 6.5 | 55 | 13.4
42 | 87 | 0 | 13.26 | 3.8 | 6.6 | 55 | 13.488
42 | 88 | 0 | 13.26 | 3.8 | 6.7 | 55 | 13.576
42 | 89 | 0 | 13.26 | 3.8 | 6.8 | 55 | 13.664
42 | 90 | 0 | 13.26 | 3.8 | 6.9 | 55 | 13.752
42 | 91 | 0 | 13.26 | 3.8 | 7 | 55 | 13.84
42 | 92 | 0 | 13.26 | 3.8 | 7.1 | 55 | 13.862
42 | 93 | 0 | 13.26 | 3.8 | 7.2 | 55 | 13.884
42 | 94 | 0 | 13.26 | 3.8 | 7.3 | 55 | 13.906
42 | 95 | 0 | 13.26 | 3.8 | 7.4 | 55 | 13.928
42 | 96 | 0 | 13.26 | 3.8 | 7.5 | 55 | 13.95
42 | 97 | 0 | 13.26 | 3.8 | 7.6 | 55 | 13.972
42 | 98 | 0 | 13.26 | 3.8 | 7.7 | 55 | 13.994
42 | 99 | 0 | 13.26 | 3.8 | 7.8 | 55 | 14.016
42 | 100 | 0 | 13.26 | 3.8 | 7.9 | 55 | 14.038
42 | 101 | 0 | 13.26 | 3.8 | 8 | 55 | 14.06
42 | 102 | 0 | 13.26 | 3.8 | 8.1 | 55 | 14.082
42 | 103 | 0 | 13.26 | 3.8 | 8.2 | 55 | 14.104
42 | 104 | 0 | 13.26 | 3.8 | 8.3 | 55 | 14.126
42 | 105 | 0 | 13.26 | 3.8 | 8.4 | 55 | 14.148
42 | 106 | 0 | 13.26 | 3.8 | 8.5 | 55 | 14.17
42 | 107 | 0 | 13.26 | 3.8 | 8.6 | 55 | 14.192
42 | 108 | 0 | 13.26 | 3.8 | 8.7 | 55 | 14.214
42 | 109 | 0 | 13.26 | 3.8 | 8.8 | 55 | 14.236
42 | 110 | 0 | 13.26 | 3.8 | 8.9 | 55 | 14.258
42 | 111 | 0 | 13.26 | 3.8 | 9 | 55 | 14.28
42 | 112 | 0 | 13.26 | 3.8 | 9.1 | 55 | 14.406
42 | 113 | 0 | 13.26 | 3.8 | 9.2 | 55 | 14.532
42 | 114 | 0 | 13.26 | 3.8 | 9.3 | 55 | 14.658
42 | 115 | 0 | 13.26 | 3.8 | 9.4 | 55 | 14.784
42 | 116 | 0 | 13.26 | 3.8 | 9.5 | 55 | 14.91
42 | 117 | 0 | 13.26 | 3.8 | 9.6 | 55 | 15.036
42 | 118 | 0 | 13.26 | 3.8 | 9.7 | 55 | 15.162
42 | 119 | 0 | 13.26 | 3.8 | 9.8 | 55 | 15.288
42 | 120 | 0 | 13.26 | 3.8 | 9.9 | 55 | 15.414
42 | 121 | 0 | 13.26 | 3.8 | 10 | 55 | 15.54
42 | 122 | 0 | 13.26 | 3.9 | 3 | 55 | 10.18
42 | 123 | 0 | 13.26 | 3.9 | 3.1 | 55 | 10.2755
42 | 124 | 0 | 13.26 | 3.9 | 3.2 | 55 | 10.371
42 | 125 | 0 | 13.26 | 3.9 | 3.3 | 55 | 10.4665
42 | 126 | 0 | 13.26 | 3.9 | 3.4 | 55 | 10.562
42 | 127 | 0 | 13.26 | 3.9 | 3.5 | 55 | 10.6575
42 | 128 | 0 | 13.26 | 3.9 | 3.6 | 55 | 10.753
42 | 129 | 0 | 13.26 | 3.9 | 3.7 | 55 | 10.8485
42 | 130 | 0 | 13.26 | 3.9 | 3.8 | 55 | 10.944
42 | 131 | 0 | 13.26 | 3.9 | 3.9 | 55 | 11.0395
42 | 132 | 0 | 13.26 | 3.9 | 4 | 55 | 11.135
42 | 133 | 0 | 13.26 | 3.9 | 4.1 | 55 | 11.2305
42 | 134 | 0 | 13.26 | 3.9 | 4.2 | 55 | 11.326
42 | 135 | 0 | 13.26 | 3.9 | 4.3 | 55 | 11.4215
42 | 136 | 0 | 13.26 | 3.9 | 4.4 | 55 | 11.517
42 | 137 | 0 | 13.26 | 3.9 | 4.5 | 55 | 11.6125
42 | 138 | 0 | 13.26 | 3.9 | 4.6 | 55 | 11.708
42 | 139 | 0 | 13.26 | 3.9 | 4.7 | 55 | 11.8035
42 | 140 | 0 | 13.26 | 3.9 | 4.8 | 55 | 11.899
42 | 141 | 0 | 13.26 | 3.9 | 4.9 | 55 | 11.9945
42 | 142 | 0 | 13.26 | 3.9 | 5 | 55 | 12.09
42 | 143 | 0 | 13.26 | 3.9 | 5.1 | 55 | 12.1815
42 | 144 | 0 | 13.26 | 3.9 | 5.2 | 55 | 12.273
42 | 145 | 0 | 13.26 | 3.9 | 5.3 | 55 | 12.3645
42 | 146 | 0 | 13.26 | 3.9 | 5.4 | 55 | 12.456
42 | 147 | 0 | 13.26 | 3.9 | 5.5 | 55 | 12.5475
42 | 148 | 0 | 13.26 | 3.9 | 5.6 | 55 | 12.639
42 | 149 | 0 | 13.26 | 3.9 | 5.7 | 55 | 12.7305
42 | 150 | 0 | 13.26 | 3.9 | 5.8 | 55 | 12.822
43 | 45 | 0 | 13.2733 | 3.9 | 5.9 | 55 | 12.9135
43 | 46 | 0 | 13.2733 | 3.9 | 6 | 55 | 13.005
43 | 47 | 0 | 13.2733 | 3.9 | 6.1 | 55 | 13.0965
43 | 48 | 0 | 13.2733 | 3.9 | 6.2 | 55 | 13.188
43 | 49 | 0 | 13.2733 | 3.9 | 6.3 | 55 | 13.2795
43 | 50 | 0 | 13.2733 | 3.9 | 6.4 | 55 | 13.371
43 | 51 | 0 | 13.2733 | 3.9 | 6.5 | 55 | 13.4625
43 | 52 | 0 | 13.2733 | 3.9 | 6.6 | 55 | 13.554
43 | 53 | 0 | 13.2733 | 3.9 | 6.7 | 55 | 13.6455
43 | 54 | 0 | 13.2733 | 3.9 | 6.8 | 55 | 13.737
43 | 55 | 0 | 13.2733 | 3.9 | 6.9 | 55 | 13.8285
43 | 56 | 0 | 13.2733 | 3.9 | 7 | 55 | 13.92
43 | 57 | 0 | 13.2733 | 3.9 | 7.1 | 55 | 13.9385
43 | 58 | 0 | 13.2733 | 3.9 | 7.2 | 55 | 13.957
43 | 59 | 0 | 13.2733 | 3.9 | 7.3 | 55 | 13.9755
43 | 60 | 0 | 13.2733 | 3.9 | 7.4 | 55 | 13.994
43 | 61 | 0 | 13.2733 | 3.9 | 7.5 | 55 | 14.0125
43 | 62 | 0 | 13.2733 | 3.9 | 7.6 | 55 | 14.031
43 | 63 | 0 | 13.2733 | 3.9 | 7.7 | 55 | 14.0495
43 | 64 | 0 | 13.2733 | 3.9 | 7.8 | 55 | 14.068
43 | 65 | 0 | 13.2733 | 3.9 | 7.9 | 55 | 14.0865
43 | 66 | 0 | 13.2733 | 3.9 | 8 | 55 | 14.105
43 | 67 | 0 | 13.2733 | 3.9 | 8.1 | 55 | 14.1235
43 | 68 | 0 | 13.2733 | 3.9 | 8.2 | 55 | 14.142
43 | 69 | 0 | 13.2733 | 3.9 | 8.3 | 55 | 14.1605
43 | 70 | 0 | 13.2733 | 3.9 | 8.4 | 55 | 14.179
43 | 71 | 0 | 13.2733 | 3.9 | 8.5 | 55 | 14.1975
43 | 72 | 0 | 13.2733 | 3.9 | 8.6 | 55 | 14.216
43 | 73 | 0 | 13.2733 | 3.9 | 8.7 | 55 | 14.2345
43 | 74 | 0 | 13.2733 | 3.9 | 8.8 | 55 | 14.253
43 | 75 | 0 | 13.2733 | 3.9 | 8.9 | 55 | 14.2715
43 | 76 | 0 | 13.2733 | 3.9 | 9 | 55 | 14.29
43 | 77 | 0 | 13.2733 | 3.9 | 9.1 | 55 | 14.418
43 | 78 | 0 | 13.2733 | 3.9 | 9.2 | 55 | 14.546
43 | 79 | 0 | 13.2733 | 3.9 | 9.3 | 55 | 14.674
43 | 80 | 0 | 13.2733 | 3.9 | 9.4 | 55 | 14.802
43 | 81 | 0 | 13.2733 | 3.9 | 9.5 | 55 | 14.93
43 | 82 | 0 | 13.2733 | 3.9 | 9.6 | 55 | 15.058
43 | 83 | 0 | 13.2733 | 3.9 | 9.7 | 55 | 15.186
43 | 84 | 0 | 13.2733 | 3.9 | 9.8 | 55 | 15.314
43 | 85 | 0 | 13.2733 | 3.9 | 9.9 | 55 | 15.442
43 | 86 | 0 | 13.2733 | 3.9 | 10 | 55 | 15.57
43 | 87 | 0 | 13.2733 | 4 | 3 | 55 | 10.2
43 | 88 | 0 | 13.2733 | 4 | 3.1 | 55 | 10.295
43 | 89 | 0 | 13.2733 | 4 | 3.2 | 55 | 10.39
43 | 90 | 0 | 13.2733 | 4 | 3.3 | 55 | 10.485
43 | 91 | 0 | 13.2733 | 4 | 3.4 | 55 | 10.58
43 | 92 | 0 | 13.2733 | 4 | 3.5 | 55 | 10.675
43 | 93 | 0 | 13.2733 | 4 | 3.6 | 55 | 10.77
43 | 94 | 0 | 13.2733 | 4 | 3.7 | 55 | 10.865
43 | 95 | 0 | 13.2733 | 4 | 3.8 | 55 | 10.96
43 | 96 | 0 | 13.2733 | 4 | 3.9 | 55 | 11.055
43 | 97 | 0 | 13.2733 | 4 | 4 | 55 | 11.15
43 | 98 | 0 | 13.2733 | 4 | 4.1 | 55 | 11.245
43 | 99 | 0 | 13.2733 | 4 | 4.2 | 55 | 11.34
43 | 100 | 0 | 13.2733 | 4 | 4.3 | 55 | 11.435
43 | 101 | 0 | 13.2733 | 4 | 4.4 | 55 | 11.53
43 | 102 | 0 | 13.2733 | 4 | 4.5 | 55 | 11.625
43 | 103 | 0 | 13.2733 | 4 | 4.6 | 55 | 11.72
43 | 104 | 0 | 13.2733 | 4 | 4.7 | 55 | 11.815
43 | 105 | 0 | 13.2733 | 4 | 4.8 | 55 | 11.91
43 | 106 | 0 | 13.2733 | 4 | 4.9 | 55 | 12.005
43 | 107 | 0 | 13.2733 | 4 | 5 | 55 | 12.1
43 | 108 | 0 | 13.2733 | 4 | 5.1 | 55 | 12.195
43 | 109 | 0 | 13.2733 | 4 | 5.2 | 55 | 12.29
43 | 110 | 0 | 13.2733 | 4 | 5.3 | 55 | 12.385
43 | 111 | 0 | 13.2733 | 4 | 5.4 | 55 | 12.48
43 | 112 | 0 | 13.2733 | 4 | 5.5 | 55 | 12.575
43 | 113 | 0 | 13.2733 | 4 | 5.6 | 55 | 12.67
43 | 114 | 0 | 13.2733 | 4 | 5.7 | 55 | 12.765
43 | 115 | 0 | 13.2733 | 4 | 5.8 | 55 | 12.86
43 | 116 | 0 | 13.2733 | 4 | 5.9 | 55 | 12.955
43 | 117 | 0 | 13.2733 | 4 | 6 | 55 | 13.05
43 | 118 | 0 | 13.2733 | 4 | 6.1 | 55 | 13.145
43 | 119 | 0 | 13.2733 | 4 | 6.2 | 55 | 13.24
43 | 120 | 0 | 13.2733 | 4 | 6.3 | 55 | 13.335
43 | 121 | 0 | 13.2733 | 4 | 6.4 | 55 | 13.43
43 | 122 | 0 | 13.2733 | 4 | 6.5 | 55 | 13.525
43 | 123 | 0 | 13.2733 | 4 | 6.6 | 55 | 13.62
43 | 124 | 0 | 13.2733 | 4 | 6.7 | 55 | 13.715
43 | 125 | 0 | 13.2733 | 4 | 6.8 | 55 | 13.81
43 | 126 | 0 | 13.2733 | 4 | 6.9 | 55 | 13.905
43 | 127 | 0 | 13.2733 | 4 | 7 | 55 | 14
43 | 128 | 0 | 13.2733 | 4 | 7.1 | 55 | 14.015
43 | 129 | 0 | 13.2733 | 4 | 7.2 | 55 | 14.03
43 | 130 | 0 | 13.2733 | 4 | 7.3 | 55 | 14.045
43 | 131 | 0 | 13.2733 | 4 | 7.4 | 55 | 14.06
43 | 132 | 0 | 13.2733 | 4 | 7.5 | 55 | 14.075
43 | 133 | 0 | 13.2733 | 4 | 7.6 | 55 | 14.09
43 | 134 | 0 | 13.2733 | 4 | 7.7 | 55 | 14.105
43 | 135 | 0 | 13.2733 | 4 | 7.8 | 55 | 14.12
43 | 136 | 0 | 13.2733 | 4 | 7.9 | 55 | 14.135
43 | 137 | 0 | 13.2733 | 4 | 8 | 55 | 14.15
43 | 138 | 0 | 13.2733 | 4 | 8.1 | 55 | 14.165
43 | 139 | 0 | 13.2733 | 4 | 8.2 | 55 | 14.18
43 | 140 | 0 | 13.2733 | 4 | 8.3 | 55 | 14.195
43 | 141 | 0 | 13.2733 | 4 | 8.4 | 55 | 14.21
43 | 142 | 0 | 13.2733 | 4 | 8.5 | 55 | 14.225
43 | 143 | 0 | 13.2733 | 4 | 8.6 | 55 | 14.24
43 | 144 | 0 | 13.2733 | 4 | 8.7 | 55 | 14.255
43 | 145 | 0 | 13.2733 | 4 | 8.8 | 55 | 14.27
43 | 146 | 0 | 13.2733 | 4 | 8.9 | 55 | 14.285
43 | 147 | 0 | 13.2733 | 4 | 9 | 55 | 14.3
43 | 148 | 0 | 13.2733 | 4 | 9.1 | 55 | 14.43
43 | 149 | 0 | 13.2733 | 4 | 9.2 | 55 | 14.56
43 | 150 | 0 | 13.2733 | 4 | 9.3 | 55 | 14.69
44 | 45 | 0 | 13.2867 | 4 | 9.4 | 55 | 14.82
44 | 46 | 0 | 13.2867 | 4 | 9.5 | 55 | 14.95
44 | 47 | 0 | 13.2867 | 4 | 9.6 | 55 | 15.08
44 | 48 | 0 | 13.2867 | 4 | 9.7 | 55 | 15.21
44 | 49 | 0 | 13.2867 | 4 | 9.8 | 55 | 15.34
44 | 50 | 0 | 13.2867 | 4 | 9.9 | 55 | 15.47
44 | 51 | 0 | 13.2867 | 4 | 10 | 55 | 15.6
44 | 52 | 0 | 13.2867 | 4.1 | 3 | 55 | 10.21
44 | 53 | 0 | 13.2867 | 4.1 | 3.1 | 55 | 10.3055
44 | 54 | 0 | 13.2867 | 4.1 | 3.2 | 55 | 10.401
44 | 55 | 0 | 13.2867 | 4.1 | 3.3 | 55 | 10.4965
44 | 56 | 0 | 13.2867 | 4.1 | 3.4 | 55 | 10.592
44 | 57 | 0 | 13.2867 | 4.1 | 3.5 | 55 | 10.6875
44 | 58 | 0 | 13.2867 | 4.1 | 3.6 | 55 | 10.783
44 | 59 | 0 | 13.2867 | 4.1 | 3.7 | 55 | 10.8785
44 | 60 | 0 | 13.2867 | 4.1 | 3.8 | 55 | 10.974
44 | 61 | 0 | 13.2867 | 4.1 | 3.9 | 55 | 11.0695
44 | 62 | 0 | 13.2867 | 4.1 | 4 | 55 | 11.165
44 | 63 | 0 | 13.2867 | 4.1 | 4.1 | 55 | 11.2605
44 | 64 | 0 | 13.2867 | 4.1 | 4.2 | 55 | 11.356
44 | 65 | 0 | 13.2867 | 4.1 | 4.3 | 55 | 11.4515
44 | 66 | 0 | 13.2867 | 4.1 | 4.4 | 55 | 11.547
44 | 67 | 0 | 13.2867 | 4.1 | 4.5 | 55 | 11.6425
44 | 68 | 0 | 13.2867 | 4.1 | 4.6 | 55 | 11.738
44 | 69 | 0 | 13.2867 | 4.1 | 4.7 | 55 | 11.8335
44 | 70 | 0 | 13.2867 | 4.1 | 4.8 | 55 | 11.929
44 | 71 | 0 | 13.2867 | 4.1 | 4.9 | 55 | 12.0245
44 | 72 | 0 | 13.2867 | 4.1 | 5 | 55 | 12.12
44 | 73 | 0 | 13.2867 | 4.1 | 5.1 | 55 | 12.215
44 | 74 | 0 | 13.2867 | 4.1 | 5.2 | 55 | 12.31
44 | 75 | 0 | 13.2867 | 4.1 | 5.3 | 55 | 12.405
44 | 76 | 0 | 13.2867 | 4.1 | 5.4 | 55 | 12.5
44 | 77 | 0 | 13.2867 | 4.1 | 5.5 | 55 | 12.595
44 | 78 | 0 | 13.2867 | 4.1 | 5.6 | 55 | 12.69
44 | 79 | 0 | 13.2867 | 4.1 | 5.7 | 55 | 12.785
44 | 80 | 0 | 13.2867 | 4.1 | 5.8 | 55 | 12.88
44 | 81 | 0 | 13.2867 | 4.1 | 5.9 | 55 | 12.975
44 | 82 | 0 | 13.2867 | 4.1 | 6 | 55 | 13.07
44 | 83 | 0 | 13.2867 | 4.1 | 6.1 | 55 | 13.165
44 | 84 | 0 | 13.2867 | 4.1 | 6.2 | 55 | 13.26
44 | 85 | 0 | 13.2867 | 4.1 | 6.3 | 55 | 13.355
44 | 86 | 0 | 13.2867 | 4.1 | 6.4 | 55 | 13.45
44 | 87 | 0 | 13.2867 | 4.1 | 6.5 | 55 | 13.545
44 | 88 | 0 | 13.2867 | 4.1 | 6.6 | 55 | 13.64
44 | 89 | 0 | 13.2867 | 4.1 | 6.7 | 55 | 13.735
44 | 90 | 0 | 13.2867 | 4.1 | 6.8 | 55 | 13.83
44 | 91 | 0 | 13.2867 | 4.1 | 6.9 | 55 | 13.925
44 | 92 | 0 | 13.2867 | 4.1 | 7 | 55 | 14.02
44 | 93 | 0 | 13.2867 | 4.1 | 7.1 | 55 | 14.035
44 | 94 | 0 | 13.2867 | 4.1 | 7.2 | 55 | 14.05
44 | 95 | 0 | 13.2867 | 4.1 | 7.3 | 55 | 14.065
44 | 96 | 0 | 13.2867 | 4.1 | 7.4 | 55 | 14.08
44 | 97 | 0 | 13.2867 | 4.1 | 7.5 | 55 | 14.095
44 | 98 | 0 | 13.2867 | 4.1 | 7.6 | 55 | 14.11
44 | 99 | 0 | 13.2867 | 4.1 | 7.7 | 55 | 14.125
44 | 100 | 0 | 13.2867 | 4.1 | 7.8 | 55 | 14.14
44 | 101 | 0 | 13.2867 | 4.1 | 7.9 | 55 | 14.155
44 | 102 | 0 | 13.2867 | 4.1 | 8 | 55 | 14.17
44 | 103 | 0 | 13.2867 | 4.1 | 8.1 | 55 | 14.185
44 | 104 | 0 | 13.2867 | 4.1 | 8.2 | 55 | 14.2
44 | 105 | 0 | 13.2867 | 4.1 | 8.3 | 55 | 14.215
44 | 106 | 0 | 13.2867 | 4.1 | 8.4 | 55 | 14.23
44 | 107 | 0 | 13.2867 | 4.1 | 8.5 | 55 | 14.245
44 | 108 | 0 | 13.2867 | 4.1 | 8.6 | 55 | 14.26
44 | 109 | 0 | 13.2867 | 4.1 | 8.7 | 55 | 14.275
44 | 110 | 0 | 13.2867 | 4.1 | 8.8 | 55 | 14.29
44 | 111 | 0 | 13.2867 | 4.1 | 8.9 | 55 | 14.305
44 | 112 | 0 | 13.2867 | 4.1 | 9 | 55 | 14.32
44 | 113 | 0 | 13.2867 | 4.1 | 9.1 | 55 | 14.449
44 | 114 | 0 | 13.2867 | 4.1 | 9.2 | 55 | 14.578
44 | 115 | 0 | 13.2867 | 4.1 | 9.3 | 55 | 14.707
44 | 116 | 0 | 13.2867 | 4.1 | 9.4 | 55 | 14.836
44 | 117 | 0 | 13.2867 | 4.1 | 9.5 | 55 | 14.965
44 | 118 | 0 | 13.2867 | 4.1 | 9.6 | 55 | 15.094
44 | 119 | 0 | 13.2867 | 4.1 | 9.7 | 55 | 15.223
44 | 120 | 0 | 13.2867 | 4.1 | 9.8 | 55 | 15.352
44 | 121 | 0 | 13.2867 | 4.1 | 9.9 | 55 | 15.481
44 | 122 | 0 | 13.2867 | 4.1 | 10 | 55 | 15.61
44 | 123 | 0 | 13.2867 | 4.2 | 3 | 55 | 10.22
44 | 124 | 0 | 13.2867 | 4.2 | 3.1 | 55 | 10.316
44 | 125 | 0 | 13.2867 | 4.2 | 3.2 | 55 | 10.412
44 | 126 | 0 | 13.2867 | 4.2 | 3.3 | 55 | 10.508
44 | 127 | 0 | 13.2867 | 4.2 | 3.4 | 55 | 10.604
44 | 128 | 0 | 13.2867 | 4.2 | 3.5 | 55 | 10.7
44 | 129 | 0 | 13.2867 | 4.2 | 3.6 | 55 | 10.796
44 | 130 | 0 | 13.2867 | 4.2 | 3.7 | 55 | 10.892
44 | 131 | 0 | 13.2867 | 4.2 | 3.8 | 55 | 10.988
44 | 132 | 0 | 13.2867 | 4.2 | 3.9 | 55 | 11.084
44 | 133 | 0 | 13.2867 | 4.2 | 4 | 55 | 11.18
44 | 134 | 0 | 13.2867 | 4.2 | 4.1 | 55 | 11.276
44 | 135 | 0 | 13.2867 | 4.2 | 4.2 | 55 | 11.372
44 | 136 | 0 | 13.2867 | 4.2 | 4.3 | 55 | 11.468
44 | 137 | 0 | 13.2867 | 4.2 | 4.4 | 55 | 11.564
44 | 138 | 0 | 13.2867 | 4.2 | 4.5 | 55 | 11.66
44 | 139 | 0 | 13.2867 | 4.2 | 4.6 | 55 | 11.756
44 | 140 | 0 | 13.2867 | 4.2 | 4.7 | 55 | 11.852
44 | 141 | 0 | 13.2867 | 4.2 | 4.8 | 55 | 11.948
44 | 142 | 0 | 13.2867 | 4.2 | 4.9 | 55 | 12.044
44 | 143 | 0 | 13.2867 | 4.2 | 5 | 55 | 12.14
44 | 144 | 0 | 13.2867 | 4.2 | 5.1 | 55 | 12.235
44 | 145 | 0 | 13.2867 | 4.2 | 5.2 | 55 | 12.33
44 | 146 | 0 | 13.2867 | 4.2 | 5.3 | 55 | 12.425
44 | 147 | 0 | 13.2867 | 4.2 | 5.4 | 55 | 12.52
44 | 148 | 0 | 13.2867 | 4.2 | 5.5 | 55 | 12.615
44 | 149 | 0 | 13.2867 | 4.2 | 5.6 | 55 | 12.71
44 | 150 | 0 | 13.2867 | 4.2 | 5.7 | 55 | 12.805
45 | 45 | 0 | 13.3 | 4.2 | 5.8 | 55 | 12.9
45 | 46 | 0 | 13.3 | 4.2 | 5.9 | 55 | 12.995
45 | 47 | 0 | 13.3 | 4.2 | 6 | 55 | 13.09
45 | 48 | 0 | 13.3 | 4.2 | 6.1 | 55 | 13.185
45 | 49 | 0 | 13.3 | 4.2 | 6.2 | 55 | 13.28
45 | 50 | 0 | 13.3 | 4.2 | 6.3 | 55 | 13.375
45 | 51 | 0 | 13.3 | 4.2 | 6.4 | 55 | 13.47
45 | 52 | 0 | 13.3 | 4.2 | 6.5 | 55 | 13.565
45 | 53 | 0 | 13.3 | 4.2 | 6.6 | 55 | 13.66
45 | 54 | 0 | 13.3 | 4.2 | 6.7 | 55 | 13.755
45 | 55 | 0 | 13.3 | 4.2 | 6.8 | 55 | 13.85
45 | 56 | 0 | 13.3 | 4.2 | 6.9 | 55 | 13.945
45 | 57 | 0 | 13.3 | 4.2 | 7 | 55 | 14.04
45 | 58 | 0 | 13.3 | 4.2 | 7.1 | 55 | 14.055
45 | 59 | 0 | 13.3 | 4.2 | 7.2 | 55 | 14.07
45 | 60 | 0 | 13.3 | 4.2 | 7.3 | 55 | 14.085
45 | 61 | 0 | 13.3 | 4.2 | 7.4 | 55 | 14.1
45 | 62 | 0 | 13.3 | 4.2 | 7.5 | 55 | 14.115
45 | 63 | 0 | 13.3 | 4.2 | 7.6 | 55 | 14.13
45 | 64 | 0 | 13.3 | 4.2 | 7.7 | 55 | 14.145
45 | 65 | 0 | 13.3 | 4.2 | 7.8 | 55 | 14.16
45 | 66 | 0 | 13.3 | 4.2 | 7.9 | 55 | 14.175
45 | 67 | 0 | 13.3 | 4.2 | 8 | 55 | 14.19
45 | 68 | 0 | 13.3 | 4.2 | 8.1 | 55 | 14.205
45 | 69 | 0 | 13.3 | 4.2 | 8.2 | 55 | 14.22
45 | 70 | 0 | 13.3 | 4.2 | 8.3 | 55 | 14.235
45 | 71 | 0 | 13.3 | 4.2 | 8.4 | 55 | 14.25
45 | 72 | 0 | 13.3 | 4.2 | 8.5 | 55 | 14.265
45 | 73 | 0 | 13.3 | 4.2 | 8.6 | 55 | 14.28
45 | 74 | 0 | 13.3 | 4.2 | 8.7 | 55 | 14.295
45 | 75 | 0 | 13.3 | 4.2 | 8.8 | 55 | 14.31
45 | 76 | 0 | 13.3 | 4.2 | 8.9 | 55 | 14.325
45 | 77 | 0 | 13.3 | 4.2 | 9 | 55 | 14.34
45 | 78 | 0 | 13.3 | 4.2 | 9.1 | 55 | 14.468
45 | 79 | 0 | 13.3 | 4.2 | 9.2 | 55 | 14.596
45 | 80 | 0 | 13.3 | 4.2 | 9.3 | 55 | 14.724
45 | 81 | 0 | 13.3 | 4.2 | 9.4 | 55 | 14.852
45 | 82 | 0 | 13.3 | 4.2 | 9.5 | 55 | 14.98
45 | 83 | 0 | 13.3 | 4.2 | 9.6 | 55 | 15.108
45 | 84 | 0 | 13.3 | 4.2 | 9.7 | 55 | 15.236
45 | 85 | 0 | 13.3 | 4.2 | 9.8 | 55 | 15.364
45 | 86 | 0 | 13.3 | 4.2 | 9.9 | 55 | 15.492
45 | 87 | 0 | 13.3 | 4.2 | 10 | 55 | 15.62
45 | 88 | 0 | 13.3 | 4.3 | 3 | 55 | 10.23
45 | 89 | 0 | 13.3 | 4.3 | 3.1 | 55 | 10.3265
45 | 90 | 0 | 13.3 | 4.3 | 3.2 | 55 | 10.423
45 | 91 | 0 | 13.3 | 4.3 | 3.3 | 55 | 10.5195
45 | 92 | 0 | 13.3 | 4.3 | 3.4 | 55 | 10.616
45 | 93 | 0 | 13.3 | 4.3 | 3.5 | 55 | 10.7125
45 | 94 | 0 | 13.3 | 4.3 | 3.6 | 55 | 10.809
45 | 95 | 0 | 13.3 | 4.3 | 3.7 | 55 | 10.9055
45 | 96 | 0 | 13.3 | 4.3 | 3.8 | 55 | 11.002
45 | 97 | 0 | 13.3 | 4.3 | 3.9 | 55 | 11.0985
45 | 98 | 0 | 13.3 | 4.3 | 4 | 55 | 11.195
45 | 99 | 0 | 13.3 | 4.3 | 4.1 | 55 | 11.2915
45 | 100 | 0 | 13.3 | 4.3 | 4.2 | 55 | 11.388
45 | 101 | 0 | 13.3 | 4.3 | 4.3 | 55 | 11.4845
45 | 102 | 0 | 13.3 | 4.3 | 4.4 | 55 | 11.581
45 | 103 | 0 | 13.3 | 4.3 | 4.5 | 55 | 11.6775
45 | 104 | 0 | 13.3 | 4.3 | 4.6 | 55 | 11.774
45 | 105 | 0 | 13.3 | 4.3 | 4.7 | 55 | 11.8705
45 | 106 | 0 | 13.3 | 4.3 | 4.8 | 55 | 11.967
45 | 107 | 0 | 13.3 | 4.3 | 4.9 | 55 | 12.0635
45 | 108 | 0 | 13.3 | 4.3 | 5 | 55 | 12.16
45 | 109 | 0 | 13.3 | 4.3 | 5.1 | 55 | 12.255
45 | 110 | 0 | 13.3 | 4.3 | 5.2 | 55 | 12.35
45 | 111 | 0 | 13.3 | 4.3 | 5.3 | 55 | 12.445
45 | 112 | 0 | 13.3 | 4.3 | 5.4 | 55 | 12.54
45 | 113 | 0 | 13.3 | 4.3 | 5.5 | 55 | 12.635
45 | 114 | 0 | 13.3 | 4.3 | 5.6 | 55 | 12.73
45 | 115 | 0 | 13.3 | 4.3 | 5.7 | 55 | 12.825
45 | 116 | 0 | 13.3 | 4.3 | 5.8 | 55 | 12.92
45 | 117 | 0 | 13.3 | 4.3 | 5.9 | 55 | 13.015
45 | 118 | 0 | 13.3 | 4.3 | 6 | 55 | 13.11
45 | 119 | 0 | 13.3 | 4.3 | 6.1 | 55 | 13.205
45 | 120 | 0 | 13.3 | 4.3 | 6.2 | 55 | 13.3
45 | 121 | 0 | 13.3 | 4.3 | 6.3 | 55 | 13.395
45 | 122 | 0 | 13.3 | 4.3 | 6.4 | 55 | 13.49
45 | 123 | 0 | 13.3 | 4.3 | 6.5 | 55 | 13.585
45 | 124 | 0 | 13.3 | 4.3 | 6.6 | 55 | 13.68
45 | 125 | 0 | 13.3 | 4.3 | 6.7 | 55 | 13.775
45 | 126 | 0 | 13.3 | 4.3 | 6.8 | 55 | 13.87
45 | 127 | 0 | 13.3 | 4.3 | 6.9 | 55 | 13.965
45 | 128 | 0 | 13.3 | 4.3 | 7 | 55 | 14.06
45 | 129 | 0 | 13.3 | 4.3 | 7.1 | 55 | 14.075
45 | 130 | 0 | 13.3 | 4.3 | 7.2 | 55 | 14.09
45 | 131 | 0 | 13.3 | 4.3 | 7.3 | 55 | 14.105
45 | 132 | 0 | 13.3 | 4.3 | 7.4 | 55 | 14.12
45 | 133 | 0 | 13.3 | 4.3 | 7.5 | 55 | 14.135
45 | 134 | 0 | 13.3 | 4.3 | 7.6 | 55 | 14.15
45 | 135 | 0 | 13.3 | 4.3 | 7.7 | 55 | 14.165
45 | 136 | 0 | 13.3 | 4.3 | 7.8 | 55 | 14.18
45 | 137 | 0 | 13.3 | 4.3 | 7.9 | 55 | 14.195
45 | 138 | 0 | 13.3 | 4.3 | 8 | 55 | 14.21
45 | 139 | 0 | 13.3 | 4.3 | 8.1 | 55 | 14.225
45 | 140 | 0 | 13.3 | 4.3 | 8.2 | 55 | 14.24
45 | 141 | 0 | 13.3 | 4.3 | 8.3 | 55 | 14.255
45 | 142 | 0 | 13.3 | 4.3 | 8.4 | 55 | 14.27
45 | 143 | 0 | 13.3 | 4.3 | 8.5 | 55 | 14.285
45 | 144 | 0 | 13.3 | 4.3 | 8.6 | 55 | 14.3
45 | 145 | 0 | 13.3 | 4.3 | 8.7 | 55 | 14.315
45 | 146 | 0 | 13.3 | 4.3 | 8.8 | 55 | 14.33
45 | 147 | 0 | 13.3 | 4.3 | 8.9 | 55 | 14.345
45 | 148 | 0 | 13.3 | 4.3 | 9 | 55 | 14.36
45 | 149 | 0 | 13.3 | 4.3 | 9.1 | 55 | 14.487
45 | 150 | 0 | 13.3 | 4.3 | 9.2 | 55 | 14.614
46 | 45 | 0 | 13.32 | 4.3 | 9.3 | 55 | 14.741
46 | 46 | 0 | 13.32 | 4.3 | 9.4 | 55 | 14.868
46 | 47 | 0 | 13.32 | 4.3 | 9.5 | 55 | 14.995
46 | 48 | 0 | 13.32 | 4.3 | 9.6 | 55 | 15.122
46 | 49 | 0 | 13.32 | 4.3 | 9.7 | 55 | 15.249
46 | 50 | 0 | 13.32 | 4.3 | 9.8 | 55 | 15.376
46 | 51 | 0 | 13.32 | 4.3 | 9.9 | 55 | 15.503
46 | 52 | 0 | 13.32 | 4.3 | 10 | 55 | 15.63
46 | 53 | 0 | 13.32 | 4.4 | 3 | 55 | 10.24
46 | 54 | 0 | 13.32 | 4.4 | 3.1 | 55 | 10.337
46 | 55 | 0 | 13.32 | 4.4 | 3.2 | 55 | 10.434
46 | 56 | 0 | 13.32 | 4.4 | 3.3 | 55 | 10.531
46 | 57 | 0 | 13.32 | 4.4 | 3.4 | 55 | 10.628
46 | 58 | 0 | 13.32 | 4.4 | 3.5 | 55 | 10.725
46 | 59 | 0 | 13.32 | 4.4 | 3.6 | 55 | 10.822
46 | 60 | 0 | 13.32 | 4.4 | 3.7 | 55 | 10.919
46 | 61 | 0 | 13.32 | 4.4 | 3.8 | 55 | 11.016
46 | 62 | 0 | 13.32 | 4.4 | 3.9 | 55 | 11.113
46 | 63 | 0 | 13.32 | 4.4 | 4 | 55 | 11.21
46 | 64 | 0 | 13.32 | 4.4 | 4.1 | 55 | 11.307
46 | 65 | 0 | 13.32 | 4.4 | 4.2 | 55 | 11.404
46 | 66 | 0 | 13.32 | 4.4 | 4.3 | 55 | 11.501
46 | 67 | 0 | 13.32 | 4.4 | 4.4 | 55 | 11.598
46 | 68 | 0 | 13.32 | 4.4 | 4.5 | 55 | 11.695
46 | 69 | 0 | 13.32 | 4.4 | 4.6 | 55 | 11.792
46 | 70 | 0 | 13.32 | 4.4 | 4.7 | 55 | 11.889
46 | 71 | 0 | 13.32 | 4.4 | 4.8 | 55 | 11.986
46 | 72 | 0 | 13.32 | 4.4 | 4.9 | 55 | 12.083
46 | 73 | 0 | 13.32 | 4.4 | 5 | 55 | 12.18
46 | 74 | 0 | 13.32 | 4.4 | 5.1 | 55 | 12.275
46 | 75 | 0 | 13.32 | 4.4 | 5.2 | 55 | 12.37
46 | 76 | 0 | 13.32 | 4.4 | 5.3 | 55 | 12.465
46 | 77 | 0 | 13.32 | 4.4 | 5.4 | 55 | 12.56
46 | 78 | 0 | 13.32 | 4.4 | 5.5 | 55 | 12.655
46 | 79 | 0 | 13.32 | 4.4 | 5.6 | 55 | 12.75
46 | 80 | 0 | 13.32 | 4.4 | 5.7 | 55 | 12.845
46 | 81 | 0 | 13.32 | 4.4 | 5.8 | 55 | 12.94
46 | 82 | 0 | 13.32 | 4.4 | 5.9 | 55 | 13.035
46 | 83 | 0 | 13.32 | 4.4 | 6 | 55 | 13.13
46 | 84 | 0 | 13.32 | 4.4 | 6.1 | 55 | 13.225
46 | 85 | 0 | 13.32 | 4.4 | 6.2 | 55 | 13.32
46 | 86 | 0 | 13.32 | 4.4 | 6.3 | 55 | 13.415
46 | 87 | 0 | 13.32 | 4.4 | 6.4 | 55 | 13.51
46 | 88 | 0 | 13.32 | 4.4 | 6.5 | 55 | 13.605
46 | 89 | 0 | 13.32 | 4.4 | 6.6 | 55 | 13.7
46 | 90 | 0 | 13.32 | 4.4 | 6.7 | 55 | 13.795
46 | 91 | 0 | 13.32 | 4.4 | 6.8 | 55 | 13.89
46 | 92 | 0 | 13.32 | 4.4 | 6.9 | 55 | 13.985
46 | 93 | 0 | 13.32 | 4.4 | 7 | 55 | 14.08
46 | 94 | 0 | 13.32 | 4.4 | 7.1 | 55 | 14.095
46 | 95 | 0 | 13.32 | 4.4 | 7.2 | 55 | 14.11
46 | 96 | 0 | 13.32 | 4.4 | 7.3 | 55 | 14.125
46 | 97 | 0 | 13.32 | 4.4 | 7.4 | 55 | 14.14
46 | 98 | 0 | 13.32 | 4.4 | 7.5 | 55 | 14.155
46 | 99 | 0 | 13.32 | 4.4 | 7.6 | 55 | 14.17
46 | 100 | 0 | 13.32 | 4.4 | 7.7 | 55 | 14.185
46 | 101 | 0 | 13.32 | 4.4 | 7.8 | 55 | 14.2
46 | 102 | 0 | 13.32 | 4.4 | 7.9 | 55 | 14.215
46 | 103 | 0 | 13.32 | 4.4 | 8 | 55 | 14.23
46 | 104 | 0 | 13.32 | 4.4 | 8.1 | 55 | 14.245
46 | 105 | 0 | 13.32 | 4.4 | 8.2 | 55 | 14.26
46 | 106 | 0 | 13.32 | 4.4 | 8.3 | 55 | 14.275
46 | 107 | 0 | 13.32 | 4.4 | 8.4 | 55 | 14.29
46 | 108 | 0 | 13.32 | 4.4 | 8.5 | 55 | 14.305
46 | 109 | 0 | 13.32 | 4.4 | 8.6 | 55 | 14.32
46 | 110 | 0 | 13.32 | 4.4 | 8.7 | 55 | 14.335
46 | 111 | 0 | 13.32 | 4.4 | 8.8 | 55 | 14.35
46 | 112 | 0 | 13.32 | 4.4 | 8.9 | 55 | 14.365
46 | 113 | 0 | 13.32 | 4.4 | 9 | 55 | 14.38
46 | 114 | 0 | 13.32 | 4.4 | 9.1 | 55 | 14.506
46 | 115 | 0 | 13.32 | 4.4 | 9.2 | 55 | 14.632
46 | 116 | 0 | 13.32 | 4.4 | 9.3 | 55 | 14.758
46 | 117 | 0 | 13.32 | 4.4 | 9.4 | 55 | 14.884
46 | 118 | 0 | 13.32 | 4.4 | 9.5 | 55 | 15.01
46 | 119 | 0 | 13.32 | 4.4 | 9.6 | 55 | 15.136
46 | 120 | 0 | 13.32 | 4.4 | 9.7 | 55 | 15.262
46 | 121 | 0 | 13.32 | 4.4 | 9.8 | 55 | 15.388
46 | 122 | 0 | 13.32 | 4.4 | 9.9 | 55 | 15.514
46 | 123 | 0 | 13.32 | 4.4 | 10 | 55 | 15.64
46 | 124 | 0 | 13.32 | 4.5 | 3 | 55 | 10.25
46 | 125 | 0 | 13.32 | 4.5 | 3.1 | 55 | 10.3475
46 | 126 | 0 | 13.32 | 4.5 | 3.2 | 55 | 10.445
46 | 127 | 0 | 13.32 | 4.5 | 3.3 | 55 | 10.5425
46 | 128 | 0 | 13.32 | 4.5 | 3.4 | 55 | 10.64
46 | 129 | 0 | 13.32 | 4.5 | 3.5 | 55 | 10.7375
46 | 130 | 0 | 13.32 | 4.5 | 3.6 | 55 | 10.835
46 | 131 | 0 | 13.32 | 4.5 | 3.7 | 55 | 10.9325
46 | 132 | 0 | 13.32 | 4.5 | 3.8 | 55 | 11.03
46 | 133 | 0 | 13.32 | 4.5 | 3.9 | 55 | 11.1275
46 | 134 | 0 | 13.32 | 4.5 | 4 | 55 | 11.225
46 | 135 | 0 | 13.32 | 4.5 | 4.1 | 55 | 11.3225
46 | 136 | 0 | 13.32 | 4.5 | 4.2 | 55 | 11.42
46 | 137 | 0 | 13.32 | 4.5 | 4.3 | 55 | 11.5175
46 | 138 | 0 | 13.32 | 4.5 | 4.4 | 55 | 11.615
46 | 139 | 0 | 13.32 | 4.5 | 4.5 | 55 | 11.7125
46 | 140 | 0 | 13.32 | 4.5 | 4.6 | 55 | 11.81
46 | 141 | 0 | 13.32 | 4.5 | 4.7 | 55 | 11.9075
46 | 142 | 0 | 13.32 | 4.5 | 4.8 | 55 | 12.005
46 | 143 | 0 | 13.32 | 4.5 | 4.9 | 55 | 12.1025
46 | 144 | 0 | 13.32 | 4.5 | 5 | 55 | 12.2
46 | 145 | 0 | 13.32 | 4.5 | 5.1 | 55 | 12.295
46 | 146 | 0 | 13.32 | 4.5 | 5.2 | 55 | 12.39
46 | 147 | 0 | 13.32 | 4.5 | 5.3 | 55 | 12.485
46 | 148 | 0 | 13.32 | 4.5 | 5.4 | 55 | 12.58
46 | 149 | 0 | 13.32 | 4.5 | 5.5 | 55 | 12.675
46 | 150 | 0 | 13.32 | 4.5 | 5.6 | 55 | 12.77
47 | 45 | 0 | 13.34 | 4.5 | 5.7 | 55 | 12.865
47 | 46 | 0 | 13.34 | 4.5 | 5.8 | 55 | 12.96
47 | 47 | 0 | 13.34 | 4.5 | 5.9 | 55 | 13.055
47 | 48 | 0 | 13.34 | 4.5 | 6 | 55 | 13.15
47 | 49 | 0 | 13.34 | 4.5 | 6.1 | 55 | 13.245
47 | 50 | 0 | 13.34 | 4.5 | 6.2 | 55 | 13.34
47 | 51 | 0 | 13.34 | 4.5 | 6.3 | 55 | 13.435
47 | 52 | 0 | 13.34 | 4.5 | 6.4 | 55 | 13.53
47 | 53 | 0 | 13.34 | 4.5 | 6.5 | 55 | 13.625
47 | 54 | 0 | 13.34 | 4.5 | 6.6 | 55 | 13.72
47 | 55 | 0 | 13.34 | 4.5 | 6.7 | 55 | 13.815
47 | 56 | 0 | 13.34 | 4.5 | 6.8 | 55 | 13.91
47 | 57 | 0 | 13.34 | 4.5 | 6.9 | 55 | 14.005
47 | 58 | 0 | 13.34 | 4.5 | 7 | 55 | 14.1
47 | 59 | 0 | 13.34 | 4.5 | 7.1 | 55 | 14.115
47 | 60 | 0 | 13.34 | 4.5 | 7.2 | 55 | 14.13
47 | 61 | 0 | 13.34 | 4.5 | 7.3 | 55 | 14.145
47 | 62 | 0 | 13.34 | 4.5 | 7.4 | 55 | 14.16
47 | 63 | 0 | 13.34 | 4.5 | 7.5 | 55 | 14.175
47 | 64 | 0 | 13.34 | 4.5 | 7.6 | 55 | 14.19
47 | 65 | 0 | 13.34 | 4.5 | 7.7 | 55 | 14.205
47 | 66 | 0 | 13.34 | 4.5 | 7.8 | 55 | 14.22
47 | 67 | 0 | 13.34 | 4.5 | 7.9 | 55 | 14.235
47 | 68 | 0 | 13.34 | 4.5 | 8 | 55 | 14.25
47 | 69 | 0 | 13.34 | 4.5 | 8.1 | 55 | 14.265
47 | 70 | 0 | 13.34 | 4.5 | 8.2 | 55 | 14.28
47 | 71 | 0 | 13.34 | 4.5 | 8.3 | 55 | 14.295
47 | 72 | 0 | 13.34 | 4.5 | 8.4 | 55 | 14.31
47 | 73 | 0 | 13.34 | 4.5 | 8.5 | 55 | 14.325
47 | 74 | 0 | 13.34 | 4.5 | 8.6 | 55 | 14.34
47 | 75 | 0 | 13.34 | 4.5 | 8.7 | 55 | 14.355
47 | 76 | 0 | 13.34 | 4.5 | 8.8 | 55 | 14.37
47 | 77 | 0 | 13.34 | 4.5 | 8.9 | 55 | 14.385
47 | 78 | 0 | 13.34 | 4.5 | 9 | 55 | 14.4
47 | 79 | 0 | 13.34 | 4.5 | 9.1 | 55 | 14.525
47 | 80 | 0 | 13.34 | 4.5 | 9.2 | 55 | 14.65
47 | 81 | 0 | 13.34 | 4.5 | 9.3 | 55 | 14.775
47 | 82 | 0 | 13.34 | 4.5 | 9.4 | 55 | 14.9
47 | 83 | 0 | 13.34 | 4.5 | 9.5 | 55 | 15.025
47 | 84 | 0 | 13.34 | 4.5 | 9.6 | 55 | 15.15
47 | 85 | 0 | 13.34 | 4.5 | 9.7 | 55 | 15.275
47 | 86 | 0 | 13.34 | 4.5 | 9.8 | 55 | 15.4
47 | 87 | 0 | 13.34 | 4.5 | 9.9 | 55 | 15.525
47 | 88 | 0 | 13.34 | 4.5 | 10 | 55 | 15.65
47 | 89 | 0 | 13.34 | 4.6 | 3 | 55 | 10.26
47 | 90 | 0 | 13.34 | 4.6 | 3.1 | 55 | 10.358
47 | 91 | 0 | 13.34 | 4.6 | 3.2 | 55 | 10.456
47 | 92 | 0 | 13.34 | 4.6 | 3.3 | 55 | 10.554
47 | 93 | 0 | 13.34 | 4.6 | 3.4 | 55 | 10.652
47 | 94 | 0 | 13.34 | 4.6 | 3.5 | 55 | 10.75
47 | 95 | 0 | 13.34 | 4.6 | 3.6 | 55 | 10.848
47 | 96 | 0 | 13.34 | 4.6 | 3.7 | 55 | 10.946
47 | 97 | 0 | 13.34 | 4.6 | 3.8 | 55 | 11.044
47 | 98 | 0 | 13.34 | 4.6 | 3.9 | 55 | 11.142
47 | 99 | 0 | 13.34 | 4.6 | 4 | 55 | 11.24
47 | 100 | 0 | 13.34 | 4.6 | 4.1 | 55 | 11.338
47 | 101 | 0 | 13.34 | 4.6 | 4.2 | 55 | 11.436
47 | 102 | 0 | 13.34 | 4.6 | 4.3 | 55 | 11.534
47 | 103 | 0 | 13.34 | 4.6 | 4.4 | 55 | 11.632
47 | 104 | 0 | 13.34 | 4.6 | 4.5 | 55 | 11.73
47 | 105 | 0 | 13.34 | 4.6 | 4.6 | 55 | 11.828
47 | 106 | 0 | 13.34 | 4.6 | 4.7 | 55 | 11.926
47 | 107 | 0 | 13.34 | 4.6 | 4.8 | 55 | 12.024
47 | 108 | 0 | 13.34 | 4.6 | 4.9 | 55 | 12.122
47 | 109 | 0 | 13.34 | 4.6 | 5 | 55 | 12.22
47 | 110 | 0 | 13.34 | 4.6 | 5.1 | 55 | 12.315
47 | 111 | 0 | 13.34 | 4.6 | 5.2 | 55 | 12.41
47 | 112 | 0 | 13.34 | 4.6 | 5.3 | 55 | 12.505
47 | 113 | 0 | 13.34 | 4.6 | 5.4 | 55 | 12.6
47 | 114 | 0 | 13.34 | 4.6 | 5.5 | 55 | 12.695
47 | 115 | 0 | 13.34 | 4.6 | 5.6 | 55 | 12.79
47 | 116 | 0 | 13.34 | 4.6 | 5.7 | 55 | 12.885
47 | 117 | 0 | 13.34 | 4.6 | 5.8 | 55 | 12.98
47 | 118 | 0 | 13.34 | 4.6 | 5.9 | 55 | 13.075
47 | 119 | 0 | 13.34 | 4.6 | 6 | 55 | 13.17
47 | 120 | 0 | 13.34 | 4.6 | 6.1 | 55 | 13.265
47 | 121 | 0 | 13.34 | 4.6 | 6.2 | 55 | 13.36
47 | 122 | 0 | 13.34 | 4.6 | 6.3 | 55 | 13.455
47 | 123 | 0 | 13.34 | 4.6 | 6.4 | 55 | 13.55
47 | 124 | 0 | 13.34 | 4.6 | 6.5 | 55 | 13.645
47 | 125 | 0 | 13.34 | 4.6 | 6.6 | 55 | 13.74
47 | 126 | 0 | 13.34 | 4.6 | 6.7 | 55 | 13.835
47 | 127 | 0 | 13.34 | 4.6 | 6.8 | 55 | 13.93
47 | 128 | 0 | 13.34 | 4.6 | 6.9 | 55 | 14.025
47 | 129 | 0 | 13.34 | 4.6 | 7 | 55 | 14.12
47 | 130 | 0 | 13.34 | 4.6 | 7.1 | 55 | 14.135
47 | 131 | 0 | 13.34 | 4.6 | 7.2 | 55 | 14.15
47 | 132 | 0 | 13.34 | 4.6 | 7.3 | 55 | 14.165
47 | 133 | 0 | 13.34 | 4.6 | 7.4 | 55 | 14.18
47 | 134 | 0 | 13.34 | 4.6 | 7.5 | 55 | 14.195
47 | 135 | 0 | 13.34 | 4.6 | 7.6 | 55 | 14.21
47 | 136 | 0 | 13.34 | 4.6 | 7.7 | 55 | 14.225
47 | 137 | 0 | 13.34 | 4.6 | 7.8 | 55 | 14.24
47 | 138 | 0 | 13.34 | 4.6 | 7.9 | 55 | 14.255
47 | 139 | 0 | 13.34 | 4.6 | 8 | 55 | 14.27
47 | 140 | 0 | 13.34 | 4.6 | 8.1 | 55 | 14.285
47 | 141 | 0 | 13.34 | 4.6 | 8.2 | 55 | 14.3
47 | 142 | 0 | 13.34 | 4.6 | 8.3 | 55 | 14.315
47 | 143 | 0 | 13.34 | 4.6 | 8.4 | 55 | 14.33
47 | 144 | 0 | 13.34 | 4.6 | 8.5 | 55 | 14.345
47 | 145 | 0 | 13.34 | 4.6 | 8.6 | 55 | 14.36
47 | 146 | 0 | 13.34 | 4.6 | 8.7 | 55 | 14.375
47 | 147 | 0 | 13.34 | 4.6 | 8.8 | 55 | 14.39
47 | 148 | 0 | 13.34 | 4.6 | 8.9 | 55 | 14.405
47 | 149 | 0 | 13.34 | 4.6 | 9 | 55 | 14.42
47 | 150 | 0 | 13.34 | 4.6 | 9.1 | 55 | 14.544
48 | 45 | 0 | 13.36 | 4.6 | 9.2 | 55 | 14.668
48 | 46 | 0 | 13.36 | 4.6 | 9.3 | 55 | 14.792
48 | 47 | 0 | 13.36 | 4.6 | 9.4 | 55 | 14.916
48 | 48 | 0 | 13.36 | 4.6 | 9.5 | 55 | 15.04
48 | 49 | 0 | 13.36 | 4.6 | 9.6 | 55 | 15.164
48 | 50 | 0 | 13.36 | 4.6 | 9.7 | 55 | 15.288
48 | 51 | 0 | 13.36 | 4.6 | 9.8 | 55 | 15.412
48 | 52 | 0 | 13.36 | 4.6 | 9.9 | 55 | 15.536
48 | 53 | 0 | 13.36 | 4.6 | 10 | 55 | 15.66
48 | 54 | 0 | 13.36 | 4.7 | 3 | 55 | 10.27
48 | 55 | 0 | 13.36 | 4.7 | 3.1 | 55 | 10.3685
48 | 56 | 0 | 13.36 | 4.7 | 3.2 | 55 | 10.467
48 | 57 | 0 | 13.36 | 4.7 | 3.3 | 55 | 10.5655
48 | 58 | 0 | 13.36 | 4.7 | 3.4 | 55 | 10.664
48 | 59 | 0 | 13.36 | 4.7 | 3.5 | 55 | 10.7625
48 | 60 | 0 | 13.36 | 4.7 | 3.6 | 55 | 10.861
48 | 61 | 0 | 13.36 | 4.7 | 3.7 | 55 | 10.9595
48 | 62 | 0 | 13.36 | 4.7 | 3.8 | 55 | 11.058
48 | 63 | 0 | 13.36 | 4.7 | 3.9 | 55 | 11.1565
48 | 64 | 0 | 13.36 | 4.7 | 4 | 55 | 11.255
48 | 65 | 0 | 13.36 | 4.7 | 4.1 | 55 | 11.3535
48 | 66 | 0 | 13.36 | 4.7 | 4.2 | 55 | 11.452
48 | 67 | 0 | 13.36 | 4.7 | 4.3 | 55 | 11.5505
48 | 68 | 0 | 13.36 | 4.7 | 4.4 | 55 | 11.649
48 | 69 | 0 | 13.36 | 4.7 | 4.5 | 55 | 11.7475
48 | 70 | 0 | 13.36 | 4.7 | 4.6 | 55 | 11.846
48 | 71 | 0 | 13.36 | 4.7 | 4.7 | 55 | 11.9445
48 | 72 | 0 | 13.36 | 4.7 | 4.8 | 55 | 12.043
48 | 73 | 0 | 13.36 | 4.7 | 4.9 | 55 | 12.1415
48 | 74 | 0 | 13.36 | 4.7 | 5 | 55 | 12.24
48 | 75 | 0 | 13.36 | 4.7 | 5.1 | 55 | 12.335
48 | 76 | 0 | 13.36 | 4.7 | 5.2 | 55 | 12.43
48 | 77 | 0 | 13.36 | 4.7 | 5.3 | 55 | 12.525
48 | 78 | 0 | 13.36 | 4.7 | 5.4 | 55 | 12.62
48 | 79 | 0 | 13.36 | 4.7 | 5.5 | 55 | 12.715
48 | 80 | 0 | 13.36 | 4.7 | 5.6 | 55 | 12.81
48 | 81 | 0 | 13.36 | 4.7 | 5.7 | 55 | 12.905
48 | 82 | 0 | 13.36 | 4.7 | 5.8 | 55 | 13
48 | 83 | 0 | 13.36 | 4.7 | 5.9 | 55 | 13.095
48 | 84 | 0 | 13.36 | 4.7 | 6 | 55 | 13.19
48 | 85 | 0 | 13.36 | 4.7 | 6.1 | 55 | 13.285
48 | 86 | 0 | 13.36 | 4.7 | 6.2 | 55 | 13.38
48 | 87 | 0 | 13.36 | 4.7 | 6.3 | 55 | 13.475
48 | 88 | 0 | 13.36 | 4.7 | 6.4 | 55 | 13.57
48 | 89 | 0 | 13.36 | 4.7 | 6.5 | 55 | 13.665
48 | 90 | 0 | 13.36 | 4.7 | 6.6 | 55 | 13.76
48 | 91 | 0 | 13.36 | 4.7 | 6.7 | 55 | 13.855
48 | 92 | 0 | 13.36 | 4.7 | 6.8 | 55 | 13.95
48 | 93 | 0 | 13.36 | 4.7 | 6.9 | 55 | 14.045
48 | 94 | 0 | 13.36 | 4.7 | 7 | 55 | 14.14
48 | 95 | 0 | 13.36 | 4.7 | 7.1 | 55 | 14.155
48 | 96 | 0 | 13.36 | 4.7 | 7.2 | 55 | 14.17
48 | 97 | 0 | 13.36 | 4.7 | 7.3 | 55 | 14.185
48 | 98 | 0 | 13.36 | 4.7 | 7.4 | 55 | 14.2
48 | 99 | 0 | 13.36 | 4.7 | 7.5 | 55 | 14.215
48 | 100 | 0 | 13.36 | 4.7 | 7.6 | 55 | 14.23
48 | 101 | 0 | 13.36 | 4.7 | 7.7 | 55 | 14.245
48 | 102 | 0 | 13.36 | 4.7 | 7.8 | 55 | 14.26
48 | 103 | 0 | 13.36 | 4.7 | 7.9 | 55 | 14.275
48 | 104 | 0 | 13.36 | 4.7 | 8 | 55 | 14.29
48 | 105 | 0 | 13.36 | 4.7 | 8.1 | 55 | 14.305
48 | 106 | 0 | 13.36 | 4.7 | 8.2 | 55 | 14.32
48 | 107 | 0 | 13.36 | 4.7 | 8.3 | 55 | 14.335
48 | 108 | 0 | 13.36 | 4.7 | 8.4 | 55 | 14.35
48 | 109 | 0 | 13.36 | 4.7 | 8.5 | 55 | 14.365
48 | 110 | 0 | 13.36 | 4.7 | 8.6 | 55 | 14.38
48 | 111 | 0 | 13.36 | 4.7 | 8.7 | 55 | 14.395
48 | 112 | 0 | 13.36 | 4.7 | 8.8 | 55 | 14.41
48 | 113 | 0 | 13.36 | 4.7 | 8.9 | 55 | 14.425
48 | 114 | 0 | 13.36 | 4.7 | 9 | 55 | 14.44
48 | 115 | 0 | 13.36 | 4.7 | 9.1 | 55 | 14.563
48 | 116 | 0 | 13.36 | 4.7 | 9.2 | 55 | 14.686
48 | 117 | 0 | 13.36 | 4.7 | 9.3 | 55 | 14.809
48 | 118 | 0 | 13.36 | 4.7 | 9.4 | 55 | 14.932
48 | 119 | 0 | 13.36 | 4.7 | 9.5 | 55 | 15.055
48 | 120 | 0 | 13.36 | 4.7 | 9.6 | 55 | 15.178
48 | 121 | 0 | 13.36 | 4.7 | 9.7 | 55 | 15.301
48 | 122 | 0 | 13.36 | 4.7 | 9.8 | 55 | 15.424
48 | 123 | 0 | 13.36 | 4.7 | 9.9 | 55 | 15.547
48 | 124 | 0 | 13.36 | 4.7 | 10 | 55 | 15.67
48 | 125 | 0 | 13.36 | 4.8 | 3 | 55 | 10.28
48 | 126 | 0 | 13.36 | 4.8 | 3.1 | 55 | 10.379
48 | 127 | 0 | 13.36 | 4.8 | 3.2 | 55 | 10.478
48 | 128 | 0 | 13.36 | 4.8 | 3.3 | 55 | 10.577
48 | 129 | 0 | 13.36 | 4.8 | 3.4 | 55 | 10.676
48 | 130 | 0 | 13.36 | 4.8 | 3.5 | 55 | 10.775
48 | 131 | 0 | 13.36 | 4.8 | 3.6 | 55 | 10.874
48 | 132 | 0 | 13.36 | 4.8 | 3.7 | 55 | 10.973
48 | 133 | 0 | 13.36 | 4.8 | 3.8 | 55 | 11.072
48 | 134 | 0 | 13.36 | 4.8 | 3.9 | 55 | 11.171
48 | 135 | 0 | 13.36 | 4.8 | 4 | 55 | 11.27
48 | 136 | 0 | 13.36 | 4.8 | 4.1 | 55 | 11.369
48 | 137 | 0 | 13.36 | 4.8 | 4.2 | 55 | 11.468
48 | 138 | 0 | 13.36 | 4.8 | 4.3 | 55 | 11.567
48 | 139 | 0 | 13.36 | 4.8 | 4.4 | 55 | 11.666
48 | 140 | 0 | 13.36 | 4.8 | 4.5 | 55 | 11.765
48 | 141 | 0 | 13.36 | 4.8 | 4.6 | 55 | 11.864
48 | 142 | 0 | 13.36 | 4.8 | 4.7 | 55 | 11.963
48 | 143 | 0 | 13.36 | 4.8 | 4.8 | 55 | 12.062
48 | 144 | 0 | 13.36 | 4.8 | 4.9 | 55 | 12.161
48 | 145 | 0 | 13.36 | 4.8 | 5 | 55 | 12.26
48 | 146 | 0 | 13.36 | 4.8 | 5.1 | 55 | 12.355
48 | 147 | 0 | 13.36 | 4.8 | 5.2 | 55 | 12.45
48 | 148 | 0 | 13.36 | 4.8 | 5.3 | 55 | 12.545
48 | 149 | 0 | 13.36 | 4.8 | 5.4 | 55 | 12.64
48 | 150 | 0 | 13.36 | 4.8 | 5.5 | 55 | 12.735
49 | 45 | 0 | 13.38 | 4.8 | 5.6 | 55 | 12.83
49 | 46 | 0 | 13.38 | 4.8 | 5.7 | 55 | 12.925
49 | 47 | 0 | 13.38 | 4.8 | 5.8 | 55 | 13.02
49 | 48 | 0 | 13.38 | 4.8 | 5.9 | 55 | 13.115
49 | 49 | 0 | 13.38 | 4.8 | 6 | 55 | 13.21
49 | 50 | 0 | 13.38 | 4.8 | 6.1 | 55 | 13.305
49 | 51 | 0 | 13.38 | 4.8 | 6.2 | 55 | 13.4
49 | 52 | 0 | 13.38 | 4.8 | 6.3 | 55 | 13.495
49 | 53 | 0 | 13.38 | 4.8 | 6.4 | 55 | 13.59
49 | 54 | 0 | 13.38 | 4.8 | 6.5 | 55 | 13.685
49 | 55 | 0 | 13.38 | 4.8 | 6.6 | 55 | 13.78
49 | 56 | 0 | 13.38 | 4.8 | 6.7 | 55 | 13.875
49 | 57 | 0 | 13.38 | 4.8 | 6.8 | 55 | 13.97
49 | 58 | 0 | 13.38 | 4.8 | 6.9 | 55 | 14.065
49 | 59 | 0 | 13.38 | 4.8 | 7 | 55 | 14.16
49 | 60 | 0 | 13.38 | 4.8 | 7.1 | 55 | 14.175
49 | 61 | 0 | 13.38 | 4.8 | 7.2 | 55 | 14.19
49 | 62 | 0 | 13.38 | 4.8 | 7.3 | 55 | 14.205
49 | 63 | 0 | 13.38 | 4.8 | 7.4 | 55 | 14.22
49 | 64 | 0 | 13.38 | 4.8 | 7.5 | 55 | 14.235
49 | 65 | 0 | 13.38 | 4.8 | 7.6 | 55 | 14.25
49 | 66 | 0 | 13.38 | 4.8 | 7.7 | 55 | 14.265
49 | 67 | 0 | 13.38 | 4.8 | 7.8 | 55 | 14.28
49 | 68 | 0 | 13.38 | 4.8 | 7.9 | 55 | 14.295
49 | 69 | 0 | 13.38 | 4.8 | 8 | 55 | 14.31
49 | 70 | 0 | 13.38 | 4.8 | 8.1 | 55 | 14.325
49 | 71 | 0 | 13.38 | 4.8 | 8.2 | 55 | 14.34
49 | 72 | 0 | 13.38 | 4.8 | 8.3 | 55 | 14.355
49 | 73 | 0 | 13.38 | 4.8 | 8.4 | 55 | 14.37
49 | 74 | 0 | 13.38 | 4.8 | 8.5 | 55 | 14.385
49 | 75 | 0 | 13.38 | 4.8 | 8.6 | 55 | 14.4
49 | 76 | 0 | 13.38 | 4.8 | 8.7 | 55 | 14.415
49 | 77 | 0 | 13.38 | 4.8 | 8.8 | 55 | 14.43
49 | 78 | 0 | 13.38 | 4.8 | 8.9 | 55 | 14.445
49 | 79 | 0 | 13.38 | 4.8 | 9 | 55 | 14.46
49 | 80 | 0 | 13.38 | 4.8 | 9.1 | 55 | 14.582
49 | 81 | 0 | 13.38 | 4.8 | 9.2 | 55 | 14.704
49 | 82 | 0 | 13.38 | 4.8 | 9.3 | 55 | 14.826
49 | 83 | 0 | 13.38 | 4.8 | 9.4 | 55 | 14.948
49 | 84 | 0 | 13.38 | 4.8 | 9.5 | 55 | 15.07
49 | 85 | 0 | 13.38 | 4.8 | 9.6 | 55 | 15.192
49 | 86 | 0 | 13.38 | 4.8 | 9.7 | 55 | 15.314
49 | 87 | 0 | 13.38 | 4.8 | 9.8 | 55 | 15.436
49 | 88 | 0 | 13.38 | 4.8 | 9.9 | 55 | 15.558
49 | 89 | 0 | 13.38 | 4.8 | 10 | 55 | 15.68
49 | 90 | 0 | 13.38 | 4.9 | 3 | 55 | 10.29
49 | 91 | 0 | 13.38 | 4.9 | 3.1 | 55 | 10.3895
49 | 92 | 0 | 13.38 | 4.9 | 3.2 | 55 | 10.489
49 | 93 | 0 | 13.38 | 4.9 | 3.3 | 55 | 10.5885
49 | 94 | 0 | 13.38 | 4.9 | 3.4 | 55 | 10.688
49 | 95 | 0 | 13.38 | 4.9 | 3.5 | 55 | 10.7875
49 | 96 | 0 | 13.38 | 4.9 | 3.6 | 55 | 10.887
49 | 97 | 0 | 13.38 | 4.9 | 3.7 | 55 | 10.9865
49 | 98 | 0 | 13.38 | 4.9 | 3.8 | 55 | 11.086
49 | 99 | 0 | 13.38 | 4.9 | 3.9 | 55 | 11.1855
49 | 100 | 0 | 13.38 | 4.9 | 4 | 55 | 11.285
49 | 101 | 0 | 13.38 | 4.9 | 4.1 | 55 | 11.3845
49 | 102 | 0 | 13.38 | 4.9 | 4.2 | 55 | 11.484
49 | 103 | 0 | 13.38 | 4.9 | 4.3 | 55 | 11.5835
49 | 104 | 0 | 13.38 | 4.9 | 4.4 | 55 | 11.683
49 | 105 | 0 | 13.38 | 4.9 | 4.5 | 55 | 11.7825
49 | 106 | 0 | 13.38 | 4.9 | 4.6 | 55 | 11.882
49 | 107 | 0 | 13.38 | 4.9 | 4.7 | 55 | 11.9815
49 | 108 | 0 | 13.38 | 4.9 | 4.8 | 55 | 12.081
49 | 109 | 0 | 13.38 | 4.9 | 4.9 | 55 | 12.1805
49 | 110 | 0 | 13.38 | 4.9 | 5 | 55 | 12.28
49 | 111 | 0 | 13.38 | 4.9 | 5.1 | 55 | 12.375
49 | 112 | 0 | 13.38 | 4.9 | 5.2 | 55 | 12.47
49 | 113 | 0 | 13.38 | 4.9 | 5.3 | 55 | 12.565
49 | 114 | 0 | 13.38 | 4.9 | 5.4 | 55 | 12.66
49 | 115 | 0 | 13.38 | 4.9 | 5.5 | 55 | 12.755
49 | 116 | 0 | 13.38 | 4.9 | 5.6 | 55 | 12.85
49 | 117 | 0 | 13.38 | 4.9 | 5.7 | 55 | 12.945
49 | 118 | 0 | 13.38 | 4.9 | 5.8 | 55 | 13.04
49 | 119 | 0 | 13.38 | 4.9 | 5.9 | 55 | 13.135
49 | 120 | 0 | 13.38 | 4.9 | 6 | 55 | 13.23
49 | 121 | 0 | 13.38 | 4.9 | 6.1 | 55 | 13.325
49 | 122 | 0 | 13.38 | 4.9 | 6.2 | 55 | 13.42
49 | 123 | 0 | 13.38 | 4.9 | 6.3 | 55 | 13.515
49 | 124 | 0 | 13.38 | 4.9 | 6.4 | 55 | 13.61
49 | 125 | 0 | 13.38 | 4.9 | 6.5 | 55 | 13.705
49 | 126 | 0 | 13.38 | 4.9 | 6.6 | 55 | 13.8
49 | 127 | 0 | 13.38 | 4.9 | 6.7 | 55 | 13.895
49 | 128 | 0 | 13.38 | 4.9 | 6.8 | 55 | 13.99
49 | 129 | 0 | 13.38 | 4.9 | 6.9 | 55 | 14.085
49 | 130 | 0 | 13.38 | 4.9 | 7 | 55 | 14.18
49 | 131 | 0 | 13.38 | 4.9 | 7.1 | 55 | 14.195
49 | 132 | 0 | 13.38 | 4.9 | 7.2 | 55 | 14.21
49 | 133 | 0 | 13.38 | 4.9 | 7.3 | 55 | 14.225
49 | 134 | 0 | 13.38 | 4.9 | 7.4 | 55 | 14.24
49 | 135 | 0 | 13.38 | 4.9 | 7.5 | 55 | 14.255
49 | 136 | 0 | 13.38 | 4.9 | 7.6 | 55 | 14.27
49 | 137 | 0 | 13.38 | 4.9 | 7.7 | 55 | 14.285
49 | 138 | 0 | 13.38 | 4.9 | 7.8 | 55 | 14.3
49 | 139 | 0 | 13.38 | 4.9 | 7.9 | 55 | 14.315
49 | 140 | 0 | 13.38 | 4.9 | 8 | 55 | 14.33
49 | 141 | 0 | 13.38 | 4.9 | 8.1 | 55 | 14.345
49 | 142 | 0 | 13.38 | 4.9 | 8.2 | 55 | 14.36
49 | 143 | 0 | 13.38 | 4.9 | 8.3 | 55 | 14.375
49 | 144 | 0 | 13.38 | 4.9 | 8.4 | 55 | 14.39
49 | 145 | 0 | 13.38 | 4.9 | 8.5 | 55 | 14.405
49 | 146 | 0 | 13.38 | 4.9 | 8.6 | 55 | 14.42
49 | 147 | 0 | 13.38 | 4.9 | 8.7 | 55 | 14.435
49 | 148 | 0 | 13.38 | 4.9 | 8.8 | 55 | 14.45
49 | 149 | 0 | 13.38 | 4.9 | 8.9 | 55 | 14.465
49 | 150 | 0 | 13.38 | 4.9 | 9 | 55 | 14.48
50 | 45 | 0 | 13.4 | 4.9 | 9.1 | 55 | 14.601
50 | 46 | 0 | 13.4 | 4.9 | 9.2 | 55 | 14.722
50 | 47 | 0 | 13.4 | 4.9 | 9.3 | 55 | 14.843
50 | 48 | 0 | 13.4 | 4.9 | 9.4 | 55 | 14.964
50 | 49 | 0 | 13.4 | 4.9 | 9.5 | 55 | 15.085
50 | 50 | 0 | 13.4 | 4.9 | 9.6 | 55 | 15.206
50 | 51 | 0 | 13.4 | 4.9 | 9.7 | 55 | 15.327
50 | 52 | 0 | 13.4 | 4.9 | 9.8 | 55 | 15.448
50 | 53 | 0 | 13.4 | 4.9 | 9.9 | 55 | 15.569
50 | 54 | 0 | 13.4 | 4.9 | 10 | 55 | 15.69
50 | 55 | 0 | 13.4 | 5 | 3 | 55 | 10.3
50 | 56 | 0 | 13.4 | 5 | 3.1 | 55 | 10.4
50 | 57 | 0 | 13.4 | 5 | 3.2 | 55 | 10.5
50 | 58 | 0 | 13.4 | 5 | 3.3 | 55 | 10.6
50 | 59 | 0 | 13.4 | 5 | 3.4 | 55 | 10.7
50 | 60 | 0 | 13.4 | 5 | 3.5 | 55 | 10.8
50 | 61 | 0 | 13.4 | 5 | 3.6 | 55 | 10.9
50 | 62 | 0 | 13.4 | 5 | 3.7 | 55 | 11
50 | 63 | 0 | 13.4 | 5 | 3.8 | 55 | 11.1
50 | 64 | 0 | 13.4 | 5 | 3.9 | 55 | 11.2
50 | 65 | 0 | 13.4 | 5 | 4 | 55 | 11.3
50 | 66 | 0 | 13.4 | 5 | 4.1 | 55 | 11.4
50 | 67 | 0 | 13.4 | 5 | 4.2 | 55 | 11.5
50 | 68 | 0 | 13.4 | 5 | 4.3 | 55 | 11.6
50 | 69 | 0 | 13.4 | 5 | 4.4 | 55 | 11.7
50 | 70 | 0 | 13.4 | 5 | 4.5 | 55 | 11.8
50 | 71 | 0 | 13.4 | 5 | 4.6 | 55 | 11.9
50 | 72 | 0 | 13.4 | 5 | 4.7 | 55 | 12
50 | 73 | 0 | 13.4 | 5 | 4.8 | 55 | 12.1
50 | 74 | 0 | 13.4 | 5 | 4.9 | 55 | 12.2
50 | 75 | 0 | 13.4 | 5 | 5 | 55 | 12.3
50 | 76 | 0 | 13.4 | 5 | 5.1 | 55 | 12.395
50 | 77 | 0 | 13.4 | 5 | 5.2 | 55 | 12.49
50 | 78 | 0 | 13.4 | 5 | 5.3 | 55 | 12.585
50 | 79 | 0 | 13.4 | 5 | 5.4 | 55 | 12.68
50 | 80 | 0 | 13.4 | 5 | 5.5 | 55 | 12.775
50 | 81 | 0 | 13.4 | 5 | 5.6 | 55 | 12.87
50 | 82 | 0 | 13.4 | 5 | 5.7 | 55 | 12.965
50 | 83 | 0 | 13.4 | 5 | 5.8 | 55 | 13.06
50 | 84 | 0 | 13.4 | 5 | 5.9 | 55 | 13.155
50 | 85 | 0 | 13.4 | 5 | 6 | 55 | 13.25
50 | 86 | 0 | 13.4 | 5 | 6.1 | 55 | 13.345
50 | 87 | 0 | 13.4 | 5 | 6.2 | 55 | 13.44
50 | 88 | 0 | 13.4 | 5 | 6.3 | 55 | 13.535
50 | 89 | 0 | 13.4 | 5 | 6.4 | 55 | 13.63
50 | 90 | 0 | 13.4 | 5 | 6.5 | 55 | 13.725
50 | 91 | 0 | 13.4 | 5 | 6.6 | 55 | 13.82
50 | 92 | 0 | 13.4 | 5 | 6.7 | 55 | 13.915
50 | 93 | 0 | 13.4 | 5 | 6.8 | 55 | 14.01
50 | 94 | 0 | 13.4 | 5 | 6.9 | 55 | 14.105
50 | 95 | 0 | 13.4 | 5 | 7 | 55 | 14.2
50 | 96 | 0 | 13.4 | 5 | 7.1 | 55 | 14.215
50 | 97 | 0 | 13.4 | 5 | 7.2 | 55 | 14.23
50 | 98 | 0 | 13.4 | 5 | 7.3 | 55 | 14.245
50 | 99 | 0 | 13.4 | 5 | 7.4 | 55 | 14.26
50 | 100 | 0 | 13.4 | 5 | 7.5 | 55 | 14.275
50 | 101 | 0 | 13.4 | 5 | 7.6 | 55 | 14.29
50 | 102 | 0 | 13.4 | 5 | 7.7 | 55 | 14.305
50 | 103 | 0 | 13.4 | 5 | 7.8 | 55 | 14.32
50 | 104 | 0 | 13.4 | 5 | 7.9 | 55 | 14.335
50 | 105 | 0 | 13.4 | 5 | 8 | 55 | 14.35
50 | 106 | 0 | 13.4 | 5 | 8.1 | 55 | 14.365
50 | 107 | 0 | 13.4 | 5 | 8.2 | 55 | 14.38
50 | 108 | 0 | 13.4 | 5 | 8.3 | 55 | 14.395
50 | 109 | 0 | 13.4 | 5 | 8.4 | 55 | 14.41
50 | 110 | 0 | 13.4 | 5 | 8.5 | 55 | 14.425
50 | 111 | 0 | 13.4 | 5 | 8.6 | 55 | 14.44
50 | 112 | 0 | 13.4 | 5 | 8.7 | 55 | 14.455
50 | 113 | 0 | 13.4 | 5 | 8.8 | 55 | 14.47
50 | 114 | 0 | 13.4 | 5 | 8.9 | 55 | 14.485
50 | 115 | 0 | 13.4 | 5 | 9 | 55 | 14.5
50 | 116 | 0 | 13.4 | 5 | 9.1 | 55 | 14.62
50 | 117 | 0 | 13.4 | 5 | 9.2 | 55 | 14.74
50 | 118 | 0 | 13.4 | 5 | 9.3 | 55 | 14.86
50 | 119 | 0 | 13.4 | 5 | 9.4 | 55 | 14.98
50 | 120 | 0 | 13.4 | 5 | 9.5 | 55 | 15.1
50 | 121 | 0 | 13.4 | 5 | 9.6 | 55 | 15.22
50 | 122 | 0 | 13.4 | 5 | 9.7 | 55 | 15.34
50 | 123 | 0 | 13.4 | 5 | 9.8 | 55 | 15.46
50 | 124 | 0 | 13.4 | 5 | 9.9 | 55 | 15.58
50 | 125 | 0 | 13.4 | 5 | 10 | 55 | 15.7
50 | 126 | 0 | 13.4 | 2 | 3 | 100 | 6.5
50 | 127 | 0 | 13.4 | 2 | 3.1 | 100 | 6.575
50 | 128 | 0 | 13.4 | 2 | 3.2 | 100 | 6.65
50 | 129 | 0 | 13.4 | 2 | 3.3 | 100 | 6.725
50 | 130 | 0 | 13.4 | 2 | 3.4 | 100 | 6.8
50 | 131 | 0 | 13.4 | 2 | 3.5 | 100 | 6.875
50 | 132 | 0 | 13.4 | 2 | 3.6 | 100 | 6.95
50 | 133 | 0 | 13.4 | 2 | 3.7 | 100 | 7.025
50 | 134 | 0 | 13.4 | 2 | 3.8 | 100 | 7.1
50 | 135 | 0 | 13.4 | 2 | 3.9 | 100 | 7.175
50 | 136 | 0 | 13.4 | 2 | 4 | 100 | 7.25
50 | 137 | 0 | 13.4 | 2 | 4.1 | 100 | 7.325
50 | 138 | 0 | 13.4 | 2 | 4.2 | 100 | 7.4
50 | 139 | 0 | 13.4 | 2 | 4.3 | 100 | 7.475
50 | 140 | 0 | 13.4 | 2 | 4.4 | 100 | 7.55
50 | 141 | 0 | 13.4 | 2 | 4.5 | 100 | 7.625
50 | 142 | 0 | 13.4 | 2 | 4.6 | 100 | 7.7
50 | 143 | 0 | 13.4 | 2 | 4.7 | 100 | 7.775
50 | 144 | 0 | 13.4 | 2 | 4.8 | 100 | 7.85
50 | 145 | 0 | 13.4 | 2 | 4.9 | 100 | 7.925
50 | 146 | 0 | 13.4 | 2 | 5 | 100 | 8
50 | 147 | 0 | 13.4 | 2 | 5.1 | 100 | 8.025
50 | 148 | 0 | 13.4 | 2 | 5.2 | 100 | 8.05
50 | 149 | 0 | 13.4 | 2 | 5.3 | 100 | 8.075
50 | 150 | 0 | 13.4 | 2 | 5.4 | 100 | 8.1
51 | 45 | 0 | 13.42 | 2 | 5.5 | 100 | 8.125
51 | 46 | 0 | 13.42 | 2 | 5.6 | 100 | 8.15
51 | 47 | 0 | 13.42 | 2 | 5.7 | 100 | 8.175
51 | 48 | 0 | 13.42 | 2 | 5.8 | 100 | 8.2
51 | 49 | 0 | 13.42 | 2 | 5.9 | 100 | 8.225
51 | 50 | 0 | 13.42 | 2 | 6 | 100 | 8.25
51 | 51 | 0 | 13.42 | 2 | 6.1 | 100 | 8.275
51 | 52 | 0 | 13.42 | 2 | 6.2 | 100 | 8.3
51 | 53 | 0 | 13.42 | 2 | 6.3 | 100 | 8.325
51 | 54 | 0 | 13.42 | 2 | 6.4 | 100 | 8.35
51 | 55 | 0 | 13.42 | 2 | 6.5 | 100 | 8.375
51 | 56 | 0 | 13.42 | 2 | 6.6 | 100 | 8.4
51 | 57 | 0 | 13.42 | 2 | 6.7 | 100 | 8.425
51 | 58 | 0 | 13.42 | 2 | 6.8 | 100 | 8.45
51 | 59 | 0 | 13.42 | 2 | 6.9 | 100 | 8.475
51 | 60 | 0 | 13.42 | 2 | 7 | 100 | 8.5
51 | 61 | 0 | 13.42 | 2 | 7.1 | 100 | 8.545
51 | 62 | 0 | 13.42 | 2 | 7.2 | 100 | 8.59
51 | 63 | 0 | 13.42 | 2 | 7.3 | 100 | 8.635
51 | 64 | 0 | 13.42 | 2 | 7.4 | 100 | 8.68
51 | 65 | 0 | 13.42 | 2 | 7.5 | 100 | 8.725
51 | 66 | 0 | 13.42 | 2 | 7.6 | 100 | 8.77
51 | 67 | 0 | 13.42 | 2 | 7.7 | 100 | 8.815
51 | 68 | 0 | 13.42 | 2 | 7.8 | 100 | 8.86
51 | 69 | 0 | 13.42 | 2 | 7.9 | 100 | 8.905
51 | 70 | 0 | 13.42 | 2 | 8 | 100 | 8.95
51 | 71 | 0 | 13.42 | 2 | 8.1 | 100 | 8.995
51 | 72 | 0 | 13.42 | 2 | 8.2 | 100 | 9.04
51 | 73 | 0 | 13.42 | 2 | 8.3 | 100 | 9.085
51 | 74 | 0 | 13.42 | 2 | 8.4 | 100 | 9.13
51 | 75 | 0 | 13.42 | 2 | 8.5 | 100 | 9.175
51 | 76 | 0 | 13.42 | 2 | 8.6 | 100 | 9.22
51 | 77 | 0 | 13.42 | 2 | 8.7 | 100 | 9.265
51 | 78 | 0 | 13.42 | 2 | 8.8 | 100 | 9.31
51 | 79 | 0 | 13.42 | 2 | 8.9 | 100 | 9.355
51 | 80 | 0 | 13.42 | 2 | 9 | 100 | 9.4
51 | 81 | 0 | 13.42 | 2 | 9.1 | 100 | 9.48
51 | 82 | 0 | 13.42 | 2 | 9.2 | 100 | 9.56
51 | 83 | 0 | 13.42 | 2 | 9.3 | 100 | 9.64
51 | 84 | 0 | 13.42 | 2 | 9.4 | 100 | 9.72
51 | 85 | 0 | 13.42 | 2 | 9.5 | 100 | 9.8
51 | 86 | 0 | 13.42 | 2 | 9.6 | 100 | 9.88
51 | 87 | 0 | 13.42 | 2 | 9.7 | 100 | 9.96
51 | 88 | 0 | 13.42 | 2 | 9.8 | 100 | 10.04
51 | 89 | 0 | 13.42 | 2 | 9.9 | 100 | 10.12
51 | 90 | 0 | 13.42 | 2 | 10 | 100 | 10.2
51 | 91 | 0 | 13.42 | 2.1 | 3 | 100 | 6.5
51 | 92 | 0 | 13.42 | 2.1 | 3.1 | 100 | 6.576
51 | 93 | 0 | 13.42 | 2.1 | 3.2 | 100 | 6.652
51 | 94 | 0 | 13.42 | 2.1 | 3.3 | 100 | 6.728
51 | 95 | 0 | 13.42 | 2.1 | 3.4 | 100 | 6.804
51 | 96 | 0 | 13.42 | 2.1 | 3.5 | 100 | 6.88
51 | 97 | 0 | 13.42 | 2.1 | 3.6 | 100 | 6.956
51 | 98 | 0 | 13.42 | 2.1 | 3.7 | 100 | 7.032
51 | 99 | 0 | 13.42 | 2.1 | 3.8 | 100 | 7.108
51 | 100 | 0 | 13.42 | 2.1 | 3.9 | 100 | 7.184
51 | 101 | 0 | 13.42 | 2.1 | 4 | 100 | 7.26
51 | 102 | 0 | 13.42 | 2.1 | 4.1 | 100 | 7.336
51 | 103 | 0 | 13.42 | 2.1 | 4.2 | 100 | 7.412
51 | 104 | 0 | 13.42 | 2.1 | 4.3 | 100 | 7.488
51 | 105 | 0 | 13.42 | 2.1 | 4.4 | 100 | 7.564
51 | 106 | 0 | 13.42 | 2.1 | 4.5 | 100 | 7.64
51 | 107 | 0 | 13.42 | 2.1 | 4.6 | 100 | 7.716
51 | 108 | 0 | 13.42 | 2.1 | 4.7 | 100 | 7.792
51 | 109 | 0 | 13.42 | 2.1 | 4.8 | 100 | 7.868
51 | 110 | 0 | 13.42 | 2.1 | 4.9 | 100 | 7.944
51 | 111 | 0 | 13.42 | 2.1 | 5 | 100 | 8.02
51 | 112 | 0 | 13.42 | 2.1 | 5.1 | 100 | 8.0465
51 | 113 | 0 | 13.42 | 2.1 | 5.2 | 100 | 8.073
51 | 114 | 0 | 13.42 | 2.1 | 5.3 | 100 | 8.0995
51 | 115 | 0 | 13.42 | 2.1 | 5.4 | 100 | 8.126
51 | 116 | 0 | 13.42 | 2.1 | 5.5 | 100 | 8.1525
51 | 117 | 0 | 13.42 | 2.1 | 5.6 | 100 | 8.179
51 | 118 | 0 | 13.42 | 2.1 | 5.7 | 100 | 8.2055
51 | 119 | 0 | 13.42 | 2.1 | 5.8 | 100 | 8.232
51 | 120 | 0 | 13.42 | 2.1 | 5.9 | 100 | 8.2585
51 | 121 | 0 | 13.42 | 2.1 | 6 | 100 | 8.285
51 | 122 | 0 | 13.42 | 2.1 | 6.1 | 100 | 8.3115
51 | 123 | 0 | 13.42 | 2.1 | 6.2 | 100 | 8.338
51 | 124 | 0 | 13.42 | 2.1 | 6.3 | 100 | 8.3645
51 | 125 | 0 | 13.42 | 2.1 | 6.4 | 100 | 8.391
51 | 126 | 0 | 13.42 | 2.1 | 6.5 | 100 | 8.4175
51 | 127 | 0 | 13.42 | 2.1 | 6.6 | 100 | 8.444
51 | 128 | 0 | 13.42 | 2.1 | 6.7 | 100 | 8.4705
51 | 129 | 0 | 13.42 | 2.1 | 6.8 | 100 | 8.497
51 | 130 | 0 | 13.42 | 2.1 | 6.9 | 100 | 8.5235
51 | 131 | 0 | 13.42 | 2.1 | 7 | 100 | 8.55
51 | 132 | 0 | 13.42 | 2.1 | 7.1 | 100 | 8.5935
51 | 133 | 0 | 13.42 | 2.1 | 7.2 | 100 | 8.637
51 | 134 | 0 | 13.42 | 2.1 | 7.3 | 100 | 8.6805
51 | 135 | 0 | 13.42 | 2.1 | 7.4 | 100 | 8.724
51 | 136 | 0 | 13.42 | 2.1 | 7.5 | 100 | 8.7675
51 | 137 | 0 | 13.42 | 2.1 | 7.6 | 100 | 8.811
51 | 138 | 0 | 13.42 | 2.1 | 7.7 | 100 | 8.8545
51 | 139 | 0 | 13.42 | 2.1 | 7.8 | 100 | 8.898
51 | 140 | 0 | 13.42 | 2.1 | 7.9 | 100 | 8.9415
51 | 141 | 0 | 13.42 | 2.1 | 8 | 100 | 8.985
51 | 142 | 0 | 13.42 | 2.1 | 8.1 | 100 | 9.0285
51 | 143 | 0 | 13.42 | 2.1 | 8.2 | 100 | 9.072
51 | 144 | 0 | 13.42 | 2.1 | 8.3 | 100 | 9.1155
51 | 145 | 0 | 13.42 | 2.1 | 8.4 | 100 | 9.159
51 | 146 | 0 | 13.42 | 2.1 | 8.5 | 100 | 9.2025
51 | 147 | 0 | 13.42 | 2.1 | 8.6 | 100 | 9.246
51 | 148 | 0 | 13.42 | 2.1 | 8.7 | 100 | 9.2895
51 | 149 | 0 | 13.42 | 2.1 | 8.8 | 100 | 9.333
51 | 150 | 0 | 13.42 | 2.1 | 8.9 | 100 | 9.3765
52 | 45 | 0 | 13.44 | 2.1 | 9 | 100 | 9.42
52 | 46 | 0 | 13.44 | 2.1 | 9.1 | 100 | 9.501
52 | 47 | 0 | 13.44 | 2.1 | 9.2 | 100 | 9.582
52 | 48 | 0 | 13.44 | 2.1 | 9.3 | 100 | 9.663
52 | 49 | 0 | 13.44 | 2.1 | 9.4 | 100 | 9.744
52 | 50 | 0 | 13.44 | 2.1 | 9.5 | 100 | 9.825
52 | 51 | 0 | 13.44 | 2.1 | 9.6 | 100 | 9.906
52 | 52 | 0 | 13.44 | 2.1 | 9.7 | 100 | 9.987
52 | 53 | 0 | 13.44 | 2.1 | 9.8 | 100 | 10.068
52 | 54 | 0 | 13.44 | 2.1 | 9.9 | 100 | 10.149
52 | 55 | 0 | 13.44 | 2.1 | 10 | 100 | 10.23
52 | 56 | 0 | 13.44 | 2.2 | 3 | 100 | 6.5
52 | 57 | 0 | 13.44 | 2.2 | 3.1 | 100 | 6.577
52 | 58 | 0 | 13.44 | 2.2 | 3.2 | 100 | 6.654
52 | 59 | 0 | 13.44 | 2.2 | 3.3 | 100 | 6.731
52 | 60 | 0 | 13.44 | 2.2 | 3.4 | 100 | 6.808
52 | 61 | 0 | 13.44 | 2.2 | 3.5 | 100 | 6.885
52 | 62 | 0 | 13.44 | 2.2 | 3.6 | 100 | 6.962
52 | 63 | 0 | 13.44 | 2.2 | 3.7 | 100 | 7.039
52 | 64 | 0 | 13.44 | 2.2 | 3.8 | 100 | 7.116
52 | 65 | 0 | 13.44 | 2.2 | 3.9 | 100 | 7.193
52 | 66 | 0 | 13.44 | 2.2 | 4 | 100 | 7.27
52 | 67 | 0 | 13.44 | 2.2 | 4.1 | 100 | 7.347
52 | 68 | 0 | 13.44 | 2.2 | 4.2 | 100 | 7.424
52 | 69 | 0 | 13.44 | 2.2 | 4.3 | 100 | 7.501
52 | 70 | 0 | 13.44 | 2.2 | 4.4 | 100 | 7.578
52 | 71 | 0 | 13.44 | 2.2 | 4.5 | 100 | 7.655
52 | 72 | 0 | 13.44 | 2.2 | 4.6 | 100 | 7.732
52 | 73 | 0 | 13.44 | 2.2 | 4.7 | 100 | 7.809
52 | 74 | 0 | 13.44 | 2.2 | 4.8 | 100 | 7.886
52 | 75 | 0 | 13.44 | 2.2 | 4.9 | 100 | 7.963
52 | 76 | 0 | 13.44 | 2.2 | 5 | 100 | 8.04
52 | 77 | 0 | 13.44 | 2.2 | 5.1 | 100 | 8.068
52 | 78 | 0 | 13.44 | 2.2 | 5.2 | 100 | 8.096
52 | 79 | 0 | 13.44 | 2.2 | 5.3 | 100 | 8.124
52 | 80 | 0 | 13.44 | 2.2 | 5.4 | 100 | 8.152
52 | 81 | 0 | 13.44 | 2.2 | 5.5 | 100 | 8.18
52 | 82 | 0 | 13.44 | 2.2 | 5.6 | 100 | 8.208
52 | 83 | 0 | 13.44 | 2.2 | 5.7 | 100 | 8.236
52 | 84 | 0 | 13.44 | 2.2 | 5.8 | 100 | 8.264
52 | 85 | 0 | 13.44 | 2.2 | 5.9 | 100 | 8.292
52 | 86 | 0 | 13.44 | 2.2 | 6 | 100 | 8.32
52 | 87 | 0 | 13.44 | 2.2 | 6.1 | 100 | 8.348
52 | 88 | 0 | 13.44 | 2.2 | 6.2 | 100 | 8.376
52 | 89 | 0 | 13.44 | 2.2 | 6.3 | 100 | 8.404
52 | 90 | 0 | 13.44 | 2.2 | 6.4 | 100 | 8.432
52 | 91 | 0 | 13.44 | 2.2 | 6.5 | 100 | 8.46
52 | 92 | 0 | 13.44 | 2.2 | 6.6 | 100 | 8.488
52 | 93 | 0 | 13.44 | 2.2 | 6.7 | 100 | 8.516
52 | 94 | 0 | 13.44 | 2.2 | 6.8 | 100 | 8.544
52 | 95 | 0 | 13.44 | 2.2 | 6.9 | 100 | 8.572
52 | 96 | 0 | 13.44 | 2.2 | 7 | 100 | 8.6
52 | 97 | 0 | 13.44 | 2.2 | 7.1 | 100 | 8.642
52 | 98 | 0 | 13.44 | 2.2 | 7.2 | 100 | 8.684
52 | 99 | 0 | 13.44 | 2.2 | 7.3 | 100 | 8.726
52 | 100 | 0 | 13.44 | 2.2 | 7.4 | 100 | 8.768
52 | 101 | 0 | 13.44 | 2.2 | 7.5 | 100 | 8.81
52 | 102 | 0 | 13.44 | 2.2 | 7.6 | 100 | 8.852
52 | 103 | 0 | 13.44 | 2.2 | 7.7 | 100 | 8.894
52 | 104 | 0 | 13.44 | 2.2 | 7.8 | 100 | 8.936
52 | 105 | 0 | 13.44 | 2.2 | 7.9 | 100 | 8.978
52 | 106 | 0 | 13.44 | 2.2 | 8 | 100 | 9.02
52 | 107 | 0 | 13.44 | 2.2 | 8.1 | 100 | 9.062
52 | 108 | 0 | 13.44 | 2.2 | 8.2 | 100 | 9.104
52 | 109 | 0 | 13.44 | 2.2 | 8.3 | 100 | 9.146
52 | 110 | 0 | 13.44 | 2.2 | 8.4 | 100 | 9.188
52 | 111 | 0 | 13.44 | 2.2 | 8.5 | 100 | 9.23
52 | 112 | 0 | 13.44 | 2.2 | 8.6 | 100 | 9.272
52 | 113 | 0 | 13.44 | 2.2 | 8.7 | 100 | 9.314
52 | 114 | 0 | 13.44 | 2.2 | 8.8 | 100 | 9.356
52 | 115 | 0 | 13.44 | 2.2 | 8.9 | 100 | 9.398
52 | 116 | 0 | 13.44 | 2.2 | 9 | 100 | 9.44
52 | 117 | 0 | 13.44 | 2.2 | 9.1 | 100 | 9.522
52 | 118 | 0 | 13.44 | 2.2 | 9.2 | 100 | 9.604
52 | 119 | 0 | 13.44 | 2.2 | 9.3 | 100 | 9.686
52 | 120 | 0 | 13.44 | 2.2 | 9.4 | 100 | 9.768
52 | 121 | 0 | 13.44 | 2.2 | 9.5 | 100 | 9.85
52 | 122 | 0 | 13.44 | 2.2 | 9.6 | 100 | 9.932
52 | 123 | 0 | 13.44 | 2.2 | 9.7 | 100 | 10.014
52 | 124 | 0 | 13.44 | 2.2 | 9.8 | 100 | 10.096
52 | 125 | 0 | 13.44 | 2.2 | 9.9 | 100 | 10.178
52 | 126 | 0 | 13.44 | 2.2 | 10 | 100 | 10.26
52 | 127 | 0 | 13.44 | 2.3 | 3 | 100 | 6.5
52 | 128 | 0 | 13.44 | 2.3 | 3.1 | 100 | 6.578
52 | 129 | 0 | 13.44 | 2.3 | 3.2 | 100 | 6.656
52 | 130 | 0 | 13.44 | 2.3 | 3.3 | 100 | 6.734
52 | 131 | 0 | 13.44 | 2.3 | 3.4 | 100 | 6.812
52 | 132 | 0 | 13.44 | 2.3 | 3.5 | 100 | 6.89
52 | 133 | 0 | 13.44 | 2.3 | 3.6 | 100 | 6.968
52 | 134 | 0 | 13.44 | 2.3 | 3.7 | 100 | 7.046
52 | 135 | 0 | 13.44 | 2.3 | 3.8 | 100 | 7.124
52 | 136 | 0 | 13.44 | 2.3 | 3.9 | 100 | 7.202
52 | 137 | 0 | 13.44 | 2.3 | 4 | 100 | 7.28
52 | 138 | 0 | 13.44 | 2.3 | 4.1 | 100 | 7.358
52 | 139 | 0 | 13.44 | 2.3 | 4.2 | 100 | 7.436
52 | 140 | 0 | 13.44 | 2.3 | 4.3 | 100 | 7.514
52 | 141 | 0 | 13.44 | 2.3 | 4.4 | 100 | 7.592
52 | 142 | 0 | 13.44 | 2.3 | 4.5 | 100 | 7.67
52 | 143 | 0 | 13.44 | 2.3 | 4.6 | 100 | 7.748
52 | 144 | 0 | 13.44 | 2.3 | 4.7 | 100 | 7.826
52 | 145 | 0 | 13.44 | 2.3 | 4.8 | 100 | 7.904
52 | 146 | 0 | 13.44 | 2.3 | 4.9 | 100 | 7.982
52 | 147 | 0 | 13.44 | 2.3 | 5 | 100 | 8.06
52 | 148 | 0 | 13.44 | 2.3 | 5.1 | 100 | 8.0895
52 | 149 | 0 | 13.44 | 2.3 | 5.2 | 100 | 8.119
52 | 150 | 0 | 13.44 | 2.3 | 5.3 | 100 | 8.1485
53 | 45 | 0 | 13.46 | 2.3 | 5.4 | 100 | 8.178
53 | 46 | 0 | 13.46 | 2.3 | 5.5 | 100 | 8.2075
53 | 47 | 0 | 13.46 | 2.3 | 5.6 | 100 | 8.237
53 | 48 | 0 | 13.46 | 2.3 | 5.7 | 100 | 8.2665
53 | 49 | 0 | 13.46 | 2.3 | 5.8 | 100 | 8.296
53 | 50 | 0 | 13.46 | 2.3 | 5.9 | 100 | 8.3255
53 | 51 | 0 | 13.46 | 2.3 | 6 | 100 | 8.355
53 | 52 | 0 | 13.46 | 2.3 | 6.1 | 100 | 8.3845
53 | 53 | 0 | 13.46 | 2.3 | 6.2 | 100 | 8.414
53 | 54 | 0 | 13.46 | 2.3 | 6.3 | 100 | 8.4435
53 | 55 | 0 | 13.46 | 2.3 | 6.4 | 100 | 8.473
53 | 56 | 0 | 13.46 | 2.3 | 6.5 | 100 | 8.5025
53 | 57 | 0 | 13.46 | 2.3 | 6.6 | 100 | 8.532
53 | 58 | 0 | 13.46 | 2.3 | 6.7 | 100 | 8.5615
53 | 59 | 0 | 13.46 | 2.3 | 6.8 | 100 | 8.591
53 | 60 | 0 | 13.46 | 2.3 | 6.9 | 100 | 8.6205
53 | 61 | 0 | 13.46 | 2.3 | 7 | 100 | 8.65
53 | 62 | 0 | 13.46 | 2.3 | 7.1 | 100 | 8.6905
53 | 63 | 0 | 13.46 | 2.3 | 7.2 | 100 | 8.731
53 | 64 | 0 | 13.46 | 2.3 | 7.3 | 100 | 8.7715
53 | 65 | 0 | 13.46 | 2.3 | 7.4 | 100 | 8.812
53 | 66 | 0 | 13.46 | 2.3 | 7.5 | 100 | 8.8525
53 | 67 | 0 | 13.46 | 2.3 | 7.6 | 100 | 8.893
53 | 68 | 0 | 13.46 | 2.3 | 7.7 | 100 | 8.9335
53 | 69 | 0 | 13.46 | 2.3 | 7.8 | 100 | 8.974
53 | 70 | 0 | 13.46 | 2.3 | 7.9 | 100 | 9.0145
53 | 71 | 0 | 13.46 | 2.3 | 8 | 100 | 9.055
53 | 72 | 0 | 13.46 | 2.3 | 8.1 | 100 | 9.0955
53 | 73 | 0 | 13.46 | 2.3 | 8.2 | 100 | 9.136
53 | 74 | 0 | 13.46 | 2.3 | 8.3 | 100 | 9.1765
53 | 75 | 0 | 13.46 | 2.3 | 8.4 | 100 | 9.217
53 | 76 | 0 | 13.46 | 2.3 | 8.5 | 100 | 9.2575
53 | 77 | 0 | 13.46 | 2.3 | 8.6 | 100 | 9.298
53 | 78 | 0 | 13.46 | 2.3 | 8.7 | 100 | 9.3385
53 | 79 | 0 | 13.46 | 2.3 | 8.8 | 100 | 9.379
53 | 80 | 0 | 13.46 | 2.3 | 8.9 | 100 | 9.4195
53 | 81 | 0 | 13.46 | 2.3 | 9 | 100 | 9.46
53 | 82 | 0 | 13.46 | 2.3 | 9.1 | 100 | 9.543
53 | 83 | 0 | 13.46 | 2.3 | 9.2 | 100 | 9.626
53 | 84 | 0 | 13.46 | 2.3 | 9.3 | 100 | 9.709
53 | 85 | 0 | 13.46 | 2.3 | 9.4 | 100 | 9.792
53 | 86 | 0 | 13.46 | 2.3 | 9.5 | 100 | 9.875
53 | 87 | 0 | 13.46 | 2.3 | 9.6 | 100 | 9.958
53 | 88 | 0 | 13.46 | 2.3 | 9.7 | 100 | 10.041
53 | 89 | 0 | 13.46 | 2.3 | 9.8 | 100 | 10.124
53 | 90 | 0 | 13.46 | 2.3 | 9.9 | 100 | 10.207
53 | 91 | 0 | 13.46 | 2.3 | 10 | 100 | 10.29
53 | 92 | 0 | 13.46 | 2.4 | 3 | 100 | 6.5
53 | 93 | 0 | 13.46 | 2.4 | 3.1 | 100 | 6.579
53 | 94 | 0 | 13.46 | 2.4 | 3.2 | 100 | 6.658
53 | 95 | 0 | 13.46 | 2.4 | 3.3 | 100 | 6.737
53 | 96 | 0 | 13.46 | 2.4 | 3.4 | 100 | 6.816
53 | 97 | 0 | 13.46 | 2.4 | 3.5 | 100 | 6.895
53 | 98 | 0 | 13.46 | 2.4 | 3.6 | 100 | 6.974
53 | 99 | 0 | 13.46 | 2.4 | 3.7 | 100 | 7.053
53 | 100 | 0 | 13.46 | 2.4 | 3.8 | 100 | 7.132
53 | 101 | 0 | 13.46 | 2.4 | 3.9 | 100 | 7.211
53 | 102 | 0 | 13.46 | 2.4 | 4 | 100 | 7.29
53 | 103 | 0 | 13.46 | 2.4 | 4.1 | 100 | 7.369
53 | 104 | 0 | 13.46 | 2.4 | 4.2 | 100 | 7.448
53 | 105 | 0 | 13.46 | 2.4 | 4.3 | 100 | 7.527
53 | 106 | 0 | 13.46 | 2.4 | 4.4 | 100 | 7.606
53 | 107 | 0 | 13.46 | 2.4 | 4.5 | 100 | 7.685
53 | 108 | 0 | 13.46 | 2.4 | 4.6 | 100 | 7.764
53 | 109 | 0 | 13.46 | 2.4 | 4.7 | 100 | 7.843
53 | 110 | 0 | 13.46 | 2.4 | 4.8 | 100 | 7.922
53 | 111 | 0 | 13.46 | 2.4 | 4.9 | 100 | 8.001
53 | 112 | 0 | 13.46 | 2.4 | 5 | 100 | 8.08
53 | 113 | 0 | 13.46 | 2.4 | 5.1 | 100 | 8.111
53 | 114 | 0 | 13.46 | 2.4 | 5.2 | 100 | 8.142
53 | 115 | 0 | 13.46 | 2.4 | 5.3 | 100 | 8.173
53 | 116 | 0 | 13.46 | 2.4 | 5.4 | 100 | 8.204
53 | 117 | 0 | 13.46 | 2.4 | 5.5 | 100 | 8.235
53 | 118 | 0 | 13.46 | 2.4 | 5.6 | 100 | 8.266
53 | 119 | 0 | 13.46 | 2.4 | 5.7 | 100 | 8.297
53 | 120 | 0 | 13.46 | 2.4 | 5.8 | 100 | 8.328
53 | 121 | 0 | 13.46 | 2.4 | 5.9 | 100 | 8.359
53 | 122 | 0 | 13.46 | 2.4 | 6 | 100 | 8.39
53 | 123 | 0 | 13.46 | 2.4 | 6.1 | 100 | 8.421
53 | 124 | 0 | 13.46 | 2.4 | 6.2 | 100 | 8.452
53 | 125 | 0 | 13.46 | 2.4 | 6.3 | 100 | 8.483
53 | 126 | 0 | 13.46 | 2.4 | 6.4 | 100 | 8.514
53 | 127 | 0 | 13.46 | 2.4 | 6.5 | 100 | 8.545
53 | 128 | 0 | 13.46 | 2.4 | 6.6 | 100 | 8.576
53 | 129 | 0 | 13.46 | 2.4 | 6.7 | 100 | 8.607
53 | 130 | 0 | 13.46 | 2.4 | 6.8 | 100 | 8.638
53 | 131 | 0 | 13.46 | 2.4 | 6.9 | 100 | 8.669
53 | 132 | 0 | 13.46 | 2.4 | 7 | 100 | 8.7
53 | 133 | 0 | 13.46 | 2.4 | 7.1 | 100 | 8.739
53 | 134 | 0 | 13.46 | 2.4 | 7.2 | 100 | 8.778
53 | 135 | 0 | 13.46 | 2.4 | 7.3 | 100 | 8.817
53 | 136 | 0 | 13.46 | 2.4 | 7.4 | 100 | 8.856
53 | 137 | 0 | 13.46 | 2.4 | 7.5 | 100 | 8.895
53 | 138 | 0 | 13.46 | 2.4 | 7.6 | 100 | 8.934
53 | 139 | 0 | 13.46 | 2.4 | 7.7 | 100 | 8.973
53 | 140 | 0 | 13.46 | 2.4 | 7.8 | 100 | 9.012
53 | 141 | 0 | 13.46 | 2.4 | 7.9 | 100 | 9.051
53 | 142 | 0 | 13.46 | 2.4 | 8 | 100 | 9.09
53 | 143 | 0 | 13.46 | 2.4 | 8.1 | 100 | 9.129
53 | 144 | 0 | 13.46 | 2.4 | 8.2 | 100 | 9.168
53 | 145 | 0 | 13.46 | 2.4 | 8.3 | 100 | 9.207
53 | 146 | 0 | 13.46 | 2.4 | 8.4 | 100 | 9.246
53 | 147 | 0 | 13.46 | 2.4 | 8.5 | 100 | 9.285
53 | 148 | 0 | 13.46 | 2.4 | 8.6 | 100 | 9.324
53 | 149 | 0 | 13.46 | 2.4 | 8.7 | 100 | 9.363
53 | 150 | 0 | 13.46 | 2.4 | 8.8 | 100 | 9.402
54 | 45 | 0 | 13.48 | 2.4 | 8.9 | 100 | 9.441
54 | 46 | 0 | 13.48 | 2.4 | 9 | 100 | 9.48
54 | 47 | 0 | 13.48 | 2.4 | 9.1 | 100 | 9.564
54 | 48 | 0 | 13.48 | 2.4 | 9.2 | 100 | 9.648
54 | 49 | 0 | 13.48 | 2.4 | 9.3 | 100 | 9.732
54 | 50 | 0 | 13.48 | 2.4 | 9.4 | 100 | 9.816
54 | 51 | 0 | 13.48 | 2.4 | 9.5 | 100 | 9.9
54 | 52 | 0 | 13.48 | 2.4 | 9.6 | 100 | 9.984
54 | 53 | 0 | 13.48 | 2.4 | 9.7 | 100 | 10.068
54 | 54 | 0 | 13.48 | 2.4 | 9.8 | 100 | 10.152
54 | 55 | 0 | 13.48 | 2.4 | 9.9 | 100 | 10.236
54 | 56 | 0 | 13.48 | 2.4 | 10 | 100 | 10.32
54 | 57 | 0 | 13.48 | 2.5 | 3 | 100 | 6.5
54 | 58 | 0 | 13.48 | 2.5 | 3.1 | 100 | 6.58
54 | 59 | 0 | 13.48 | 2.5 | 3.2 | 100 | 6.66
54 | 60 | 0 | 13.48 | 2.5 | 3.3 | 100 | 6.74
54 | 61 | 0 | 13.48 | 2.5 | 3.4 | 100 | 6.82
54 | 62 | 0 | 13.48 | 2.5 | 3.5 | 100 | 6.9
54 | 63 | 0 | 13.48 | 2.5 | 3.6 | 100 | 6.98
54 | 64 | 0 | 13.48 | 2.5 | 3.7 | 100 | 7.06
54 | 65 | 0 | 13.48 | 2.5 | 3.8 | 100 | 7.14
54 | 66 | 0 | 13.48 | 2.5 | 3.9 | 100 | 7.22
54 | 67 | 0 | 13.48 | 2.5 | 4 | 100 | 7.3
54 | 68 | 0 | 13.48 | 2.5 | 4.1 | 100 | 7.38
54 | 69 | 0 | 13.48 | 2.5 | 4.2 | 100 | 7.46
54 | 70 | 0 | 13.48 | 2.5 | 4.3 | 100 | 7.54
54 | 71 | 0 | 13.48 | 2.5 | 4.4 | 100 | 7.62
54 | 72 | 0 | 13.48 | 2.5 | 4.5 | 100 | 7.7
54 | 73 | 0 | 13.48 | 2.5 | 4.6 | 100 | 7.78
54 | 74 | 0 | 13.48 | 2.5 | 4.7 | 100 | 7.86
54 | 75 | 0 | 13.48 | 2.5 | 4.8 | 100 | 7.94
54 | 76 | 0 | 13.48 | 2.5 | 4.9 | 100 | 8.02
54 | 77 | 0 | 13.48 | 2.5 | 5 | 100 | 8.1
54 | 78 | 0 | 13.48 | 2.5 | 5.1 | 100 | 8.1325
54 | 79 | 0 | 13.48 | 2.5 | 5.2 | 100 | 8.165
54 | 80 | 0 | 13.48 | 2.5 | 5.3 | 100 | 8.1975
54 | 81 | 0 | 13.48 | 2.5 | 5.4 | 100 | 8.23
54 | 82 | 0 | 13.48 | 2.5 | 5.5 | 100 | 8.2625
54 | 83 | 0 | 13.48 | 2.5 | 5.6 | 100 | 8.295
54 | 84 | 0 | 13.48 | 2.5 | 5.7 | 100 | 8.3275
54 | 85 | 0 | 13.48 | 2.5 | 5.8 | 100 | 8.36
54 | 86 | 0 | 13.48 | 2.5 | 5.9 | 100 | 8.3925
54 | 87 | 0 | 13.48 | 2.5 | 6 | 100 | 8.425
54 | 88 | 0 | 13.48 | 2.5 | 6.1 | 100 | 8.4575
54 | 89 | 0 | 13.48 | 2.5 | 6.2 | 100 | 8.49
54 | 90 | 0 | 13.48 | 2.5 | 6.3 | 100 | 8.5225
54 | 91 | 0 | 13.48 | 2.5 | 6.4 | 100 | 8.555
54 | 92 | 0 | 13.48 | 2.5 | 6.5 | 100 | 8.5875
54 | 93 | 0 | 13.48 | 2.5 | 6.6 | 100 | 8.62
54 | 94 | 0 | 13.48 | 2.5 | 6.7 | 100 | 8.6525
54 | 95 | 0 | 13.48 | 2.5 | 6.8 | 100 | 8.685
54 | 96 | 0 | 13.48 | 2.5 | 6.9 | 100 | 8.7175
54 | 97 | 0 | 13.48 | 2.5 | 7 | 100 | 8.75
54 | 98 | 0 | 13.48 | 2.5 | 7.1 | 100 | 8.7875
54 | 99 | 0 | 13.48 | 2.5 | 7.2 | 100 | 8.825
54 | 100 | 0 | 13.48 | 2.5 | 7.3 | 100 | 8.8625
54 | 101 | 0 | 13.48 | 2.5 | 7.4 | 100 | 8.9
54 | 102 | 0 | 13.48 | 2.5 | 7.5 | 100 | 8.9375
54 | 103 | 0 | 13.48 | 2.5 | 7.6 | 100 | 8.975
54 | 104 | 0 | 13.48 | 2.5 | 7.7 | 100 | 9.0125
54 | 105 | 0 | 13.48 | 2.5 | 7.8 | 100 | 9.05
54 | 106 | 0 | 13.48 | 2.5 | 7.9 | 100 | 9.0875
54 | 107 | 0 | 13.48 | 2.5 | 8 | 100 | 9.125
54 | 108 | 0 | 13.48 | 2.5 | 8.1 | 100 | 9.1625
54 | 109 | 0 | 13.48 | 2.5 | 8.2 | 100 | 9.2
54 | 110 | 0 | 13.48 | 2.5 | 8.3 | 100 | 9.2375
54 | 111 | 0 | 13.48 | 2.5 | 8.4 | 100 | 9.275
54 | 112 | 0 | 13.48 | 2.5 | 8.5 | 100 | 9.3125
54 | 113 | 0 | 13.48 | 2.5 | 8.6 | 100 | 9.35
54 | 114 | 0 | 13.48 | 2.5 | 8.7 | 100 | 9.3875
54 | 115 | 0 | 13.48 | 2.5 | 8.8 | 100 | 9.425
54 | 116 | 0 | 13.48 | 2.5 | 8.9 | 100 | 9.4625
54 | 117 | 0 | 13.48 | 2.5 | 9 | 100 | 9.5
54 | 118 | 0 | 13.48 | 2.5 | 9.1 | 100 | 9.585
54 | 119 | 0 | 13.48 | 2.5 | 9.2 | 100 | 9.67
54 | 120 | 0 | 13.48 | 2.5 | 9.3 | 100 | 9.755
54 | 121 | 0 | 13.48 | 2.5 | 9.4 | 100 | 9.84
54 | 122 | 0 | 13.48 | 2.5 | 9.5 | 100 | 9.925
54 | 123 | 0 | 13.48 | 2.5 | 9.6 | 100 | 10.01
54 | 124 | 0 | 13.48 | 2.5 | 9.7 | 100 | 10.095
54 | 125 | 0 | 13.48 | 2.5 | 9.8 | 100 | 10.18
54 | 126 | 0 | 13.48 | 2.5 | 9.9 | 100 | 10.265
54 | 127 | 0 | 13.48 | 2.5 | 10 | 100 | 10.35
54 | 128 | 0 | 13.48 | 2.6 | 3 | 100 | 6.5
54 | 129 | 0 | 13.48 | 2.6 | 3.1 | 100 | 6.581
54 | 130 | 0 | 13.48 | 2.6 | 3.2 | 100 | 6.662
54 | 131 | 0 | 13.48 | 2.6 | 3.3 | 100 | 6.743
54 | 132 | 0 | 13.48 | 2.6 | 3.4 | 100 | 6.824
54 | 133 | 0 | 13.48 | 2.6 | 3.5 | 100 | 6.905
54 | 134 | 0 | 13.48 | 2.6 | 3.6 | 100 | 6.986
54 | 135 | 0 | 13.48 | 2.6 | 3.7 | 100 | 7.067
54 | 136 | 0 | 13.48 | 2.6 | 3.8 | 100 | 7.148
54 | 137 | 0 | 13.48 | 2.6 | 3.9 | 100 | 7.229
54 | 138 | 0 | 13.48 | 2.6 | 4 | 100 | 7.31
54 | 139 | 0 | 13.48 | 2.6 | 4.1 | 100 | 7.391
54 | 140 | 0 | 13.48 | 2.6 | 4.2 | 100 | 7.472
54 | 141 | 0 | 13.48 | 2.6 | 4.3 | 100 | 7.553
54 | 142 | 0 | 13.48 | 2.6 | 4.4 | 100 | 7.634
54 | 143 | 0 | 13.48 | 2.6 | 4.5 | 100 | 7.715
54 | 144 | 0 | 13.48 | 2.6 | 4.6 | 100 | 7.796
54 | 145 | 0 | 13.48 | 2.6 | 4.7 | 100 | 7.877
54 | 146 | 0 | 13.48 | 2.6 | 4.8 | 100 | 7.958
54 | 147 | 0 | 13.48 | 2.6 | 4.9 | 100 | 8.039
54 | 148 | 0 | 13.48 | 2.6 | 5 | 100 | 8.12
54 | 149 | 0 | 13.48 | 2.6 | 5.1 | 100 | 8.154
54 | 150 | 0 | 13.48 | 2.6 | 5.2 | 100 | 8.188
55 | 45 | 0 | 13.5 | 2.6 | 5.3 | 100 | 8.222
55 | 46 | 0 | 13.5 | 2.6 | 5.4 | 100 | 8.256
55 | 47 | 0 | 13.5 | 2.6 | 5.5 | 100 | 8.29
55 | 48 | 0 | 13.5 | 2.6 | 5.6 | 100 | 8.324
55 | 49 | 0 | 13.5 | 2.6 | 5.7 | 100 | 8.358
55 | 50 | 0 | 13.5 | 2.6 | 5.8 | 100 | 8.392
55 | 51 | 0 | 13.5 | 2.6 | 5.9 | 100 | 8.426
55 | 52 | 0 | 13.5 | 2.6 | 6 | 100 | 8.46
55 | 53 | 0 | 13.5 | 2.6 | 6.1 | 100 | 8.494
55 | 54 | 0 | 13.5 | 2.6 | 6.2 | 100 | 8.528
55 | 55 | 0 | 13.5 | 2.6 | 6.3 | 100 | 8.562
55 | 56 | 0 | 13.5 | 2.6 | 6.4 | 100 | 8.596
55 | 57 | 0 | 13.5 | 2.6 | 6.5 | 100 | 8.63
55 | 58 | 0 | 13.5 | 2.6 | 6.6 | 100 | 8.664
55 | 59 | 0 | 13.5 | 2.6 | 6.7 | 100 | 8.698
55 | 60 | 0 | 13.5 | 2.6 | 6.8 | 100 | 8.732
55 | 61 | 0 | 13.5 | 2.6 | 6.9 | 100 | 8.766
55 | 62 | 0 | 13.5 | 2.6 | 7 | 100 | 8.8
55 | 63 | 0 | 13.5 | 2.6 | 7.1 | 100 | 8.836
55 | 64 | 0 | 13.5 | 2.6 | 7.2 | 100 | 8.872
55 | 65 | 0 | 13.5 | 2.6 | 7.3 | 100 | 8.908
55 | 66 | 0 | 13.5 | 2.6 | 7.4 | 100 | 8.944
55 | 67 | 0 | 13.5 | 2.6 | 7.5 | 100 | 8.98
55 | 68 | 0 | 13.5 | 2.6 | 7.6 | 100 | 9.016
55 | 69 | 0 | 13.5 | 2.6 | 7.7 | 100 | 9.052
55 | 70 | 0 | 13.5 | 2.6 | 7.8 | 100 | 9.088
55 | 71 | 0 | 13.5 | 2.6 | 7.9 | 100 | 9.124
55 | 72 | 0 | 13.5 | 2.6 | 8 | 100 | 9.16
55 | 73 | 0 | 13.5 | 2.6 | 8.1 | 100 | 9.196
55 | 74 | 0 | 13.5 | 2.6 | 8.2 | 100 | 9.232
55 | 75 | 0 | 13.5 | 2.6 | 8.3 | 100 | 9.268
55 | 76 | 0 | 13.5 | 2.6 | 8.4 | 100 | 9.304
55 | 77 | 0 | 13.5 | 2.6 | 8.5 | 100 | 9.34
55 | 78 | 0 | 13.5 | 2.6 | 8.6 | 100 | 9.376
55 | 79 | 0 | 13.5 | 2.6 | 8.7 | 100 | 9.412
55 | 80 | 0 | 13.5 | 2.6 | 8.8 | 100 | 9.448
55 | 81 | 0 | 13.5 | 2.6 | 8.9 | 100 | 9.484
55 | 82 | 0 | 13.5 | 2.6 | 9 | 100 | 9.52
55 | 83 | 0 | 13.5 | 2.6 | 9.1 | 100 | 9.606
55 | 84 | 0 | 13.5 | 2.6 | 9.2 | 100 | 9.692
55 | 85 | 0 | 13.5 | 2.6 | 9.3 | 100 | 9.778
55 | 86 | 0 | 13.5 | 2.6 | 9.4 | 100 | 9.864
55 | 87 | 0 | 13.5 | 2.6 | 9.5 | 100 | 9.95
55 | 88 | 0 | 13.5 | 2.6 | 9.6 | 100 | 10.036
55 | 89 | 0 | 13.5 | 2.6 | 9.7 | 100 | 10.122
55 | 90 | 0 | 13.5 | 2.6 | 9.8 | 100 | 10.208
55 | 91 | 0 | 13.5 | 2.6 | 9.9 | 100 | 10.294
55 | 92 | 0 | 13.5 | 2.6 | 10 | 100 | 10.38
55 | 93 | 0 | 13.5 | 2.7 | 3 | 100 | 6.5
55 | 94 | 0 | 13.5 | 2.7 | 3.1 | 100 | 6.582
55 | 95 | 0 | 13.5 | 2.7 | 3.2 | 100 | 6.664
55 | 96 | 0 | 13.5 | 2.7 | 3.3 | 100 | 6.746
55 | 97 | 0 | 13.5 | 2.7 | 3.4 | 100 | 6.828
55 | 98 | 0 | 13.5 | 2.7 | 3.5 | 100 | 6.91
55 | 99 | 0 | 13.5 | 2.7 | 3.6 | 100 | 6.992
55 | 100 | 0 | 13.5 | 2.7 | 3.7 | 100 | 7.074
55 | 101 | 0 | 13.5 | 2.7 | 3.8 | 100 | 7.156
55 | 102 | 0 | 13.5 | 2.7 | 3.9 | 100 | 7.238
55 | 103 | 0 | 13.5 | 2.7 | 4 | 100 | 7.32
55 | 104 | 0 | 13.5 | 2.7 | 4.1 | 100 | 7.402
55 | 105 | 0 | 13.5 | 2.7 | 4.2 | 100 | 7.484
55 | 106 | 0 | 13.5 | 2.7 | 4.3 | 100 | 7.566
55 | 107 | 0 | 13.5 | 2.7 | 4.4 | 100 | 7.648
55 | 108 | 0 | 13.5 | 2.7 | 4.5 | 100 | 7.73
55 | 109 | 0 | 13.5 | 2.7 | 4.6 | 100 | 7.812
55 | 110 | 0 | 13.5 | 2.7 | 4.7 | 100 | 7.894
55 | 111 | 0 | 13.5 | 2.7 | 4.8 | 100 | 7.976
55 | 112 | 0 | 13.5 | 2.7 | 4.9 | 100 | 8.058
55 | 113 | 0 | 13.5 | 2.7 | 5 | 100 | 8.14
55 | 114 | 0 | 13.5 | 2.7 | 5.1 | 100 | 8.1755
55 | 115 | 0 | 13.5 | 2.7 | 5.2 | 100 | 8.211
55 | 116 | 0 | 13.5 | 2.7 | 5.3 | 100 | 8.2465
55 | 117 | 0 | 13.5 | 2.7 | 5.4 | 100 | 8.282
55 | 118 | 0 | 13.5 | 2.7 | 5.5 | 100 | 8.3175
55 | 119 | 0 | 13.5 | 2.7 | 5.6 | 100 | 8.353
55 | 120 | 0 | 13.5 | 2.7 | 5.7 | 100 | 8.3885
55 | 121 | 0 | 13.5 | 2.7 | 5.8 | 100 | 8.424
55 | 122 | 0 | 13.5 | 2.7 | 5.9 | 100 | 8.4595
55 | 123 | 0 | 13.5 | 2.7 | 6 | 100 | 8.495
55 | 124 | 0 | 13.5 | 2.7 | 6.1 | 100 | 8.5305
55 | 125 | 0 | 13.5 | 2.7 | 6.2 | 100 | 8.566
55 | 126 | 0 | 13.5 | 2.7 | 6.3 | 100 | 8.6015
55 | 127 | 0 | 13.5 | 2.7 | 6.4 | 100 | 8.637
55 | 128 | 0 | 13.5 | 2.7 | 6.5 | 100 | 8.6725
55 | 129 | 0 | 13.5 | 2.7 | 6.6 | 100 | 8.708
55 | 130 | 0 | 13.5 | 2.7 | 6.7 | 100 | 8.7435
55 | 131 | 0 | 13.5 | 2.7 | 6.8 | 100 | 8.779
55 | 132 | 0 | 13.5 | 2.7 | 6.9 | 100 | 8.8145
55 | 133 | 0 | 13.5 | 2.7 | 7 | 100 | 8.85
55 | 134 | 0 | 13.5 | 2.7 | 7.1 | 100 | 8.8845
55 | 135 | 0 | 13.5 | 2.7 | 7.2 | 100 | 8.919
55 | 136 | 0 | 13.5 | 2.7 | 7.3 | 100 | 8.9535
55 | 137 | 0 | 13.5 | 2.7 | 7.4 | 100 | 8.988
55 | 138 | 0 | 13.5 | 2.7 | 7.5 | 100 | 9.0225
55 | 139 | 0 | 13.5 | 2.7 | 7.6 | 100 | 9.057
55 | 140 | 0 | 13.5 | 2.7 | 7.7 | 100 | 9.0915
55 | 141 | 0 | 13.5 | 2.7 | 7.8 | 100 | 9.126
55 | 142 | 0 | 13.5 | 2.7 | 7.9 | 100 | 9.1605
55 | 143 | 0 | 13.5 | 2.7 | 8 | 100 | 9.195
55 | 144 | 0 | 13.5 | 2.7 | 8.1 | 100 | 9.2295
55 | 145 | 0 | 13.5 | 2.7 | 8.2 | 100 | 9.264
55 | 146 | 0 | 13.5 | 2.7 | 8.3 | 100 | 9.2985
55 | 147 | 0 | 13.5 | 2.7 | 8.4 | 100 | 9.333
55 | 148 | 0 | 13.5 | 2.7 | 8.5 | 100 | 9.3675
55 | 149 | 0 | 13.5 | 2.7 | 8.6 | 100 | 9.402
55 | 150 | 0 | 13.5 | 2.7 | 8.7 | 100 | 9.4365
56 | 45 | 0 | 13.52 | 2.7 | 8.8 | 100 | 9.471
56 | 46 | 0 | 13.52 | 2.7 | 8.9 | 100 | 9.5055
56 | 47 | 0 | 13.52 | 2.7 | 9 | 100 | 9.54
56 | 48 | 0 | 13.52 | 2.7 | 9.1 | 100 | 9.627
56 | 49 | 0 | 13.52 | 2.7 | 9.2 | 100 | 9.714
56 | 50 | 0 | 13.52 | 2.7 | 9.3 | 100 | 9.801
56 | 51 | 0 | 13.52 | 2.7 | 9.4 | 100 | 9.888
56 | 52 | 0 | 13.52 | 2.7 | 9.5 | 100 | 9.975
56 | 53 | 0 | 13.52 | 2.7 | 9.6 | 100 | 10.062
56 | 54 | 0 | 13.52 | 2.7 | 9.7 | 100 | 10.149
56 | 55 | 0 | 13.52 | 2.7 | 9.8 | 100 | 10.236
56 | 56 | 0 | 13.52 | 2.7 | 9.9 | 100 | 10.323
56 | 57 | 0 | 13.52 | 2.7 | 10 | 100 | 10.41
56 | 58 | 0 | 13.52 | 2.8 | 3 | 100 | 6.5
56 | 59 | 0 | 13.52 | 2.8 | 3.1 | 100 | 6.583
56 | 60 | 0 | 13.52 | 2.8 | 3.2 | 100 | 6.666
56 | 61 | 0 | 13.52 | 2.8 | 3.3 | 100 | 6.749
56 | 62 | 0 | 13.52 | 2.8 | 3.4 | 100 | 6.832
56 | 63 | 0 | 13.52 | 2.8 | 3.5 | 100 | 6.915
56 | 64 | 0 | 13.52 | 2.8 | 3.6 | 100 | 6.998
56 | 65 | 0 | 13.52 | 2.8 | 3.7 | 100 | 7.081
56 | 66 | 0 | 13.52 | 2.8 | 3.8 | 100 | 7.164
56 | 67 | 0 | 13.52 | 2.8 | 3.9 | 100 | 7.247
56 | 68 | 0 | 13.52 | 2.8 | 4 | 100 | 7.33
56 | 69 | 0 | 13.52 | 2.8 | 4.1 | 100 | 7.413
56 | 70 | 0 | 13.52 | 2.8 | 4.2 | 100 | 7.496
56 | 71 | 0 | 13.52 | 2.8 | 4.3 | 100 | 7.579
56 | 72 | 0 | 13.52 | 2.8 | 4.4 | 100 | 7.662
56 | 73 | 0 | 13.52 | 2.8 | 4.5 | 100 | 7.745
56 | 74 | 0 | 13.52 | 2.8 | 4.6 | 100 | 7.828
56 | 75 | 0 | 13.52 | 2.8 | 4.7 | 100 | 7.911
56 | 76 | 0 | 13.52 | 2.8 | 4.8 | 100 | 7.994
56 | 77 | 0 | 13.52 | 2.8 | 4.9 | 100 | 8.077
56 | 78 | 0 | 13.52 | 2.8 | 5 | 100 | 8.16
56 | 79 | 0 | 13.52 | 2.8 | 5.1 | 100 | 8.197
56 | 80 | 0 | 13.52 | 2.8 | 5.2 | 100 | 8.234
56 | 81 | 0 | 13.52 | 2.8 | 5.3 | 100 | 8.271
56 | 82 | 0 | 13.52 | 2.8 | 5.4 | 100 | 8.308
56 | 83 | 0 | 13.52 | 2.8 | 5.5 | 100 | 8.345
56 | 84 | 0 | 13.52 | 2.8 | 5.6 | 100 | 8.382
56 | 85 | 0 | 13.52 | 2.8 | 5.7 | 100 | 8.419
56 | 86 | 0 | 13.52 | 2.8 | 5.8 | 100 | 8.456
56 | 87 | 0 | 13.52 | 2.8 | 5.9 | 100 | 8.493
56 | 88 | 0 | 13.52 | 2.8 | 6 | 100 | 8.53
56 | 89 | 0 | 13.52 | 2.8 | 6.1 | 100 | 8.567
56 | 90 | 0 | 13.52 | 2.8 | 6.2 | 100 | 8.604
56 | 91 | 0 | 13.52 | 2.8 | 6.3 | 100 | 8.641
56 | 92 | 0 | 13.52 | 2.8 | 6.4 | 100 | 8.678
56 | 93 | 0 | 13.52 | 2.8 | 6.5 | 100 | 8.715
56 | 94 | 0 | 13.52 | 2.8 | 6.6 | 100 | 8.752
56 | 95 | 0 | 13.52 | 2.8 | 6.7 | 100 | 8.789
56 | 96 | 0 | 13.52 | 2.8 | 6.8 | 100 | 8.826
56 | 97 | 0 | 13.52 | 2.8 | 6.9 | 100 | 8.863
56 | 98 | 0 | 13.52 | 2.8 | 7 | 100 | 8.9
56 | 99 | 0 | 13.52 | 2.8 | 7.1 | 100 | 8.933
56 | 100 | 0 | 13.52 | 2.8 | 7.2 | 100 | 8.966
56 | 101 | 0 | 13.52 | 2.8 | 7.3 | 100 | 8.999
56 | 102 | 0 | 13.52 | 2.8 | 7.4 | 100 | 9.032
56 | 103 | 0 | 13.52 | 2.8 | 7.5 | 100 | 9.065
56 | 104 | 0 | 13.52 | 2.8 | 7.6 | 100 | 9.098
56 | 105 | 0 | 13.52 | 2.8 | 7.7 | 100 | 9.131
56 | 106 | 0 | 13.52 | 2.8 | 7.8 | 100 | 9.164
56 | 107 | 0 | 13.52 | 2.8 | 7.9 | 100 | 9.197
56 | 108 | 0 | 13.52 | 2.8 | 8 | 100 | 9.23
56 | 109 | 0 | 13.52 | 2.8 | 8.1 | 100 | 9.263
56 | 110 | 0 | 13.52 | 2.8 | 8.2 | 100 | 9.296
56 | 111 | 0 | 13.52 | 2.8 | 8.3 | 100 | 9.329
56 | 112 | 0 | 13.52 | 2.8 | 8.4 | 100 | 9.362
56 | 113 | 0 | 13.52 | 2.8 | 8.5 | 100 | 9.395
56 | 114 | 0 | 13.52 | 2.8 | 8.6 | 100 | 9.428
56 | 115 | 0 | 13.52 | 2.8 | 8.7 | 100 | 9.461
56 | 116 | 0 | 13.52 | 2.8 | 8.8 | 100 | 9.494
56 | 117 | 0 | 13.52 | 2.8 | 8.9 | 100 | 9.527
56 | 118 | 0 | 13.52 | 2.8 | 9 | 100 | 9.56
56 | 119 | 0 | 13.52 | 2.8 | 9.1 | 100 | 9.648
56 | 120 | 0 | 13.52 | 2.8 | 9.2 | 100 | 9.736
56 | 121 | 0 | 13.52 | 2.8 | 9.3 | 100 | 9.824
56 | 122 | 0 | 13.52 | 2.8 | 9.4 | 100 | 9.912
56 | 123 | 0 | 13.52 | 2.8 | 9.5 | 100 | 10
56 | 124 | 0 | 13.52 | 2.8 | 9.6 | 100 | 10.088
56 | 125 | 0 | 13.52 | 2.8 | 9.7 | 100 | 10.176
56 | 126 | 0 | 13.52 | 2.8 | 9.8 | 100 | 10.264
56 | 127 | 0 | 13.52 | 2.8 | 9.9 | 100 | 10.352
56 | 128 | 0 | 13.52 | 2.8 | 10 | 100 | 10.44
56 | 129 | 0 | 13.52 | 2.9 | 3 | 100 | 6.5
56 | 130 | 0 | 13.52 | 2.9 | 3.1 | 100 | 6.584
56 | 131 | 0 | 13.52 | 2.9 | 3.2 | 100 | 6.668
56 | 132 | 0 | 13.52 | 2.9 | 3.3 | 100 | 6.752
56 | 133 | 0 | 13.52 | 2.9 | 3.4 | 100 | 6.836
56 | 134 | 0 | 13.52 | 2.9 | 3.5 | 100 | 6.92
56 | 135 | 0 | 13.52 | 2.9 | 3.6 | 100 | 7.004
56 | 136 | 0 | 13.52 | 2.9 | 3.7 | 100 | 7.088
56 | 137 | 0 | 13.52 | 2.9 | 3.8 | 100 | 7.172
56 | 138 | 0 | 13.52 | 2.9 | 3.9 | 100 | 7.256
56 | 139 | 0 | 13.52 | 2.9 | 4 | 100 | 7.34
56 | 140 | 0 | 13.52 | 2.9 | 4.1 | 100 | 7.424
56 | 141 | 0 | 13.52 | 2.9 | 4.2 | 100 | 7.508
56 | 142 | 0 | 13.52 | 2.9 | 4.3 | 100 | 7.592
56 | 143 | 0 | 13.52 | 2.9 | 4.4 | 100 | 7.676
56 | 144 | 0 | 13.52 | 2.9 | 4.5 | 100 | 7.76
56 | 145 | 0 | 13.52 | 2.9 | 4.6 | 100 | 7.844
56 | 146 | 0 | 13.52 | 2.9 | 4.7 | 100 | 7.928
56 | 147 | 0 | 13.52 | 2.9 | 4.8 | 100 | 8.012
56 | 148 | 0 | 13.52 | 2.9 | 4.9 | 100 | 8.096
56 | 149 | 0 | 13.52 | 2.9 | 5 | 100 | 8.18
56 | 150 | 0 | 13.52 | 2.9 | 5.1 | 100 | 8.2185
57 | 45 | 0 | 13.54 | 2.9 | 5.2 | 100 | 8.257
57 | 46 | 0 | 13.54 | 2.9 | 5.3 | 100 | 8.2955
57 | 47 | 0 | 13.54 | 2.9 | 5.4 | 100 | 8.334
57 | 48 | 0 | 13.54 | 2.9 | 5.5 | 100 | 8.3725
57 | 49 | 0 | 13.54 | 2.9 | 5.6 | 100 | 8.411
57 | 50 | 0 | 13.54 | 2.9 | 5.7 | 100 | 8.4495
57 | 51 | 0 | 13.54 | 2.9 | 5.8 | 100 | 8.488
57 | 52 | 0 | 13.54 | 2.9 | 5.9 | 100 | 8.5265
57 | 53 | 0 | 13.54 | 2.9 | 6 | 100 | 8.565
57 | 54 | 0 | 13.54 | 2.9 | 6.1 | 100 | 8.6035
57 | 55 | 0 | 13.54 | 2.9 | 6.2 | 100 | 8.642
57 | 56 | 0 | 13.54 | 2.9 | 6.3 | 100 | 8.6805
57 | 57 | 0 | 13.54 | 2.9 | 6.4 | 100 | 8.719
57 | 58 | 0 | 13.54 | 2.9 | 6.5 | 100 | 8.7575
57 | 59 | 0 | 13.54 | 2.9 | 6.6 | 100 | 8.796
57 | 60 | 0 | 13.54 | 2.9 | 6.7 | 100 | 8.8345
57 | 61 | 0 | 13.54 | 2.9 | 6.8 | 100 | 8.873
57 | 62 | 0 | 13.54 | 2.9 | 6.9 | 100 | 8.9115
57 | 63 | 0 | 13.54 | 2.9 | 7 | 100 | 8.95
57 | 64 | 0 | 13.54 | 2.9 | 7.1 | 100 | 8.9815
57 | 65 | 0 | 13.54 | 2.9 | 7.2 | 100 | 9.013
57 | 66 | 0 | 13.54 | 2.9 | 7.3 | 100 | 9.0445
57 | 67 | 0 | 13.54 | 2.9 | 7.4 | 100 | 9.076
57 | 68 | 0 | 13.54 | 2.9 | 7.5 | 100 | 9.1075
57 | 69 | 0 | 13.54 | 2.9 | 7.6 | 100 | 9.139
57 | 70 | 0 | 13.54 | 2.9 | 7.7 | 100 | 9.1705
57 | 71 | 0 | 13.54 | 2.9 | 7.8 | 100 | 9.202
57 | 72 | 0 | 13.54 | 2.9 | 7.9 | 100 | 9.2335
57 | 73 | 0 | 13.54 | 2.9 | 8 | 100 | 9.265
57 | 74 | 0 | 13.54 | 2.9 | 8.1 | 100 | 9.2965
57 | 75 | 0 | 13.54 | 2.9 | 8.2 | 100 | 9.328
57 | 76 | 0 | 13.54 | 2.9 | 8.3 | 100 | 9.3595
57 | 77 | 0 | 13.54 | 2.9 | 8.4 | 100 | 9.391
57 | 78 | 0 | 13.54 | 2.9 | 8.5 | 100 | 9.4225
57 | 79 | 0 | 13.54 | 2.9 | 8.6 | 100 | 9.454
57 | 80 | 0 | 13.54 | 2.9 | 8.7 | 100 | 9.4855
57 | 81 | 0 | 13.54 | 2.9 | 8.8 | 100 | 9.517
57 | 82 | 0 | 13.54 | 2.9 | 8.9 | 100 | 9.5485
57 | 83 | 0 | 13.54 | 2.9 | 9 | 100 | 9.58
57 | 84 | 0 | 13.54 | 2.9 | 9.1 | 100 | 9.669
57 | 85 | 0 | 13.54 | 2.9 | 9.2 | 100 | 9.758
57 | 86 | 0 | 13.54 | 2.9 | 9.3 | 100 | 9.847
57 | 87 | 0 | 13.54 | 2.9 | 9.4 | 100 | 9.936
57 | 88 | 0 | 13.54 | 2.9 | 9.5 | 100 | 10.025
57 | 89 | 0 | 13.54 | 2.9 | 9.6 | 100 | 10.114
57 | 90 | 0 | 13.54 | 2.9 | 9.7 | 100 | 10.203
57 | 91 | 0 | 13.54 | 2.9 | 9.8 | 100 | 10.292
57 | 92 | 0 | 13.54 | 2.9 | 9.9 | 100 | 10.381
57 | 93 | 0 | 13.54 | 2.9 | 10 | 100 | 10.47
57 | 94 | 0 | 13.54 | 3 | 3 | 100 | 6.5
57 | 95 | 0 | 13.54 | 3 | 3.1 | 100 | 6.585
57 | 96 | 0 | 13.54 | 3 | 3.2 | 100 | 6.67
57 | 97 | 0 | 13.54 | 3 | 3.3 | 100 | 6.755
57 | 98 | 0 | 13.54 | 3 | 3.4 | 100 | 6.84
57 | 99 | 0 | 13.54 | 3 | 3.5 | 100 | 6.925
57 | 100 | 0 | 13.54 | 3 | 3.6 | 100 | 7.01
57 | 101 | 0 | 13.54 | 3 | 3.7 | 100 | 7.095
57 | 102 | 0 | 13.54 | 3 | 3.8 | 100 | 7.18
57 | 103 | 0 | 13.54 | 3 | 3.9 | 100 | 7.265
57 | 104 | 0 | 13.54 | 3 | 4 | 100 | 7.35
57 | 105 | 0 | 13.54 | 3 | 4.1 | 100 | 7.435
57 | 106 | 0 | 13.54 | 3 | 4.2 | 100 | 7.52
57 | 107 | 0 | 13.54 | 3 | 4.3 | 100 | 7.605
57 | 108 | 0 | 13.54 | 3 | 4.4 | 100 | 7.69
57 | 109 | 0 | 13.54 | 3 | 4.5 | 100 | 7.775
57 | 110 | 0 | 13.54 | 3 | 4.6 | 100 | 7.86
57 | 111 | 0 | 13.54 | 3 | 4.7 | 100 | 7.945
57 | 112 | 0 | 13.54 | 3 | 4.8 | 100 | 8.03
57 | 113 | 0 | 13.54 | 3 | 4.9 | 100 | 8.115
57 | 114 | 0 | 13.54 | 3 | 5 | 100 | 8.2
57 | 115 | 0 | 13.54 | 3 | 5.1 | 100 | 8.24
57 | 116 | 0 | 13.54 | 3 | 5.2 | 100 | 8.28
57 | 117 | 0 | 13.54 | 3 | 5.3 | 100 | 8.32
57 | 118 | 0 | 13.54 | 3 | 5.4 | 100 | 8.36
57 | 119 | 0 | 13.54 | 3 | 5.5 | 100 | 8.4
57 | 120 | 0 | 13.54 | 3 | 5.6 | 100 | 8.44
57 | 121 | 0 | 13.54 | 3 | 5.7 | 100 | 8.48
57 | 122 | 0 | 13.54 | 3 | 5.8 | 100 | 8.52
57 | 123 | 0 | 13.54 | 3 | 5.9 | 100 | 8.56
57 | 124 | 0 | 13.54 | 3 | 6 | 100 | 8.6
57 | 125 | 0 | 13.54 | 3 | 6.1 | 100 | 8.64
57 | 126 | 0 | 13.54 | 3 | 6.2 | 100 | 8.68
57 | 127 | 0 | 13.54 | 3 | 6.3 | 100 | 8.72
57 | 128 | 0 | 13.54 | 3 | 6.4 | 100 | 8.76
57 | 129 | 0 | 13.54 | 3 | 6.5 | 100 | 8.8
57 | 130 | 0 | 13.54 | 3 | 6.6 | 100 | 8.84
57 | 131 | 0 | 13.54 | 3 | 6.7 | 100 | 8.88
57 | 132 | 0 | 13.54 | 3 | 6.8 | 100 | 8.92
57 | 133 | 0 | 13.54 | 3 | 6.9 | 100 | 8.96
57 | 134 | 0 | 13.54 | 3 | 7 | 100 | 9
57 | 135 | 0 | 13.54 | 3 | 7.1 | 100 | 9.03
57 | 136 | 0 | 13.54 | 3 | 7.2 | 100 | 9.06
57 | 137 | 0 | 13.54 | 3 | 7.3 | 100 | 9.09
57 | 138 | 0 | 13.54 | 3 | 7.4 | 100 | 9.12
57 | 139 | 0 | 13.54 | 3 | 7.5 | 100 | 9.15
57 | 140 | 0 | 13.54 | 3 | 7.6 | 100 | 9.18
57 | 141 | 0 | 13.54 | 3 | 7.7 | 100 | 9.21
57 | 142 | 0 | 13.54 | 3 | 7.8 | 100 | 9.24
57 | 143 | 0 | 13.54 | 3 | 7.9 | 100 | 9.27
57 | 144 | 0 | 13.54 | 3 | 8 | 100 | 9.3
57 | 145 | 0 | 13.54 | 3 | 8.1 | 100 | 9.33
57 | 146 | 0 | 13.54 | 3 | 8.2 | 100 | 9.36
57 | 147 | 0 | 13.54 | 3 | 8.3 | 100 | 9.39
57 | 148 | 0 | 13.54 | 3 | 8.4 | 100 | 9.42
57 | 149 | 0 | 13.54 | 3 | 8.5 | 100 | 9.45
57 | 150 | 0 | 13.54 | 3 | 8.6 | 100 | 9.48
58 | 45 | 0 | 13.56 | 3 | 8.7 | 100 | 9.51
58 | 46 | 0 | 13.56 | 3 | 8.8 | 100 | 9.54
58 | 47 | 0 | 13.56 | 3 | 8.9 | 100 | 9.57
58 | 48 | 0 | 13.56 | 3 | 9 | 100 | 9.6
58 | 49 | 0 | 13.56 | 3 | 9.1 | 100 | 9.69
58 | 50 | 0 | 13.56 | 3 | 9.2 | 100 | 9.78
58 | 51 | 0 | 13.56 | 3 | 9.3 | 100 | 9.87
58 | 52 | 0 | 13.56 | 3 | 9.4 | 100 | 9.96
58 | 53 | 0 | 13.56 | 3 | 9.5 | 100 | 10.05
58 | 54 | 0 | 13.56 | 3 | 9.6 | 100 | 10.14
58 | 55 | 0 | 13.56 | 3 | 9.7 | 100 | 10.23
58 | 56 | 0 | 13.56 | 3 | 9.8 | 100 | 10.32
58 | 57 | 0 | 13.56 | 3 | 9.9 | 100 | 10.41
58 | 58 | 0 | 13.56 | 3 | 10 | 100 | 10.5
58 | 59 | 0 | 13.56 | 3.1 | 3 | 100 | 6.53
58 | 60 | 0 | 13.56 | 3.1 | 3.1 | 100 | 6.6135
58 | 61 | 0 | 13.56 | 3.1 | 3.2 | 100 | 6.697
58 | 62 | 0 | 13.56 | 3.1 | 3.3 | 100 | 6.7805
58 | 63 | 0 | 13.56 | 3.1 | 3.4 | 100 | 6.864
58 | 64 | 0 | 13.56 | 3.1 | 3.5 | 100 | 6.9475
58 | 65 | 0 | 13.56 | 3.1 | 3.6 | 100 | 7.031
58 | 66 | 0 | 13.56 | 3.1 | 3.7 | 100 | 7.1145
58 | 67 | 0 | 13.56 | 3.1 | 3.8 | 100 | 7.198
58 | 68 | 0 | 13.56 | 3.1 | 3.9 | 100 | 7.2815
58 | 69 | 0 | 13.56 | 3.1 | 4 | 100 | 7.365
58 | 70 | 0 | 13.56 | 3.1 | 4.1 | 100 | 7.4485
58 | 71 | 0 | 13.56 | 3.1 | 4.2 | 100 | 7.532
58 | 72 | 0 | 13.56 | 3.1 | 4.3 | 100 | 7.6155
58 | 73 | 0 | 13.56 | 3.1 | 4.4 | 100 | 7.699
58 | 74 | 0 | 13.56 | 3.1 | 4.5 | 100 | 7.7825
58 | 75 | 0 | 13.56 | 3.1 | 4.6 | 100 | 7.866
58 | 76 | 0 | 13.56 | 3.1 | 4.7 | 100 | 7.9495
58 | 77 | 0 | 13.56 | 3.1 | 4.8 | 100 | 8.033
58 | 78 | 0 | 13.56 | 3.1 | 4.9 | 100 | 8.1165
58 | 79 | 0 | 13.56 | 3.1 | 5 | 100 | 8.2
58 | 80 | 0 | 13.56 | 3.1 | 5.1 | 100 | 8.2445
58 | 81 | 0 | 13.56 | 3.1 | 5.2 | 100 | 8.289
58 | 82 | 0 | 13.56 | 3.1 | 5.3 | 100 | 8.3335
58 | 83 | 0 | 13.56 | 3.1 | 5.4 | 100 | 8.378
58 | 84 | 0 | 13.56 | 3.1 | 5.5 | 100 | 8.4225
58 | 85 | 0 | 13.56 | 3.1 | 5.6 | 100 | 8.467
58 | 86 | 0 | 13.56 | 3.1 | 5.7 | 100 | 8.5115
58 | 87 | 0 | 13.56 | 3.1 | 5.8 | 100 | 8.556
58 | 88 | 0 | 13.56 | 3.1 | 5.9 | 100 | 8.6005
58 | 89 | 0 | 13.56 | 3.1 | 6 | 100 | 8.645
58 | 90 | 0 | 13.56 | 3.1 | 6.1 | 100 | 8.6895
58 | 91 | 0 | 13.56 | 3.1 | 6.2 | 100 | 8.734
58 | 92 | 0 | 13.56 | 3.1 | 6.3 | 100 | 8.7785
58 | 93 | 0 | 13.56 | 3.1 | 6.4 | 100 | 8.823
58 | 94 | 0 | 13.56 | 3.1 | 6.5 | 100 | 8.8675
58 | 95 | 0 | 13.56 | 3.1 | 6.6 | 100 | 8.912
58 | 96 | 0 | 13.56 | 3.1 | 6.7 | 100 | 8.9565
58 | 97 | 0 | 13.56 | 3.1 | 6.8 | 100 | 9.001
58 | 98 | 0 | 13.56 | 3.1 | 6.9 | 100 | 9.0455
58 | 99 | 0 | 13.56 | 3.1 | 7 | 100 | 9.09
58 | 100 | 0 | 13.56 | 3.1 | 7.1 | 100 | 9.1175
58 | 101 | 0 | 13.56 | 3.1 | 7.2 | 100 | 9.145
58 | 102 | 0 | 13.56 | 3.1 | 7.3 | 100 | 9.1725
58 | 103 | 0 | 13.56 | 3.1 | 7.4 | 100 | 9.2
58 | 104 | 0 | 13.56 | 3.1 | 7.5 | 100 | 9.2275
58 | 105 | 0 | 13.56 | 3.1 | 7.6 | 100 | 9.255
58 | 106 | 0 | 13.56 | 3.1 | 7.7 | 100 | 9.2825
58 | 107 | 0 | 13.56 | 3.1 | 7.8 | 100 | 9.31
58 | 108 | 0 | 13.56 | 3.1 | 7.9 | 100 | 9.3375
58 | 109 | 0 | 13.56 | 3.1 | 8 | 100 | 9.365
58 | 110 | 0 | 13.56 | 3.1 | 8.1 | 100 | 9.3925
58 | 111 | 0 | 13.56 | 3.1 | 8.2 | 100 | 9.42
58 | 112 | 0 | 13.56 | 3.1 | 8.3 | 100 | 9.4475
58 | 113 | 0 | 13.56 | 3.1 | 8.4 | 100 | 9.475
58 | 114 | 0 | 13.56 | 3.1 | 8.5 | 100 | 9.5025
58 | 115 | 0 | 13.56 | 3.1 | 8.6 | 100 | 9.53
58 | 116 | 0 | 13.56 | 3.1 | 8.7 | 100 | 9.5575
58 | 117 | 0 | 13.56 | 3.1 | 8.8 | 100 | 9.585
58 | 118 | 0 | 13.56 | 3.1 | 8.9 | 100 | 9.6125
58 | 119 | 0 | 13.56 | 3.1 | 9 | 100 | 9.64
58 | 120 | 0 | 13.56 | 3.1 | 9.1 | 100 | 9.728
58 | 121 | 0 | 13.56 | 3.1 | 9.2 | 100 | 9.816
58 | 122 | 0 | 13.56 | 3.1 | 9.3 | 100 | 9.904
58 | 123 | 0 | 13.56 | 3.1 | 9.4 | 100 | 9.992
58 | 124 | 0 | 13.56 | 3.1 | 9.5 | 100 | 10.08
58 | 125 | 0 | 13.56 | 3.1 | 9.6 | 100 | 10.168
58 | 126 | 0 | 13.56 | 3.1 | 9.7 | 100 | 10.256
58 | 127 | 0 | 13.56 | 3.1 | 9.8 | 100 | 10.344
58 | 128 | 0 | 13.56 | 3.1 | 9.9 | 100 | 10.432
58 | 129 | 0 | 13.56 | 3.1 | 10 | 100 | 10.52
58 | 130 | 0 | 13.56 | 3.2 | 3 | 100 | 6.56
58 | 131 | 0 | 13.56 | 3.2 | 3.1 | 100 | 6.642
58 | 132 | 0 | 13.56 | 3.2 | 3.2 | 100 | 6.724
58 | 133 | 0 | 13.56 | 3.2 | 3.3 | 100 | 6.806
58 | 134 | 0 | 13.56 | 3.2 | 3.4 | 100 | 6.888
58 | 135 | 0 | 13.56 | 3.2 | 3.5 | 100 | 6.97
58 | 136 | 0 | 13.56 | 3.2 | 3.6 | 100 | 7.052
58 | 137 | 0 | 13.56 | 3.2 | 3.7 | 100 | 7.134
58 | 138 | 0 | 13.56 | 3.2 | 3.8 | 100 | 7.216
58 | 139 | 0 | 13.56 | 3.2 | 3.9 | 100 | 7.298
58 | 140 | 0 | 13.56 | 3.2 | 4 | 100 | 7.38
58 | 141 | 0 | 13.56 | 3.2 | 4.1 | 100 | 7.462
58 | 142 | 0 | 13.56 | 3.2 | 4.2 | 100 | 7.544
58 | 143 | 0 | 13.56 | 3.2 | 4.3 | 100 | 7.626
58 | 144 | 0 | 13.56 | 3.2 | 4.4 | 100 | 7.708
58 | 145 | 0 | 13.56 | 3.2 | 4.5 | 100 | 7.79
58 | 146 | 0 | 13.56 | 3.2 | 4.6 | 100 | 7.872
58 | 147 | 0 | 13.56 | 3.2 | 4.7 | 100 | 7.954
58 | 148 | 0 | 13.56 | 3.2 | 4.8 | 100 | 8.036
58 | 149 | 0 | 13.56 | 3.2 | 4.9 | 100 | 8.118
58 | 150 | 0 | 13.56 | 3.2 | 5 | 100 | 8.2
59 | 45 | 0 | 13.58 | 3.2 | 5.1 | 100 | 8.249
59 | 46 | 0 | 13.58 | 3.2 | 5.2 | 100 | 8.298
59 | 47 | 0 | 13.58 | 3.2 | 5.3 | 100 | 8.347
59 | 48 | 0 | 13.58 | 3.2 | 5.4 | 100 | 8.396
59 | 49 | 0 | 13.58 | 3.2 | 5.5 | 100 | 8.445
59 | 50 | 0 | 13.58 | 3.2 | 5.6 | 100 | 8.494
59 | 51 | 0 | 13.58 | 3.2 | 5.7 | 100 | 8.543
59 | 52 | 0 | 13.58 | 3.2 | 5.8 | 100 | 8.592
59 | 53 | 0 | 13.58 | 3.2 | 5.9 | 100 | 8.641
59 | 54 | 0 | 13.58 | 3.2 | 6 | 100 | 8.69
59 | 55 | 0 | 13.58 | 3.2 | 6.1 | 100 | 8.739
59 | 56 | 0 | 13.58 | 3.2 | 6.2 | 100 | 8.788
59 | 57 | 0 | 13.58 | 3.2 | 6.3 | 100 | 8.837
59 | 58 | 0 | 13.58 | 3.2 | 6.4 | 100 | 8.886
59 | 59 | 0 | 13.58 | 3.2 | 6.5 | 100 | 8.935
59 | 60 | 0 | 13.58 | 3.2 | 6.6 | 100 | 8.984
59 | 61 | 0 | 13.58 | 3.2 | 6.7 | 100 | 9.033
59 | 62 | 0 | 13.58 | 3.2 | 6.8 | 100 | 9.082
59 | 63 | 0 | 13.58 | 3.2 | 6.9 | 100 | 9.131
59 | 64 | 0 | 13.58 | 3.2 | 7 | 100 | 9.18
59 | 65 | 0 | 13.58 | 3.2 | 7.1 | 100 | 9.205
59 | 66 | 0 | 13.58 | 3.2 | 7.2 | 100 | 9.23
59 | 67 | 0 | 13.58 | 3.2 | 7.3 | 100 | 9.255
59 | 68 | 0 | 13.58 | 3.2 | 7.4 | 100 | 9.28
59 | 69 | 0 | 13.58 | 3.2 | 7.5 | 100 | 9.305
59 | 70 | 0 | 13.58 | 3.2 | 7.6 | 100 | 9.33
59 | 71 | 0 | 13.58 | 3.2 | 7.7 | 100 | 9.355
59 | 72 | 0 | 13.58 | 3.2 | 7.8 | 100 | 9.38
59 | 73 | 0 | 13.58 | 3.2 | 7.9 | 100 | 9.405
59 | 74 | 0 | 13.58 | 3.2 | 8 | 100 | 9.43
59 | 75 | 0 | 13.58 | 3.2 | 8.1 | 100 | 9.455
59 | 76 | 0 | 13.58 | 3.2 | 8.2 | 100 | 9.48
59 | 77 | 0 | 13.58 | 3.2 | 8.3 | 100 | 9.505
59 | 78 | 0 | 13.58 | 3.2 | 8.4 | 100 | 9.53
59 | 79 | 0 | 13.58 | 3.2 | 8.5 | 100 | 9.555
59 | 80 | 0 | 13.58 | 3.2 | 8.6 | 100 | 9.58
59 | 81 | 0 | 13.58 | 3.2 | 8.7 | 100 | 9.605
59 | 82 | 0 | 13.58 | 3.2 | 8.8 | 100 | 9.63
59 | 83 | 0 | 13.58 | 3.2 | 8.9 | 100 | 9.655
59 | 84 | 0 | 13.58 | 3.2 | 9 | 100 | 9.68
59 | 85 | 0 | 13.58 | 3.2 | 9.1 | 100 | 9.766
59 | 86 | 0 | 13.58 | 3.2 | 9.2 | 100 | 9.852
59 | 87 | 0 | 13.58 | 3.2 | 9.3 | 100 | 9.938
59 | 88 | 0 | 13.58 | 3.2 | 9.4 | 100 | 10.024
59 | 89 | 0 | 13.58 | 3.2 | 9.5 | 100 | 10.11
59 | 90 | 0 | 13.58 | 3.2 | 9.6 | 100 | 10.196
59 | 91 | 0 | 13.58 | 3.2 | 9.7 | 100 | 10.282
59 | 92 | 0 | 13.58 | 3.2 | 9.8 | 100 | 10.368
59 | 93 | 0 | 13.58 | 3.2 | 9.9 | 100 | 10.454
59 | 94 | 0 | 13.58 | 3.2 | 10 | 100 | 10.54
59 | 95 | 0 | 13.58 | 3.3 | 3 | 100 | 6.59
59 | 96 | 0 | 13.58 | 3.3 | 3.1 | 100 | 6.6705
59 | 97 | 0 | 13.58 | 3.3 | 3.2 | 100 | 6.751
59 | 98 | 0 | 13.58 | 3.3 | 3.3 | 100 | 6.8315
59 | 99 | 0 | 13.58 | 3.3 | 3.4 | 100 | 6.912
59 | 100 | 0 | 13.58 | 3.3 | 3.5 | 100 | 6.9925
59 | 101 | 0 | 13.58 | 3.3 | 3.6 | 100 | 7.073
59 | 102 | 0 | 13.58 | 3.3 | 3.7 | 100 | 7.1535
59 | 103 | 0 | 13.58 | 3.3 | 3.8 | 100 | 7.234
59 | 104 | 0 | 13.58 | 3.3 | 3.9 | 100 | 7.3145
59 | 105 | 0 | 13.58 | 3.3 | 4 | 100 | 7.395
59 | 106 | 0 | 13.58 | 3.3 | 4.1 | 100 | 7.4755
59 | 107 | 0 | 13.58 | 3.3 | 4.2 | 100 | 7.556
59 | 108 | 0 | 13.58 | 3.3 | 4.3 | 100 | 7.6365
59 | 109 | 0 | 13.58 | 3.3 | 4.4 | 100 | 7.717
59 | 110 | 0 | 13.58 | 3.3 | 4.5 | 100 | 7.7975
59 | 111 | 0 | 13.58 | 3.3 | 4.6 | 100 | 7.878
59 | 112 | 0 | 13.58 | 3.3 | 4.7 | 100 | 7.9585
59 | 113 | 0 | 13.58 | 3.3 | 4.8 | 100 | 8.039
59 | 114 | 0 | 13.58 | 3.3 | 4.9 | 100 | 8.1195
59 | 115 | 0 | 13.58 | 3.3 | 5 | 100 | 8.2
59 | 116 | 0 | 13.58 | 3.3 | 5.1 | 100 | 8.2535
59 | 117 | 0 | 13.58 | 3.3 | 5.2 | 100 | 8.307
59 | 118 | 0 | 13.58 | 3.3 | 5.3 | 100 | 8.3605
59 | 119 | 0 | 13.58 | 3.3 | 5.4 | 100 | 8.414
59 | 120 | 0 | 13.58 | 3.3 | 5.5 | 100 | 8.4675
59 | 121 | 0 | 13.58 | 3.3 | 5.6 | 100 | 8.521
59 | 122 | 0 | 13.58 | 3.3 | 5.7 | 100 | 8.5745
59 | 123 | 0 | 13.58 | 3.3 | 5.8 | 100 | 8.628
59 | 124 | 0 | 13.58 | 3.3 | 5.9 | 100 | 8.6815
59 | 125 | 0 | 13.58 | 3.3 | 6 | 100 | 8.735
59 | 126 | 0 | 13.58 | 3.3 | 6.1 | 100 | 8.7885
59 | 127 | 0 | 13.58 | 3.3 | 6.2 | 100 | 8.842
59 | 128 | 0 | 13.58 | 3.3 | 6.3 | 100 | 8.8955
59 | 129 | 0 | 13.58 | 3.3 | 6.4 | 100 | 8.949
59 | 130 | 0 | 13.58 | 3.3 | 6.5 | 100 | 9.0025
59 | 131 | 0 | 13.58 | 3.3 | 6.6 | 100 | 9.056
59 | 132 | 0 | 13.58 | 3.3 | 6.7 | 100 | 9.1095
59 | 133 | 0 | 13.58 | 3.3 | 6.8 | 100 | 9.163
59 | 134 | 0 | 13.58 | 3.3 | 6.9 | 100 | 9.2165
59 | 135 | 0 | 13.58 | 3.3 | 7 | 100 | 9.27
59 | 136 | 0 | 13.58 | 3.3 | 7.1 | 100 | 9.2925
59 | 137 | 0 | 13.58 | 3.3 | 7.2 | 100 | 9.315
59 | 138 | 0 | 13.58 | 3.3 | 7.3 | 100 | 9.3375
59 | 139 | 0 | 13.58 | 3.3 | 7.4 | 100 | 9.36
59 | 140 | 0 | 13.58 | 3.3 | 7.5 | 100 | 9.3825
59 | 141 | 0 | 13.58 | 3.3 | 7.6 | 100 | 9.405
59 | 142 | 0 | 13.58 | 3.3 | 7.7 | 100 | 9.4275
59 | 143 | 0 | 13.58 | 3.3 | 7.8 | 100 | 9.45
59 | 144 | 0 | 13.58 | 3.3 | 7.9 | 100 | 9.4725
59 | 145 | 0 | 13.58 | 3.3 | 8 | 100 | 9.495
59 | 146 | 0 | 13.58 | 3.3 | 8.1 | 100 | 9.5175
59 | 147 | 0 | 13.58 | 3.3 | 8.2 | 100 | 9.54
59 | 148 | 0 | 13.58 | 3.3 | 8.3 | 100 | 9.5625
59 | 149 | 0 | 13.58 | 3.3 | 8.4 | 100 | 9.585
59 | 150 | 0 | 13.58 | 3.3 | 8.5 | 100 | 9.6075
60 | 45 | 0 | 13.6 | 3.3 | 8.6 | 100 | 9.63
60 | 46 | 0 | 13.6 | 3.3 | 8.7 | 100 | 9.6525
60 | 47 | 0 | 13.6 | 3.3 | 8.8 | 100 | 9.675
60 | 48 | 0 | 13.6 | 3.3 | 8.9 | 100 | 9.6975
60 | 49 | 0 | 13.6 | 3.3 | 9 | 100 | 9.72
60 | 50 | 0 | 13.6 | 3.3 | 9.1 | 100 | 9.804
60 | 51 | 0 | 13.6 | 3.3 | 9.2 | 100 | 9.888
60 | 52 | 0 | 13.6 | 3.3 | 9.3 | 100 | 9.972
60 | 53 | 0 | 13.6 | 3.3 | 9.4 | 100 | 10.056
60 | 54 | 0 | 13.6 | 3.3 | 9.5 | 100 | 10.14
60 | 55 | 0 | 13.6 | 3.3 | 9.6 | 100 | 10.224
60 | 56 | 0 | 13.6 | 3.3 | 9.7 | 100 | 10.308
60 | 57 | 0 | 13.6 | 3.3 | 9.8 | 100 | 10.392
60 | 58 | 0 | 13.6 | 3.3 | 9.9 | 100 | 10.476
60 | 59 | 0 | 13.6 | 3.3 | 10 | 100 | 10.56
60 | 60 | 0 | 13.6 | 3.4 | 3 | 100 | 6.62
60 | 61 | 0 | 13.6 | 3.4 | 3.1 | 100 | 6.699
60 | 62 | 0 | 13.6 | 3.4 | 3.2 | 100 | 6.778
60 | 63 | 0 | 13.6 | 3.4 | 3.3 | 100 | 6.857
60 | 64 | 0 | 13.6 | 3.4 | 3.4 | 100 | 6.936
60 | 65 | 0 | 13.6 | 3.4 | 3.5 | 100 | 7.015
60 | 66 | 0 | 13.6 | 3.4 | 3.6 | 100 | 7.094
60 | 67 | 0 | 13.6 | 3.4 | 3.7 | 100 | 7.173
60 | 68 | 0 | 13.6 | 3.4 | 3.8 | 100 | 7.252
60 | 69 | 0 | 13.6 | 3.4 | 3.9 | 100 | 7.331
60 | 70 | 0 | 13.6 | 3.4 | 4 | 100 | 7.41
60 | 71 | 0 | 13.6 | 3.4 | 4.1 | 100 | 7.489
60 | 72 | 0 | 13.6 | 3.4 | 4.2 | 100 | 7.568
60 | 73 | 0 | 13.6 | 3.4 | 4.3 | 100 | 7.647
60 | 74 | 0 | 13.6 | 3.4 | 4.4 | 100 | 7.726
60 | 75 | 0 | 13.6 | 3.4 | 4.5 | 100 | 7.805
60 | 76 | 0 | 13.6 | 3.4 | 4.6 | 100 | 7.884
60 | 77 | 0 | 13.6 | 3.4 | 4.7 | 100 | 7.963
60 | 78 | 0 | 13.6 | 3.4 | 4.8 | 100 | 8.042
60 | 79 | 0 | 13.6 | 3.4 | 4.9 | 100 | 8.121
60 | 80 | 0 | 13.6 | 3.4 | 5 | 100 | 8.2
60 | 81 | 0 | 13.6 | 3.4 | 5.1 | 100 | 8.258
60 | 82 | 0 | 13.6 | 3.4 | 5.2 | 100 | 8.316
60 | 83 | 0 | 13.6 | 3.4 | 5.3 | 100 | 8.374
60 | 84 | 0 | 13.6 | 3.4 | 5.4 | 100 | 8.432
60 | 85 | 0 | 13.6 | 3.4 | 5.5 | 100 | 8.49
60 | 86 | 0 | 13.6 | 3.4 | 5.6 | 100 | 8.548
60 | 87 | 0 | 13.6 | 3.4 | 5.7 | 100 | 8.606
60 | 88 | 0 | 13.6 | 3.4 | 5.8 | 100 | 8.664
60 | 89 | 0 | 13.6 | 3.4 | 5.9 | 100 | 8.722
60 | 90 | 0 | 13.6 | 3.4 | 6 | 100 | 8.78
60 | 91 | 0 | 13.6 | 3.4 | 6.1 | 100 | 8.838
60 | 92 | 0 | 13.6 | 3.4 | 6.2 | 100 | 8.896
60 | 93 | 0 | 13.6 | 3.4 | 6.3 | 100 | 8.954
60 | 94 | 0 | 13.6 | 3.4 | 6.4 | 100 | 9.012
60 | 95 | 0 | 13.6 | 3.4 | 6.5 | 100 | 9.07
60 | 96 | 0 | 13.6 | 3.4 | 6.6 | 100 | 9.128
60 | 97 | 0 | 13.6 | 3.4 | 6.7 | 100 | 9.186
60 | 98 | 0 | 13.6 | 3.4 | 6.8 | 100 | 9.244
60 | 99 | 0 | 13.6 | 3.4 | 6.9 | 100 | 9.302
60 | 100 | 0 | 13.6 | 3.4 | 7 | 100 | 9.36
60 | 101 | 0 | 13.6 | 3.4 | 7.1 | 100 | 9.38
60 | 102 | 0 | 13.6 | 3.4 | 7.2 | 100 | 9.4
60 | 103 | 0 | 13.6 | 3.4 | 7.3 | 100 | 9.42
60 | 104 | 0 | 13.6 | 3.4 | 7.4 | 100 | 9.44
60 | 105 | 0 | 13.6 | 3.4 | 7.5 | 100 | 9.46
60 | 106 | 0 | 13.6 | 3.4 | 7.6 | 100 | 9.48
60 | 107 | 0 | 13.6 | 3.4 | 7.7 | 100 | 9.5
60 | 108 | 0 | 13.6 | 3.4 | 7.8 | 100 | 9.52
60 | 109 | 0 | 13.6 | 3.4 | 7.9 | 100 | 9.54
60 | 110 | 0 | 13.6 | 3.4 | 8 | 100 | 9.56
60 | 111 | 0 | 13.6 | 3.4 | 8.1 | 100 | 9.58
60 | 112 | 0 | 13.6 | 3.4 | 8.2 | 100 | 9.6
60 | 113 | 0 | 13.6 | 3.4 | 8.3 | 100 | 9.62
60 | 114 | 0 | 13.6 | 3.4 | 8.4 | 100 | 9.64
60 | 115 | 0 | 13.6 | 3.4 | 8.5 | 100 | 9.66
60 | 116 | 0 | 13.6 | 3.4 | 8.6 | 100 | 9.68
60 | 117 | 0 | 13.6 | 3.4 | 8.7 | 100 | 9.7
60 | 118 | 0 | 13.6 | 3.4 | 8.8 | 100 | 9.72
60 | 119 | 0 | 13.6 | 3.4 | 8.9 | 100 | 9.74
60 | 120 | 0 | 13.6 | 3.4 | 9 | 100 | 9.76
60 | 121 | 0 | 13.6 | 3.4 | 9.1 | 100 | 9.842
60 | 122 | 0 | 13.6 | 3.4 | 9.2 | 100 | 9.924
60 | 123 | 0 | 13.6 | 3.4 | 9.3 | 100 | 10.006
60 | 124 | 0 | 13.6 | 3.4 | 9.4 | 100 | 10.088
60 | 125 | 0 | 13.6 | 3.4 | 9.5 | 100 | 10.17
60 | 126 | 0 | 13.6 | 3.4 | 9.6 | 100 | 10.252
60 | 127 | 0 | 13.6 | 3.4 | 9.7 | 100 | 10.334
60 | 128 | 0 | 13.6 | 3.4 | 9.8 | 100 | 10.416
60 | 129 | 0 | 13.6 | 3.4 | 9.9 | 100 | 10.498
60 | 130 | 0 | 13.6 | 3.4 | 10 | 100 | 10.58
60 | 131 | 0 | 13.6 | 3.5 | 3 | 100 | 6.65
60 | 132 | 0 | 13.6 | 3.5 | 3.1 | 100 | 6.7275
60 | 133 | 0 | 13.6 | 3.5 | 3.2 | 100 | 6.805
60 | 134 | 0 | 13.6 | 3.5 | 3.3 | 100 | 6.8825
60 | 135 | 0 | 13.6 | 3.5 | 3.4 | 100 | 6.96
60 | 136 | 0 | 13.6 | 3.5 | 3.5 | 100 | 7.0375
60 | 137 | 0 | 13.6 | 3.5 | 3.6 | 100 | 7.115
60 | 138 | 0 | 13.6 | 3.5 | 3.7 | 100 | 7.1925
60 | 139 | 0 | 13.6 | 3.5 | 3.8 | 100 | 7.27
60 | 140 | 0 | 13.6 | 3.5 | 3.9 | 100 | 7.3475
60 | 141 | 0 | 13.6 | 3.5 | 4 | 100 | 7.425
60 | 142 | 0 | 13.6 | 3.5 | 4.1 | 100 | 7.5025
60 | 143 | 0 | 13.6 | 3.5 | 4.2 | 100 | 7.58
60 | 144 | 0 | 13.6 | 3.5 | 4.3 | 100 | 7.6575
60 | 145 | 0 | 13.6 | 3.5 | 4.4 | 100 | 7.735
60 | 146 | 0 | 13.6 | 3.5 | 4.5 | 100 | 7.8125
60 | 147 | 0 | 13.6 | 3.5 | 4.6 | 100 | 7.89
60 | 148 | 0 | 13.6 | 3.5 | 4.7 | 100 | 7.9675
60 | 149 | 0 | 13.6 | 3.5 | 4.8 | 100 | 8.045
60 | 150 | 0 | 13.6 | 3.5 | 4.9 | 100 | 8.1225
61 | 45 | 0 | 13.6133 | 3.5 | 5 | 100 | 8.2
61 | 46 | 0 | 13.6133 | 3.5 | 5.1 | 100 | 8.2625
61 | 47 | 0 | 13.6133 | 3.5 | 5.2 | 100 | 8.325
61 | 48 | 0 | 13.6133 | 3.5 | 5.3 | 100 | 8.3875
61 | 49 | 0 | 13.6133 | 3.5 | 5.4 | 100 | 8.45
61 | 50 | 0 | 13.6133 | 3.5 | 5.5 | 100 | 8.5125
61 | 51 | 0 | 13.6133 | 3.5 | 5.6 | 100 | 8.575
61 | 52 | 0 | 13.6133 | 3.5 | 5.7 | 100 | 8.6375
61 | 53 | 0 | 13.6133 | 3.5 | 5.8 | 100 | 8.7
61 | 54 | 0 | 13.6133 | 3.5 | 5.9 | 100 | 8.7625
61 | 55 | 0 | 13.6133 | 3.5 | 6 | 100 | 8.825
61 | 56 | 0 | 13.6133 | 3.5 | 6.1 | 100 | 8.8875
61 | 57 | 0 | 13.6133 | 3.5 | 6.2 | 100 | 8.95
61 | 58 | 0 | 13.6133 | 3.5 | 6.3 | 100 | 9.0125
61 | 59 | 0 | 13.6133 | 3.5 | 6.4 | 100 | 9.075
61 | 60 | 0 | 13.6133 | 3.5 | 6.5 | 100 | 9.1375
61 | 61 | 0 | 13.6133 | 3.5 | 6.6 | 100 | 9.2
61 | 62 | 0 | 13.6133 | 3.5 | 6.7 | 100 | 9.2625
61 | 63 | 0 | 13.6133 | 3.5 | 6.8 | 100 | 9.325
61 | 64 | 0 | 13.6133 | 3.5 | 6.9 | 100 | 9.3875
61 | 65 | 0 | 13.6133 | 3.5 | 7 | 100 | 9.45
61 | 66 | 0 | 13.6133 | 3.5 | 7.1 | 100 | 9.4675
61 | 67 | 0 | 13.6133 | 3.5 | 7.2 | 100 | 9.485
61 | 68 | 0 | 13.6133 | 3.5 | 7.3 | 100 | 9.5025
61 | 69 | 0 | 13.6133 | 3.5 | 7.4 | 100 | 9.52
61 | 70 | 0 | 13.6133 | 3.5 | 7.5 | 100 | 9.5375
61 | 71 | 0 | 13.6133 | 3.5 | 7.6 | 100 | 9.555
61 | 72 | 0 | 13.6133 | 3.5 | 7.7 | 100 | 9.5725
61 | 73 | 0 | 13.6133 | 3.5 | 7.8 | 100 | 9.59
61 | 74 | 0 | 13.6133 | 3.5 | 7.9 | 100 | 9.6075
61 | 75 | 0 | 13.6133 | 3.5 | 8 | 100 | 9.625
61 | 76 | 0 | 13.6133 | 3.5 | 8.1 | 100 | 9.6425
61 | 77 | 0 | 13.6133 | 3.5 | 8.2 | 100 | 9.66
61 | 78 | 0 | 13.6133 | 3.5 | 8.3 | 100 | 9.6775
61 | 79 | 0 | 13.6133 | 3.5 | 8.4 | 100 | 9.695
61 | 80 | 0 | 13.6133 | 3.5 | 8.5 | 100 | 9.7125
61 | 81 | 0 | 13.6133 | 3.5 | 8.6 | 100 | 9.73
61 | 82 | 0 | 13.6133 | 3.5 | 8.7 | 100 | 9.7475
61 | 83 | 0 | 13.6133 | 3.5 | 8.8 | 100 | 9.765
61 | 84 | 0 | 13.6133 | 3.5 | 8.9 | 100 | 9.7825
61 | 85 | 0 | 13.6133 | 3.5 | 9 | 100 | 9.8
61 | 86 | 0 | 13.6133 | 3.5 | 9.1 | 100 | 9.88
61 | 87 | 0 | 13.6133 | 3.5 | 9.2 | 100 | 9.96
61 | 88 | 0 | 13.6133 | 3.5 | 9.3 | 100 | 10.04
61 | 89 | 0 | 13.6133 | 3.5 | 9.4 | 100 | 10.12
61 | 90 | 0 | 13.6133 | 3.5 | 9.5 | 100 | 10.2
61 | 91 | 0 | 13.6133 | 3.5 | 9.6 | 100 | 10.28
61 | 92 | 0 | 13.6133 | 3.5 | 9.7 | 100 | 10.36
61 | 93 | 0 | 13.6133 | 3.5 | 9.8 | 100 | 10.44
61 | 94 | 0 | 13.6133 | 3.5 | 9.9 | 100 | 10.52
61 | 95 | 0 | 13.6133 | 3.5 | 10 | 100 | 10.6
61 | 96 | 0 | 13.6133 | 3.6 | 3 | 100 | 6.68
61 | 97 | 0 | 13.6133 | 3.6 | 3.1 | 100 | 6.756
61 | 98 | 0 | 13.6133 | 3.6 | 3.2 | 100 | 6.832
61 | 99 | 0 | 13.6133 | 3.6 | 3.3 | 100 | 6.908
61 | 100 | 0 | 13.6133 | 3.6 | 3.4 | 100 | 6.984
61 | 101 | 0 | 13.6133 | 3.6 | 3.5 | 100 | 7.06
61 | 102 | 0 | 13.6133 | 3.6 | 3.6 | 100 | 7.136
61 | 103 | 0 | 13.6133 | 3.6 | 3.7 | 100 | 7.212
61 | 104 | 0 | 13.6133 | 3.6 | 3.8 | 100 | 7.288
61 | 105 | 0 | 13.6133 | 3.6 | 3.9 | 100 | 7.364
61 | 106 | 0 | 13.6133 | 3.6 | 4 | 100 | 7.44
61 | 107 | 0 | 13.6133 | 3.6 | 4.1 | 100 | 7.516
61 | 108 | 0 | 13.6133 | 3.6 | 4.2 | 100 | 7.592
61 | 109 | 0 | 13.6133 | 3.6 | 4.3 | 100 | 7.668
61 | 110 | 0 | 13.6133 | 3.6 | 4.4 | 100 | 7.744
61 | 111 | 0 | 13.6133 | 3.6 | 4.5 | 100 | 7.82
61 | 112 | 0 | 13.6133 | 3.6 | 4.6 | 100 | 7.896
61 | 113 | 0 | 13.6133 | 3.6 | 4.7 | 100 | 7.972
61 | 114 | 0 | 13.6133 | 3.6 | 4.8 | 100 | 8.048
61 | 115 | 0 | 13.6133 | 3.6 | 4.9 | 100 | 8.124
61 | 116 | 0 | 13.6133 | 3.6 | 5 | 100 | 8.2
61 | 117 | 0 | 13.6133 | 3.6 | 5.1 | 100 | 8.267
61 | 118 | 0 | 13.6133 | 3.6 | 5.2 | 100 | 8.334
61 | 119 | 0 | 13.6133 | 3.6 | 5.3 | 100 | 8.401
61 | 120 | 0 | 13.6133 | 3.6 | 5.4 | 100 | 8.468
61 | 121 | 0 | 13.6133 | 3.6 | 5.5 | 100 | 8.535
61 | 122 | 0 | 13.6133 | 3.6 | 5.6 | 100 | 8.602
61 | 123 | 0 | 13.6133 | 3.6 | 5.7 | 100 | 8.669
61 | 124 | 0 | 13.6133 | 3.6 | 5.8 | 100 | 8.736
61 | 125 | 0 | 13.6133 | 3.6 | 5.9 | 100 | 8.803
61 | 126 | 0 | 13.6133 | 3.6 | 6 | 100 | 8.87
61 | 127 | 0 | 13.6133 | 3.6 | 6.1 | 100 | 8.937
61 | 128 | 0 | 13.6133 | 3.6 | 6.2 | 100 | 9.004
61 | 129 | 0 | 13.6133 | 3.6 | 6.3 | 100 | 9.071
61 | 130 | 0 | 13.6133 | 3.6 | 6.4 | 100 | 9.138
61 | 131 | 0 | 13.6133 | 3.6 | 6.5 | 100 | 9.205
61 | 132 | 0 | 13.6133 | 3.6 | 6.6 | 100 | 9.272
61 | 133 | 0 | 13.6133 | 3.6 | 6.7 | 100 | 9.339
61 | 134 | 0 | 13.6133 | 3.6 | 6.8 | 100 | 9.406
61 | 135 | 0 | 13.6133 | 3.6 | 6.9 | 100 | 9.473
61 | 136 | 0 | 13.6133 | 3.6 | 7 | 100 | 9.54
61 | 137 | 0 | 13.6133 | 3.6 | 7.1 | 100 | 9.555
61 | 138 | 0 | 13.6133 | 3.6 | 7.2 | 100 | 9.57
61 | 139 | 0 | 13.6133 | 3.6 | 7.3 | 100 | 9.585
61 | 140 | 0 | 13.6133 | 3.6 | 7.4 | 100 | 9.6
61 | 141 | 0 | 13.6133 | 3.6 | 7.5 | 100 | 9.615
61 | 142 | 0 | 13.6133 | 3.6 | 7.6 | 100 | 9.63
61 | 143 | 0 | 13.6133 | 3.6 | 7.7 | 100 | 9.645
61 | 144 | 0 | 13.6133 | 3.6 | 7.8 | 100 | 9.66
61 | 145 | 0 | 13.6133 | 3.6 | 7.9 | 100 | 9.675
61 | 146 | 0 | 13.6133 | 3.6 | 8 | 100 | 9.69
61 | 147 | 0 | 13.6133 | 3.6 | 8.1 | 100 | 9.705
61 | 148 | 0 | 13.6133 | 3.6 | 8.2 | 100 | 9.72
61 | 149 | 0 | 13.6133 | 3.6 | 8.3 | 100 | 9.735
61 | 150 | 0 | 13.6133 | 3.6 | 8.4 | 100 | 9.75
62 | 45 | 0 | 13.6267 | 3.6 | 8.5 | 100 | 9.765
62 | 46 | 0 | 13.6267 | 3.6 | 8.6 | 100 | 9.78
62 | 47 | 0 | 13.6267 | 3.6 | 8.7 | 100 | 9.795
62 | 48 | 0 | 13.6267 | 3.6 | 8.8 | 100 | 9.81
62 | 49 | 0 | 13.6267 | 3.6 | 8.9 | 100 | 9.825
62 | 50 | 0 | 13.6267 | 3.6 | 9 | 100 | 9.84
62 | 51 | 0 | 13.6267 | 3.6 | 9.1 | 100 | 9.918
62 | 52 | 0 | 13.6267 | 3.6 | 9.2 | 100 | 9.996
62 | 53 | 0 | 13.6267 | 3.6 | 9.3 | 100 | 10.074
62 | 54 | 0 | 13.6267 | 3.6 | 9.4 | 100 | 10.152
62 | 55 | 0 | 13.6267 | 3.6 | 9.5 | 100 | 10.23
62 | 56 | 0 | 13.6267 | 3.6 | 9.6 | 100 | 10.308
62 | 57 | 0 | 13.6267 | 3.6 | 9.7 | 100 | 10.386
62 | 58 | 0 | 13.6267 | 3.6 | 9.8 | 100 | 10.464
62 | 59 | 0 | 13.6267 | 3.6 | 9.9 | 100 | 10.542
62 | 60 | 0 | 13.6267 | 3.6 | 10 | 100 | 10.62
62 | 61 | 0 | 13.6267 | 3.7 | 3 | 100 | 6.71
62 | 62 | 0 | 13.6267 | 3.7 | 3.1 | 100 | 6.7845
62 | 63 | 0 | 13.6267 | 3.7 | 3.2 | 100 | 6.859
62 | 64 | 0 | 13.6267 | 3.7 | 3.3 | 100 | 6.9335
62 | 65 | 0 | 13.6267 | 3.7 | 3.4 | 100 | 7.008
62 | 66 | 0 | 13.6267 | 3.7 | 3.5 | 100 | 7.0825
62 | 67 | 0 | 13.6267 | 3.7 | 3.6 | 100 | 7.157
62 | 68 | 0 | 13.6267 | 3.7 | 3.7 | 100 | 7.2315
62 | 69 | 0 | 13.6267 | 3.7 | 3.8 | 100 | 7.306
62 | 70 | 0 | 13.6267 | 3.7 | 3.9 | 100 | 7.3805
62 | 71 | 0 | 13.6267 | 3.7 | 4 | 100 | 7.455
62 | 72 | 0 | 13.6267 | 3.7 | 4.1 | 100 | 7.5295
62 | 73 | 0 | 13.6267 | 3.7 | 4.2 | 100 | 7.604
62 | 74 | 0 | 13.6267 | 3.7 | 4.3 | 100 | 7.6785
62 | 75 | 0 | 13.6267 | 3.7 | 4.4 | 100 | 7.753
62 | 76 | 0 | 13.6267 | 3.7 | 4.5 | 100 | 7.8275
62 | 77 | 0 | 13.6267 | 3.7 | 4.6 | 100 | 7.902
62 | 78 | 0 | 13.6267 | 3.7 | 4.7 | 100 | 7.9765
62 | 79 | 0 | 13.6267 | 3.7 | 4.8 | 100 | 8.051
62 | 80 | 0 | 13.6267 | 3.7 | 4.9 | 100 | 8.1255
62 | 81 | 0 | 13.6267 | 3.7 | 5 | 100 | 8.2
62 | 82 | 0 | 13.6267 | 3.7 | 5.1 | 100 | 8.2715
62 | 83 | 0 | 13.6267 | 3.7 | 5.2 | 100 | 8.343
62 | 84 | 0 | 13.6267 | 3.7 | 5.3 | 100 | 8.4145
62 | 85 | 0 | 13.6267 | 3.7 | 5.4 | 100 | 8.486
62 | 86 | 0 | 13.6267 | 3.7 | 5.5 | 100 | 8.5575
62 | 87 | 0 | 13.6267 | 3.7 | 5.6 | 100 | 8.629
62 | 88 | 0 | 13.6267 | 3.7 | 5.7 | 100 | 8.7005
62 | 89 | 0 | 13.6267 | 3.7 | 5.8 | 100 | 8.772
62 | 90 | 0 | 13.6267 | 3.7 | 5.9 | 100 | 8.8435
62 | 91 | 0 | 13.6267 | 3.7 | 6 | 100 | 8.915
62 | 92 | 0 | 13.6267 | 3.7 | 6.1 | 100 | 8.9865
62 | 93 | 0 | 13.6267 | 3.7 | 6.2 | 100 | 9.058
62 | 94 | 0 | 13.6267 | 3.7 | 6.3 | 100 | 9.1295
62 | 95 | 0 | 13.6267 | 3.7 | 6.4 | 100 | 9.201
62 | 96 | 0 | 13.6267 | 3.7 | 6.5 | 100 | 9.2725
62 | 97 | 0 | 13.6267 | 3.7 | 6.6 | 100 | 9.344
62 | 98 | 0 | 13.6267 | 3.7 | 6.7 | 100 | 9.4155
62 | 99 | 0 | 13.6267 | 3.7 | 6.8 | 100 | 9.487
62 | 100 | 0 | 13.6267 | 3.7 | 6.9 | 100 | 9.5585
62 | 101 | 0 | 13.6267 | 3.7 | 7 | 100 | 9.63
62 | 102 | 0 | 13.6267 | 3.7 | 7.1 | 100 | 9.6425
62 | 103 | 0 | 13.6267 | 3.7 | 7.2 | 100 | 9.655
62 | 104 | 0 | 13.6267 | 3.7 | 7.3 | 100 | 9.6675
62 | 105 | 0 | 13.6267 | 3.7 | 7.4 | 100 | 9.68
62 | 106 | 0 | 13.6267 | 3.7 | 7.5 | 100 | 9.6925
62 | 107 | 0 | 13.6267 | 3.7 | 7.6 | 100 | 9.705
62 | 108 | 0 | 13.6267 | 3.7 | 7.7 | 100 | 9.7175
62 | 109 | 0 | 13.6267 | 3.7 | 7.8 | 100 | 9.73
62 | 110 | 0 | 13.6267 | 3.7 | 7.9 | 100 | 9.7425
62 | 111 | 0 | 13.6267 | 3.7 | 8 | 100 | 9.755
62 | 112 | 0 | 13.6267 | 3.7 | 8.1 | 100 | 9.7675
62 | 113 | 0 | 13.6267 | 3.7 | 8.2 | 100 | 9.78
62 | 114 | 0 | 13.6267 | 3.7 | 8.3 | 100 | 9.7925
62 | 115 | 0 | 13.6267 | 3.7 | 8.4 | 100 | 9.805
62 | 116 | 0 | 13.6267 | 3.7 | 8.5 | 100 | 9.8175
62 | 117 | 0 | 13.6267 | 3.7 | 8.6 | 100 | 9.83
62 | 118 | 0 | 13.6267 | 3.7 | 8.7 | 100 | 9.8425
62 | 119 | 0 | 13.6267 | 3.7 | 8.8 | 100 | 9.855
62 | 120 | 0 | 13.6267 | 3.7 | 8.9 | 100 | 9.8675
62 | 121 | 0 | 13.6267 | 3.7 | 9 | 100 | 9.88
62 | 122 | 0 | 13.6267 | 3.7 | 9.1 | 100 | 9.956
62 | 123 | 0 | 13.6267 | 3.7 | 9.2 | 100 | 10.032
62 | 124 | 0 | 13.6267 | 3.7 | 9.3 | 100 | 10.108
62 | 125 | 0 | 13.6267 | 3.7 | 9.4 | 100 | 10.184
62 | 126 | 0 | 13.6267 | 3.7 | 9.5 | 100 | 10.26
62 | 127 | 0 | 13.6267 | 3.7 | 9.6 | 100 | 10.336
62 | 128 | 0 | 13.6267 | 3.7 | 9.7 | 100 | 10.412
62 | 129 | 0 | 13.6267 | 3.7 | 9.8 | 100 | 10.488
62 | 130 | 0 | 13.6267 | 3.7 | 9.9 | 100 | 10.564
62 | 131 | 0 | 13.6267 | 3.7 | 10 | 100 | 10.64
62 | 132 | 0 | 13.6267 | 3.8 | 3 | 100 | 6.74
62 | 133 | 0 | 13.6267 | 3.8 | 3.1 | 100 | 6.813
62 | 134 | 0 | 13.6267 | 3.8 | 3.2 | 100 | 6.886
62 | 135 | 0 | 13.6267 | 3.8 | 3.3 | 100 | 6.959
62 | 136 | 0 | 13.6267 | 3.8 | 3.4 | 100 | 7.032
62 | 137 | 0 | 13.6267 | 3.8 | 3.5 | 100 | 7.105
62 | 138 | 0 | 13.6267 | 3.8 | 3.6 | 100 | 7.178
62 | 139 | 0 | 13.6267 | 3.8 | 3.7 | 100 | 7.251
62 | 140 | 0 | 13.6267 | 3.8 | 3.8 | 100 | 7.324
62 | 141 | 0 | 13.6267 | 3.8 | 3.9 | 100 | 7.397
62 | 142 | 0 | 13.6267 | 3.8 | 4 | 100 | 7.47
62 | 143 | 0 | 13.6267 | 3.8 | 4.1 | 100 | 7.543
62 | 144 | 0 | 13.6267 | 3.8 | 4.2 | 100 | 7.616
62 | 145 | 0 | 13.6267 | 3.8 | 4.3 | 100 | 7.689
62 | 146 | 0 | 13.6267 | 3.8 | 4.4 | 100 | 7.762
62 | 147 | 0 | 13.6267 | 3.8 | 4.5 | 100 | 7.835
62 | 148 | 0 | 13.6267 | 3.8 | 4.6 | 100 | 7.908
62 | 149 | 0 | 13.6267 | 3.8 | 4.7 | 100 | 7.981
62 | 150 | 0 | 13.6267 | 3.8 | 4.8 | 100 | 8.054
63 | 45 | 0 | 13.64 | 3.8 | 4.9 | 100 | 8.127
63 | 46 | 0 | 13.64 | 3.8 | 5 | 100 | 8.2
63 | 47 | 0 | 13.64 | 3.8 | 5.1 | 100 | 8.276
63 | 48 | 0 | 13.64 | 3.8 | 5.2 | 100 | 8.352
63 | 49 | 0 | 13.64 | 3.8 | 5.3 | 100 | 8.428
63 | 50 | 0 | 13.64 | 3.8 | 5.4 | 100 | 8.504
63 | 51 | 0 | 13.64 | 3.8 | 5.5 | 100 | 8.58
63 | 52 | 0 | 13.64 | 3.8 | 5.6 | 100 | 8.656
63 | 53 | 0 | 13.64 | 3.8 | 5.7 | 100 | 8.732
63 | 54 | 0 | 13.64 | 3.8 | 5.8 | 100 | 8.808
63 | 55 | 0 | 13.64 | 3.8 | 5.9 | 100 | 8.884
63 | 56 | 0 | 13.64 | 3.8 | 6 | 100 | 8.96
63 | 57 | 0 | 13.64 | 3.8 | 6.1 | 100 | 9.036
63 | 58 | 0 | 13.64 | 3.8 | 6.2 | 100 | 9.112
63 | 59 | 0 | 13.64 | 3.8 | 6.3 | 100 | 9.188
63 | 60 | 0 | 13.64 | 3.8 | 6.4 | 100 | 9.264
63 | 61 | 0 | 13.64 | 3.8 | 6.5 | 100 | 9.34
63 | 62 | 0 | 13.64 | 3.8 | 6.6 | 100 | 9.416
63 | 63 | 0 | 13.64 | 3.8 | 6.7 | 100 | 9.492
63 | 64 | 0 | 13.64 | 3.8 | 6.8 | 100 | 9.568
63 | 65 | 0 | 13.64 | 3.8 | 6.9 | 100 | 9.644
63 | 66 | 0 | 13.64 | 3.8 | 7 | 100 | 9.72
63 | 67 | 0 | 13.64 | 3.8 | 7.1 | 100 | 9.73
63 | 68 | 0 | 13.64 | 3.8 | 7.2 | 100 | 9.74
63 | 69 | 0 | 13.64 | 3.8 | 7.3 | 100 | 9.75
63 | 70 | 0 | 13.64 | 3.8 | 7.4 | 100 | 9.76
63 | 71 | 0 | 13.64 | 3.8 | 7.5 | 100 | 9.77
63 | 72 | 0 | 13.64 | 3.8 | 7.6 | 100 | 9.78
63 | 73 | 0 | 13.64 | 3.8 | 7.7 | 100 | 9.79
63 | 74 | 0 | 13.64 | 3.8 | 7.8 | 100 | 9.8
63 | 75 | 0 | 13.64 | 3.8 | 7.9 | 100 | 9.81
63 | 76 | 0 | 13.64 | 3.8 | 8 | 100 | 9.82
63 | 77 | 0 | 13.64 | 3.8 | 8.1 | 100 | 9.83
63 | 78 | 0 | 13.64 | 3.8 | 8.2 | 100 | 9.84
63 | 79 | 0 | 13.64 | 3.8 | 8.3 | 100 | 9.85
63 | 80 | 0 | 13.64 | 3.8 | 8.4 | 100 | 9.86
63 | 81 | 0 | 13.64 | 3.8 | 8.5 | 100 | 9.87
63 | 82 | 0 | 13.64 | 3.8 | 8.6 | 100 | 9.88
63 | 83 | 0 | 13.64 | 3.8 | 8.7 | 100 | 9.89
63 | 84 | 0 | 13.64 | 3.8 | 8.8 | 100 | 9.9
63 | 85 | 0 | 13.64 | 3.8 | 8.9 | 100 | 9.91
63 | 86 | 0 | 13.64 | 3.8 | 9 | 100 | 9.92
63 | 87 | 0 | 13.64 | 3.8 | 9.1 | 100 | 9.994
63 | 88 | 0 | 13.64 | 3.8 | 9.2 | 100 | 10.068
63 | 89 | 0 | 13.64 | 3.8 | 9.3 | 100 | 10.142
63 | 90 | 0 | 13.64 | 3.8 | 9.4 | 100 | 10.216
63 | 91 | 0 | 13.64 | 3.8 | 9.5 | 100 | 10.29
63 | 92 | 0 | 13.64 | 3.8 | 9.6 | 100 | 10.364
63 | 93 | 0 | 13.64 | 3.8 | 9.7 | 100 | 10.438
63 | 94 | 0 | 13.64 | 3.8 | 9.8 | 100 | 10.512
63 | 95 | 0 | 13.64 | 3.8 | 9.9 | 100 | 10.586
63 | 96 | 0 | 13.64 | 3.8 | 10 | 100 | 10.66
63 | 97 | 0 | 13.64 | 3.9 | 3 | 100 | 6.77
63 | 98 | 0 | 13.64 | 3.9 | 3.1 | 100 | 6.8415
63 | 99 | 0 | 13.64 | 3.9 | 3.2 | 100 | 6.913
63 | 100 | 0 | 13.64 | 3.9 | 3.3 | 100 | 6.9845
63 | 101 | 0 | 13.64 | 3.9 | 3.4 | 100 | 7.056
63 | 102 | 0 | 13.64 | 3.9 | 3.5 | 100 | 7.1275
63 | 103 | 0 | 13.64 | 3.9 | 3.6 | 100 | 7.199
63 | 104 | 0 | 13.64 | 3.9 | 3.7 | 100 | 7.2705
63 | 105 | 0 | 13.64 | 3.9 | 3.8 | 100 | 7.342
63 | 106 | 0 | 13.64 | 3.9 | 3.9 | 100 | 7.4135
63 | 107 | 0 | 13.64 | 3.9 | 4 | 100 | 7.485
63 | 108 | 0 | 13.64 | 3.9 | 4.1 | 100 | 7.5565
63 | 109 | 0 | 13.64 | 3.9 | 4.2 | 100 | 7.628
63 | 110 | 0 | 13.64 | 3.9 | 4.3 | 100 | 7.6995
63 | 111 | 0 | 13.64 | 3.9 | 4.4 | 100 | 7.771
63 | 112 | 0 | 13.64 | 3.9 | 4.5 | 100 | 7.8425
63 | 113 | 0 | 13.64 | 3.9 | 4.6 | 100 | 7.914
63 | 114 | 0 | 13.64 | 3.9 | 4.7 | 100 | 7.9855
63 | 115 | 0 | 13.64 | 3.9 | 4.8 | 100 | 8.057
63 | 116 | 0 | 13.64 | 3.9 | 4.9 | 100 | 8.1285
63 | 117 | 0 | 13.64 | 3.9 | 5 | 100 | 8.2
63 | 118 | 0 | 13.64 | 3.9 | 5.1 | 100 | 8.2805
63 | 119 | 0 | 13.64 | 3.9 | 5.2 | 100 | 8.361
63 | 120 | 0 | 13.64 | 3.9 | 5.3 | 100 | 8.4415
63 | 121 | 0 | 13.64 | 3.9 | 5.4 | 100 | 8.522
63 | 122 | 0 | 13.64 | 3.9 | 5.5 | 100 | 8.6025
63 | 123 | 0 | 13.64 | 3.9 | 5.6 | 100 | 8.683
63 | 124 | 0 | 13.64 | 3.9 | 5.7 | 100 | 8.7635
63 | 125 | 0 | 13.64 | 3.9 | 5.8 | 100 | 8.844
63 | 126 | 0 | 13.64 | 3.9 | 5.9 | 100 | 8.9245
63 | 127 | 0 | 13.64 | 3.9 | 6 | 100 | 9.005
63 | 128 | 0 | 13.64 | 3.9 | 6.1 | 100 | 9.0855
63 | 129 | 0 | 13.64 | 3.9 | 6.2 | 100 | 9.166
63 | 130 | 0 | 13.64 | 3.9 | 6.3 | 100 | 9.2465
63 | 131 | 0 | 13.64 | 3.9 | 6.4 | 100 | 9.327
63 | 132 | 0 | 13.64 | 3.9 | 6.5 | 100 | 9.4075
63 | 133 | 0 | 13.64 | 3.9 | 6.6 | 100 | 9.488
63 | 134 | 0 | 13.64 | 3.9 | 6.7 | 100 | 9.5685
63 | 135 | 0 | 13.64 | 3.9 | 6.8 | 100 | 9.649
63 | 136 | 0 | 13.64 | 3.9 | 6.9 | 100 | 9.7295
63 | 137 | 0 | 13.64 | 3.9 | 7 | 100 | 9.81
63 | 138 | 0 | 13.64 | 3.9 | 7.1 | 100 | 9.8175
63 | 139 | 0 | 13.64 | 3.9 | 7.2 | 100 | 9.825
63 | 140 | 0 | 13.64 | 3.9 | 7.3 | 100 | 9.8325
63 | 141 | 0 | 13.64 | 3.9 | 7.4 | 100 | 9.84
63 | 142 | 0 | 13.64 | 3.9 | 7.5 | 100 | 9.8475
63 | 143 | 0 | 13.64 | 3.9 | 7.6 | 100 | 9.855
63 | 144 | 0 | 13.64 | 3.9 | 7.7 | 100 | 9.8625
63 | 145 | 0 | 13.64 | 3.9 | 7.8 | 100 | 9.87
63 | 146 | 0 | 13.64 | 3.9 | 7.9 | 100 | 9.8775
63 | 147 | 0 | 13.64 | 3.9 | 8 | 100 | 9.885
63 | 148 | 0 | 13.64 | 3.9 | 8.1 | 100 | 9.8925
63 | 149 | 0 | 13.64 | 3.9 | 8.2 | 100 | 9.9
63 | 150 | 0 | 13.64 | 3.9 | 8.3 | 100 | 9.9075
64 | 45 | 0 | 13.6533 | 3.9 | 8.4 | 100 | 9.915
64 | 46 | 0 | 13.6533 | 3.9 | 8.5 | 100 | 9.9225
64 | 47 | 0 | 13.6533 | 3.9 | 8.6 | 100 | 9.93
64 | 48 | 0 | 13.6533 | 3.9 | 8.7 | 100 | 9.9375
64 | 49 | 0 | 13.6533 | 3.9 | 8.8 | 100 | 9.945
64 | 50 | 0 | 13.6533 | 3.9 | 8.9 | 100 | 9.9525
64 | 51 | 0 | 13.6533 | 3.9 | 9 | 100 | 9.96
64 | 52 | 0 | 13.6533 | 3.9 | 9.1 | 100 | 10.032
64 | 53 | 0 | 13.6533 | 3.9 | 9.2 | 100 | 10.104
64 | 54 | 0 | 13.6533 | 3.9 | 9.3 | 100 | 10.176
64 | 55 | 0 | 13.6533 | 3.9 | 9.4 | 100 | 10.248
64 | 56 | 0 | 13.6533 | 3.9 | 9.5 | 100 | 10.32
64 | 57 | 0 | 13.6533 | 3.9 | 9.6 | 100 | 10.392
64 | 58 | 0 | 13.6533 | 3.9 | 9.7 | 100 | 10.464
64 | 59 | 0 | 13.6533 | 3.9 | 9.8 | 100 | 10.536
64 | 60 | 0 | 13.6533 | 3.9 | 9.9 | 100 | 10.608
64 | 61 | 0 | 13.6533 | 3.9 | 10 | 100 | 10.68
64 | 62 | 0 | 13.6533 | 4 | 3 | 100 | 6.8
64 | 63 | 0 | 13.6533 | 4 | 3.1 | 100 | 6.87
64 | 64 | 0 | 13.6533 | 4 | 3.2 | 100 | 6.94
64 | 65 | 0 | 13.6533 | 4 | 3.3 | 100 | 7.01
64 | 66 | 0 | 13.6533 | 4 | 3.4 | 100 | 7.08
64 | 67 | 0 | 13.6533 | 4 | 3.5 | 100 | 7.15
64 | 68 | 0 | 13.6533 | 4 | 3.6 | 100 | 7.22
64 | 69 | 0 | 13.6533 | 4 | 3.7 | 100 | 7.29
64 | 70 | 0 | 13.6533 | 4 | 3.8 | 100 | 7.36
64 | 71 | 0 | 13.6533 | 4 | 3.9 | 100 | 7.43
64 | 72 | 0 | 13.6533 | 4 | 4 | 100 | 7.5
64 | 73 | 0 | 13.6533 | 4 | 4.1 | 100 | 7.57
64 | 74 | 0 | 13.6533 | 4 | 4.2 | 100 | 7.64
64 | 75 | 0 | 13.6533 | 4 | 4.3 | 100 | 7.71
64 | 76 | 0 | 13.6533 | 4 | 4.4 | 100 | 7.78
64 | 77 | 0 | 13.6533 | 4 | 4.5 | 100 | 7.85
64 | 78 | 0 | 13.6533 | 4 | 4.6 | 100 | 7.92
64 | 79 | 0 | 13.6533 | 4 | 4.7 | 100 | 7.99
64 | 80 | 0 | 13.6533 | 4 | 4.8 | 100 | 8.06
64 | 81 | 0 | 13.6533 | 4 | 4.9 | 100 | 8.13
64 | 82 | 0 | 13.6533 | 4 | 5 | 100 | 8.2
64 | 83 | 0 | 13.6533 | 4 | 5.1 | 100 | 8.285
64 | 84 | 0 | 13.6533 | 4 | 5.2 | 100 | 8.37
64 | 85 | 0 | 13.6533 | 4 | 5.3 | 100 | 8.455
64 | 86 | 0 | 13.6533 | 4 | 5.4 | 100 | 8.54
64 | 87 | 0 | 13.6533 | 4 | 5.5 | 100 | 8.625
64 | 88 | 0 | 13.6533 | 4 | 5.6 | 100 | 8.71
64 | 89 | 0 | 13.6533 | 4 | 5.7 | 100 | 8.795
64 | 90 | 0 | 13.6533 | 4 | 5.8 | 100 | 8.88
64 | 91 | 0 | 13.6533 | 4 | 5.9 | 100 | 8.965
64 | 92 | 0 | 13.6533 | 4 | 6 | 100 | 9.05
64 | 93 | 0 | 13.6533 | 4 | 6.1 | 100 | 9.135
64 | 94 | 0 | 13.6533 | 4 | 6.2 | 100 | 9.22
64 | 95 | 0 | 13.6533 | 4 | 6.3 | 100 | 9.305
64 | 96 | 0 | 13.6533 | 4 | 6.4 | 100 | 9.39
64 | 97 | 0 | 13.6533 | 4 | 6.5 | 100 | 9.475
64 | 98 | 0 | 13.6533 | 4 | 6.6 | 100 | 9.56
64 | 99 | 0 | 13.6533 | 4 | 6.7 | 100 | 9.645
64 | 100 | 0 | 13.6533 | 4 | 6.8 | 100 | 9.73
64 | 101 | 0 | 13.6533 | 4 | 6.9 | 100 | 9.815
64 | 102 | 0 | 13.6533 | 4 | 7 | 100 | 9.9
64 | 103 | 0 | 13.6533 | 4 | 7.1 | 100 | 9.905
64 | 104 | 0 | 13.6533 | 4 | 7.2 | 100 | 9.91
64 | 105 | 0 | 13.6533 | 4 | 7.3 | 100 | 9.915
64 | 106 | 0 | 13.6533 | 4 | 7.4 | 100 | 9.92
64 | 107 | 0 | 13.6533 | 4 | 7.5 | 100 | 9.925
64 | 108 | 0 | 13.6533 | 4 | 7.6 | 100 | 9.93
64 | 109 | 0 | 13.6533 | 4 | 7.7 | 100 | 9.935
64 | 110 | 0 | 13.6533 | 4 | 7.8 | 100 | 9.94
64 | 111 | 0 | 13.6533 | 4 | 7.9 | 100 | 9.945
64 | 112 | 0 | 13.6533 | 4 | 8 | 100 | 9.95
64 | 113 | 0 | 13.6533 | 4 | 8.1 | 100 | 9.955
64 | 114 | 0 | 13.6533 | 4 | 8.2 | 100 | 9.96
64 | 115 | 0 | 13.6533 | 4 | 8.3 | 100 | 9.965
64 | 116 | 0 | 13.6533 | 4 | 8.4 | 100 | 9.97
64 | 117 | 0 | 13.6533 | 4 | 8.5 | 100 | 9.975
64 | 118 | 0 | 13.6533 | 4 | 8.6 | 100 | 9.98
64 | 119 | 0 | 13.6533 | 4 | 8.7 | 100 | 9.985
64 | 120 | 0 | 13.6533 | 4 | 8.8 | 100 | 9.99
64 | 121 | 0 | 13.6533 | 4 | 8.9 | 100 | 9.995
64 | 122 | 0 | 13.6533 | 4 | 9 | 100 | 10
64 | 123 | 0 | 13.6533 | 4 | 9.1 | 100 | 10.07
64 | 124 | 0 | 13.6533 | 4 | 9.2 | 100 | 10.14
64 | 125 | 0 | 13.6533 | 4 | 9.3 | 100 | 10.21
64 | 126 | 0 | 13.6533 | 4 | 9.4 | 100 | 10.28
64 | 127 | 0 | 13.6533 | 4 | 9.5 | 100 | 10.35
64 | 128 | 0 | 13.6533 | 4 | 9.6 | 100 | 10.42
64 | 129 | 0 | 13.6533 | 4 | 9.7 | 100 | 10.49
64 | 130 | 0 | 13.6533 | 4 | 9.8 | 100 | 10.56
64 | 131 | 0 | 13.6533 | 4 | 9.9 | 100 | 10.63
64 | 132 | 0 | 13.6533 | 4 | 10 | 100 | 10.7
64 | 133 | 0 | 13.6533 | 4.1 | 3 | 100 | 6.81
64 | 134 | 0 | 13.6533 | 4.1 | 3.1 | 100 | 6.88
64 | 135 | 0 | 13.6533 | 4.1 | 3.2 | 100 | 6.95
64 | 136 | 0 | 13.6533 | 4.1 | 3.3 | 100 | 7.02
64 | 137 | 0 | 13.6533 | 4.1 | 3.4 | 100 | 7.09
64 | 138 | 0 | 13.6533 | 4.1 | 3.5 | 100 | 7.16
64 | 139 | 0 | 13.6533 | 4.1 | 3.6 | 100 | 7.23
64 | 140 | 0 | 13.6533 | 4.1 | 3.7 | 100 | 7.3
64 | 141 | 0 | 13.6533 | 4.1 | 3.8 | 100 | 7.37
64 | 142 | 0 | 13.6533 | 4.1 | 3.9 | 100 | 7.44
64 | 143 | 0 | 13.6533 | 4.1 | 4 | 100 | 7.51
64 | 144 | 0 | 13.6533 | 4.1 | 4.1 | 100 | 7.58
64 | 145 | 0 | 13.6533 | 4.1 | 4.2 | 100 | 7.65
64 | 146 | 0 | 13.6533 | 4.1 | 4.3 | 100 | 7.72
64 | 147 | 0 | 13.6533 | 4.1 | 4.4 | 100 | 7.79
64 | 148 | 0 | 13.6533 | 4.1 | 4.5 | 100 | 7.86
64 | 149 | 0 | 13.6533 | 4.1 | 4.6 | 100 | 7.93
64 | 150 | 0 | 13.6533 | 4.1 | 4.7 | 100 | 8
65 | 45 | 0 | 13.6667 | 4.1 | 4.8 | 100 | 8.07
65 | 46 | 0 | 13.6667 | 4.1 | 4.9 | 100 | 8.14
65 | 47 | 0 | 13.6667 | 4.1 | 5 | 100 | 8.21
65 | 48 | 0 | 13.6667 | 4.1 | 5.1 | 100 | 8.2955
65 | 49 | 0 | 13.6667 | 4.1 | 5.2 | 100 | 8.381
65 | 50 | 0 | 13.6667 | 4.1 | 5.3 | 100 | 8.4665
65 | 51 | 0 | 13.6667 | 4.1 | 5.4 | 100 | 8.552
65 | 52 | 0 | 13.6667 | 4.1 | 5.5 | 100 | 8.6375
65 | 53 | 0 | 13.6667 | 4.1 | 5.6 | 100 | 8.723
65 | 54 | 0 | 13.6667 | 4.1 | 5.7 | 100 | 8.8085
65 | 55 | 0 | 13.6667 | 4.1 | 5.8 | 100 | 8.894
65 | 56 | 0 | 13.6667 | 4.1 | 5.9 | 100 | 8.9795
65 | 57 | 0 | 13.6667 | 4.1 | 6 | 100 | 9.065
65 | 58 | 0 | 13.6667 | 4.1 | 6.1 | 100 | 9.1505
65 | 59 | 0 | 13.6667 | 4.1 | 6.2 | 100 | 9.236
65 | 60 | 0 | 13.6667 | 4.1 | 6.3 | 100 | 9.3215
65 | 61 | 0 | 13.6667 | 4.1 | 6.4 | 100 | 9.407
65 | 62 | 0 | 13.6667 | 4.1 | 6.5 | 100 | 9.4925
65 | 63 | 0 | 13.6667 | 4.1 | 6.6 | 100 | 9.578
65 | 64 | 0 | 13.6667 | 4.1 | 6.7 | 100 | 9.6635
65 | 65 | 0 | 13.6667 | 4.1 | 6.8 | 100 | 9.749
65 | 66 | 0 | 13.6667 | 4.1 | 6.9 | 100 | 9.8345
65 | 67 | 0 | 13.6667 | 4.1 | 7 | 100 | 9.92
65 | 68 | 0 | 13.6667 | 4.1 | 7.1 | 100 | 9.9255
65 | 69 | 0 | 13.6667 | 4.1 | 7.2 | 100 | 9.931
65 | 70 | 0 | 13.6667 | 4.1 | 7.3 | 100 | 9.9365
65 | 71 | 0 | 13.6667 | 4.1 | 7.4 | 100 | 9.942
65 | 72 | 0 | 13.6667 | 4.1 | 7.5 | 100 | 9.9475
65 | 73 | 0 | 13.6667 | 4.1 | 7.6 | 100 | 9.953
65 | 74 | 0 | 13.6667 | 4.1 | 7.7 | 100 | 9.9585
65 | 75 | 0 | 13.6667 | 4.1 | 7.8 | 100 | 9.964
65 | 76 | 0 | 13.6667 | 4.1 | 7.9 | 100 | 9.9695
65 | 77 | 0 | 13.6667 | 4.1 | 8 | 100 | 9.975
65 | 78 | 0 | 13.6667 | 4.1 | 8.1 | 100 | 9.9805
65 | 79 | 0 | 13.6667 | 4.1 | 8.2 | 100 | 9.986
65 | 80 | 0 | 13.6667 | 4.1 | 8.3 | 100 | 9.9915
65 | 81 | 0 | 13.6667 | 4.1 | 8.4 | 100 | 9.997
65 | 82 | 0 | 13.6667 | 4.1 | 8.5 | 100 | 10.0025
65 | 83 | 0 | 13.6667 | 4.1 | 8.6 | 100 | 10.008
65 | 84 | 0 | 13.6667 | 4.1 | 8.7 | 100 | 10.0135
65 | 85 | 0 | 13.6667 | 4.1 | 8.8 | 100 | 10.019
65 | 86 | 0 | 13.6667 | 4.1 | 8.9 | 100 | 10.0245
65 | 87 | 0 | 13.6667 | 4.1 | 9 | 100 | 10.03
65 | 88 | 0 | 13.6667 | 4.1 | 9.1 | 100 | 10.099
65 | 89 | 0 | 13.6667 | 4.1 | 9.2 | 100 | 10.168
65 | 90 | 0 | 13.6667 | 4.1 | 9.3 | 100 | 10.237
65 | 91 | 0 | 13.6667 | 4.1 | 9.4 | 100 | 10.306
65 | 92 | 0 | 13.6667 | 4.1 | 9.5 | 100 | 10.375
65 | 93 | 0 | 13.6667 | 4.1 | 9.6 | 100 | 10.444
65 | 94 | 0 | 13.6667 | 4.1 | 9.7 | 100 | 10.513
65 | 95 | 0 | 13.6667 | 4.1 | 9.8 | 100 | 10.582
65 | 96 | 0 | 13.6667 | 4.1 | 9.9 | 100 | 10.651
65 | 97 | 0 | 13.6667 | 4.1 | 10 | 100 | 10.72
65 | 98 | 0 | 13.6667 | 4.2 | 3 | 100 | 6.82
65 | 99 | 0 | 13.6667 | 4.2 | 3.1 | 100 | 6.89
65 | 100 | 0 | 13.6667 | 4.2 | 3.2 | 100 | 6.96
65 | 101 | 0 | 13.6667 | 4.2 | 3.3 | 100 | 7.03
65 | 102 | 0 | 13.6667 | 4.2 | 3.4 | 100 | 7.1
65 | 103 | 0 | 13.6667 | 4.2 | 3.5 | 100 | 7.17
65 | 104 | 0 | 13.6667 | 4.2 | 3.6 | 100 | 7.24
65 | 105 | 0 | 13.6667 | 4.2 | 3.7 | 100 | 7.31
65 | 106 | 0 | 13.6667 | 4.2 | 3.8 | 100 | 7.38
65 | 107 | 0 | 13.6667 | 4.2 | 3.9 | 100 | 7.45
65 | 108 | 0 | 13.6667 | 4.2 | 4 | 100 | 7.52
65 | 109 | 0 | 13.6667 | 4.2 | 4.1 | 100 | 7.59
65 | 110 | 0 | 13.6667 | 4.2 | 4.2 | 100 | 7.66
65 | 111 | 0 | 13.6667 | 4.2 | 4.3 | 100 | 7.73
65 | 112 | 0 | 13.6667 | 4.2 | 4.4 | 100 | 7.8
65 | 113 | 0 | 13.6667 | 4.2 | 4.5 | 100 | 7.87
65 | 114 | 0 | 13.6667 | 4.2 | 4.6 | 100 | 7.94
65 | 115 | 0 | 13.6667 | 4.2 | 4.7 | 100 | 8.01
65 | 116 | 0 | 13.6667 | 4.2 | 4.8 | 100 | 8.08
65 | 117 | 0 | 13.6667 | 4.2 | 4.9 | 100 | 8.15
65 | 118 | 0 | 13.6667 | 4.2 | 5 | 100 | 8.22
65 | 119 | 0 | 13.6667 | 4.2 | 5.1 | 100 | 8.306
65 | 120 | 0 | 13.6667 | 4.2 | 5.2 | 100 | 8.392
65 | 121 | 0 | 13.6667 | 4.2 | 5.3 | 100 | 8.478
65 | 122 | 0 | 13.6667 | 4.2 | 5.4 | 100 | 8.564
65 | 123 | 0 | 13.6667 | 4.2 | 5.5 | 100 | 8.65
65 | 124 | 0 | 13.6667 | 4.2 | 5.6 | 100 | 8.736
65 | 125 | 0 | 13.6667 | 4.2 | 5.7 | 100 | 8.822
65 | 126 | 0 | 13.6667 | 4.2 | 5.8 | 100 | 8.908
65 | 127 | 0 | 13.6667 | 4.2 | 5.9 | 100 | 8.994
65 | 128 | 0 | 13.6667 | 4.2 | 6 | 100 | 9.08
65 | 129 | 0 | 13.6667 | 4.2 | 6.1 | 100 | 9.166
65 | 130 | 0 | 13.6667 | 4.2 | 6.2 | 100 | 9.252
65 | 131 | 0 | 13.6667 | 4.2 | 6.3 | 100 | 9.338
65 | 132 | 0 | 13.6667 | 4.2 | 6.4 | 100 | 9.424
65 | 133 | 0 | 13.6667 | 4.2 | 6.5 | 100 | 9.51
65 | 134 | 0 | 13.6667 | 4.2 | 6.6 | 100 | 9.596
65 | 135 | 0 | 13.6667 | 4.2 | 6.7 | 100 | 9.682
65 | 136 | 0 | 13.6667 | 4.2 | 6.8 | 100 | 9.768
65 | 137 | 0 | 13.6667 | 4.2 | 6.9 | 100 | 9.854
65 | 138 | 0 | 13.6667 | 4.2 | 7 | 100 | 9.94
65 | 139 | 0 | 13.6667 | 4.2 | 7.1 | 100 | 9.946
65 | 140 | 0 | 13.6667 | 4.2 | 7.2 | 100 | 9.952
65 | 141 | 0 | 13.6667 | 4.2 | 7.3 | 100 | 9.958
65 | 142 | 0 | 13.6667 | 4.2 | 7.4 | 100 | 9.964
65 | 143 | 0 | 13.6667 | 4.2 | 7.5 | 100 | 9.97
65 | 144 | 0 | 13.6667 | 4.2 | 7.6 | 100 | 9.976
65 | 145 | 0 | 13.6667 | 4.2 | 7.7 | 100 | 9.982
65 | 146 | 0 | 13.6667 | 4.2 | 7.8 | 100 | 9.988
65 | 147 | 0 | 13.6667 | 4.2 | 7.9 | 100 | 9.994
65 | 148 | 0 | 13.6667 | 4.2 | 8 | 100 | 10
65 | 149 | 0 | 13.6667 | 4.2 | 8.1 | 100 | 10.006
65 | 150 | 0 | 13.6667 | 4.2 | 8.2 | 100 | 10.012
66 | 45 | 0 | 13.68 | 4.2 | 8.3 | 100 | 10.018
66 | 46 | 0 | 13.68 | 4.2 | 8.4 | 100 | 10.024
66 | 47 | 0 | 13.68 | 4.2 | 8.5 | 100 | 10.03
66 | 48 | 0 | 13.68 | 4.2 | 8.6 | 100 | 10.036
66 | 49 | 0 | 13.68 | 4.2 | 8.7 | 100 | 10.042
66 | 50 | 0 | 13.68 | 4.2 | 8.8 | 100 | 10.048
66 | 51 | 0 | 13.68 | 4.2 | 8.9 | 100 | 10.054
66 | 52 | 0 | 13.68 | 4.2 | 9 | 100 | 10.06
66 | 53 | 0 | 13.68 | 4.2 | 9.1 | 100 | 10.128
66 | 54 | 0 | 13.68 | 4.2 | 9.2 | 100 | 10.196
66 | 55 | 0 | 13.68 | 4.2 | 9.3 | 100 | 10.264
66 | 56 | 0 | 13.68 | 4.2 | 9.4 | 100 | 10.332
66 | 57 | 0 | 13.68 | 4.2 | 9.5 | 100 | 10.4
66 | 58 | 0 | 13.68 | 4.2 | 9.6 | 100 | 10.468
66 | 59 | 0 | 13.68 | 4.2 | 9.7 | 100 | 10.536
66 | 60 | 0 | 13.68 | 4.2 | 9.8 | 100 | 10.604
66 | 61 | 0 | 13.68 | 4.2 | 9.9 | 100 | 10.672
66 | 62 | 0 | 13.68 | 4.2 | 10 | 100 | 10.74
66 | 63 | 0 | 13.68 | 4.3 | 3 | 100 | 6.83
66 | 64 | 0 | 13.68 | 4.3 | 3.1 | 100 | 6.9
66 | 65 | 0 | 13.68 | 4.3 | 3.2 | 100 | 6.97
66 | 66 | 0 | 13.68 | 4.3 | 3.3 | 100 | 7.04
66 | 67 | 0 | 13.68 | 4.3 | 3.4 | 100 | 7.11
66 | 68 | 0 | 13.68 | 4.3 | 3.5 | 100 | 7.18
66 | 69 | 0 | 13.68 | 4.3 | 3.6 | 100 | 7.25
66 | 70 | 0 | 13.68 | 4.3 | 3.7 | 100 | 7.32
66 | 71 | 0 | 13.68 | 4.3 | 3.8 | 100 | 7.39
66 | 72 | 0 | 13.68 | 4.3 | 3.9 | 100 | 7.46
66 | 73 | 0 | 13.68 | 4.3 | 4 | 100 | 7.53
66 | 74 | 0 | 13.68 | 4.3 | 4.1 | 100 | 7.6
66 | 75 | 0 | 13.68 | 4.3 | 4.2 | 100 | 7.67
66 | 76 | 0 | 13.68 | 4.3 | 4.3 | 100 | 7.74
66 | 77 | 0 | 13.68 | 4.3 | 4.4 | 100 | 7.81
66 | 78 | 0 | 13.68 | 4.3 | 4.5 | 100 | 7.88
66 | 79 | 0 | 13.68 | 4.3 | 4.6 | 100 | 7.95
66 | 80 | 0 | 13.68 | 4.3 | 4.7 | 100 | 8.02
66 | 81 | 0 | 13.68 | 4.3 | 4.8 | 100 | 8.09
66 | 82 | 0 | 13.68 | 4.3 | 4.9 | 100 | 8.16
66 | 83 | 0 | 13.68 | 4.3 | 5 | 100 | 8.23
66 | 84 | 0 | 13.68 | 4.3 | 5.1 | 100 | 8.3165
66 | 85 | 0 | 13.68 | 4.3 | 5.2 | 100 | 8.403
66 | 86 | 0 | 13.68 | 4.3 | 5.3 | 100 | 8.4895
66 | 87 | 0 | 13.68 | 4.3 | 5.4 | 100 | 8.576
66 | 88 | 0 | 13.68 | 4.3 | 5.5 | 100 | 8.6625
66 | 89 | 0 | 13.68 | 4.3 | 5.6 | 100 | 8.749
66 | 90 | 0 | 13.68 | 4.3 | 5.7 | 100 | 8.8355
66 | 91 | 0 | 13.68 | 4.3 | 5.8 | 100 | 8.922
66 | 92 | 0 | 13.68 | 4.3 | 5.9 | 100 | 9.0085
66 | 93 | 0 | 13.68 | 4.3 | 6 | 100 | 9.095
66 | 94 | 0 | 13.68 | 4.3 | 6.1 | 100 | 9.1815
66 | 95 | 0 | 13.68 | 4.3 | 6.2 | 100 | 9.268
66 | 96 | 0 | 13.68 | 4.3 | 6.3 | 100 | 9.3545
66 | 97 | 0 | 13.68 | 4.3 | 6.4 | 100 | 9.441
66 | 98 | 0 | 13.68 | 4.3 | 6.5 | 100 | 9.5275
66 | 99 | 0 | 13.68 | 4.3 | 6.6 | 100 | 9.614
66 | 100 | 0 | 13.68 | 4.3 | 6.7 | 100 | 9.7005
66 | 101 | 0 | 13.68 | 4.3 | 6.8 | 100 | 9.787
66 | 102 | 0 | 13.68 | 4.3 | 6.9 | 100 | 9.8735
66 | 103 | 0 | 13.68 | 4.3 | 7 | 100 | 9.96
66 | 104 | 0 | 13.68 | 4.3 | 7.1 | 100 | 9.9665
66 | 105 | 0 | 13.68 | 4.3 | 7.2 | 100 | 9.973
66 | 106 | 0 | 13.68 | 4.3 | 7.3 | 100 | 9.9795
66 | 107 | 0 | 13.68 | 4.3 | 7.4 | 100 | 9.986
66 | 108 | 0 | 13.68 | 4.3 | 7.5 | 100 | 9.9925
66 | 109 | 0 | 13.68 | 4.3 | 7.6 | 100 | 9.999
66 | 110 | 0 | 13.68 | 4.3 | 7.7 | 100 | 10.0055
66 | 111 | 0 | 13.68 | 4.3 | 7.8 | 100 | 10.012
66 | 112 | 0 | 13.68 | 4.3 | 7.9 | 100 | 10.0185
66 | 113 | 0 | 13.68 | 4.3 | 8 | 100 | 10.025
66 | 114 | 0 | 13.68 | 4.3 | 8.1 | 100 | 10.0315
66 | 115 | 0 | 13.68 | 4.3 | 8.2 | 100 | 10.038
66 | 116 | 0 | 13.68 | 4.3 | 8.3 | 100 | 10.0445
66 | 117 | 0 | 13.68 | 4.3 | 8.4 | 100 | 10.051
66 | 118 | 0 | 13.68 | 4.3 | 8.5 | 100 | 10.0575
66 | 119 | 0 | 13.68 | 4.3 | 8.6 | 100 | 10.064
66 | 120 | 0 | 13.68 | 4.3 | 8.7 | 100 | 10.0705
66 | 121 | 0 | 13.68 | 4.3 | 8.8 | 100 | 10.077
66 | 122 | 0 | 13.68 | 4.3 | 8.9 | 100 | 10.0835
66 | 123 | 0 | 13.68 | 4.3 | 9 | 100 | 10.09
66 | 124 | 0 | 13.68 | 4.3 | 9.1 | 100 | 10.157
66 | 125 | 0 | 13.68 | 4.3 | 9.2 | 100 | 10.224
66 | 126 | 0 | 13.68 | 4.3 | 9.3 | 100 | 10.291
66 | 127 | 0 | 13.68 | 4.3 | 9.4 | 100 | 10.358
66 | 128 | 0 | 13.68 | 4.3 | 9.5 | 100 | 10.425
66 | 129 | 0 | 13.68 | 4.3 | 9.6 | 100 | 10.492
66 | 130 | 0 | 13.68 | 4.3 | 9.7 | 100 | 10.559
66 | 131 | 0 | 13.68 | 4.3 | 9.8 | 100 | 10.626
66 | 132 | 0 | 13.68 | 4.3 | 9.9 | 100 | 10.693
66 | 133 | 0 | 13.68 | 4.3 | 10 | 100 | 10.76
66 | 134 | 0 | 13.68 | 4.4 | 3 | 100 | 6.84
66 | 135 | 0 | 13.68 | 4.4 | 3.1 | 100 | 6.91
66 | 136 | 0 | 13.68 | 4.4 | 3.2 | 100 | 6.98
66 | 137 | 0 | 13.68 | 4.4 | 3.3 | 100 | 7.05
66 | 138 | 0 | 13.68 | 4.4 | 3.4 | 100 | 7.12
66 | 139 | 0 | 13.68 | 4.4 | 3.5 | 100 | 7.19
66 | 140 | 0 | 13.68 | 4.4 | 3.6 | 100 | 7.26
66 | 141 | 0 | 13.68 | 4.4 | 3.7 | 100 | 7.33
66 | 142 | 0 | 13.68 | 4.4 | 3.8 | 100 | 7.4
66 | 143 | 0 | 13.68 | 4.4 | 3.9 | 100 | 7.47
66 | 144 | 0 | 13.68 | 4.4 | 4 | 100 | 7.54
66 | 145 | 0 | 13.68 | 4.4 | 4.1 | 100 | 7.61
66 | 146 | 0 | 13.68 | 4.4 | 4.2 | 100 | 7.68
66 | 147 | 0 | 13.68 | 4.4 | 4.3 | 100 | 7.75
66 | 148 | 0 | 13.68 | 4.4 | 4.4 | 100 | 7.82
66 | 149 | 0 | 13.68 | 4.4 | 4.5 | 100 | 7.89
66 | 150 | 0 | 13.68 | 4.4 | 4.6 | 100 | 7.96
67 | 45 | 0 | 13.6933 | 4.4 | 4.7 | 100 | 8.03
67 | 46 | 0 | 13.6933 | 4.4 | 4.8 | 100 | 8.1
67 | 47 | 0 | 13.6933 | 4.4 | 4.9 | 100 | 8.17
67 | 48 | 0 | 13.6933 | 4.4 | 5 | 100 | 8.24
67 | 49 | 0 | 13.6933 | 4.4 | 5.1 | 100 | 8.327
67 | 50 | 0 | 13.6933 | 4.4 | 5.2 | 100 | 8.414
67 | 51 | 0 | 13.6933 | 4.4 | 5.3 | 100 | 8.501
67 | 52 | 0 | 13.6933 | 4.4 | 5.4 | 100 | 8.588
67 | 53 | 0 | 13.6933 | 4.4 | 5.5 | 100 | 8.675
67 | 54 | 0 | 13.6933 | 4.4 | 5.6 | 100 | 8.762
67 | 55 | 0 | 13.6933 | 4.4 | 5.7 | 100 | 8.849
67 | 56 | 0 | 13.6933 | 4.4 | 5.8 | 100 | 8.936
67 | 57 | 0 | 13.6933 | 4.4 | 5.9 | 100 | 9.023
67 | 58 | 0 | 13.6933 | 4.4 | 6 | 100 | 9.11
67 | 59 | 0 | 13.6933 | 4.4 | 6.1 | 100 | 9.197
67 | 60 | 0 | 13.6933 | 4.4 | 6.2 | 100 | 9.284
67 | 61 | 0 | 13.6933 | 4.4 | 6.3 | 100 | 9.371
67 | 62 | 0 | 13.6933 | 4.4 | 6.4 | 100 | 9.458
67 | 63 | 0 | 13.6933 | 4.4 | 6.5 | 100 | 9.545
67 | 64 | 0 | 13.6933 | 4.4 | 6.6 | 100 | 9.632
67 | 65 | 0 | 13.6933 | 4.4 | 6.7 | 100 | 9.719
67 | 66 | 0 | 13.6933 | 4.4 | 6.8 | 100 | 9.806
67 | 67 | 0 | 13.6933 | 4.4 | 6.9 | 100 | 9.893
67 | 68 | 0 | 13.6933 | 4.4 | 7 | 100 | 9.98
67 | 69 | 0 | 13.6933 | 4.4 | 7.1 | 100 | 9.987
67 | 70 | 0 | 13.6933 | 4.4 | 7.2 | 100 | 9.994
67 | 71 | 0 | 13.6933 | 4.4 | 7.3 | 100 | 10.001
67 | 72 | 0 | 13.6933 | 4.4 | 7.4 | 100 | 10.008
67 | 73 | 0 | 13.6933 | 4.4 | 7.5 | 100 | 10.015
67 | 74 | 0 | 13.6933 | 4.4 | 7.6 | 100 | 10.022
67 | 75 | 0 | 13.6933 | 4.4 | 7.7 | 100 | 10.029
67 | 76 | 0 | 13.6933 | 4.4 | 7.8 | 100 | 10.036
67 | 77 | 0 | 13.6933 | 4.4 | 7.9 | 100 | 10.043
67 | 78 | 0 | 13.6933 | 4.4 | 8 | 100 | 10.05
67 | 79 | 0 | 13.6933 | 4.4 | 8.1 | 100 | 10.057
67 | 80 | 0 | 13.6933 | 4.4 | 8.2 | 100 | 10.064
67 | 81 | 0 | 13.6933 | 4.4 | 8.3 | 100 | 10.071
67 | 82 | 0 | 13.6933 | 4.4 | 8.4 | 100 | 10.078
67 | 83 | 0 | 13.6933 | 4.4 | 8.5 | 100 | 10.085
67 | 84 | 0 | 13.6933 | 4.4 | 8.6 | 100 | 10.092
67 | 85 | 0 | 13.6933 | 4.4 | 8.7 | 100 | 10.099
67 | 86 | 0 | 13.6933 | 4.4 | 8.8 | 100 | 10.106
67 | 87 | 0 | 13.6933 | 4.4 | 8.9 | 100 | 10.113
67 | 88 | 0 | 13.6933 | 4.4 | 9 | 100 | 10.12
67 | 89 | 0 | 13.6933 | 4.4 | 9.1 | 100 | 10.186
67 | 90 | 0 | 13.6933 | 4.4 | 9.2 | 100 | 10.252
67 | 91 | 0 | 13.6933 | 4.4 | 9.3 | 100 | 10.318
67 | 92 | 0 | 13.6933 | 4.4 | 9.4 | 100 | 10.384
67 | 93 | 0 | 13.6933 | 4.4 | 9.5 | 100 | 10.45
67 | 94 | 0 | 13.6933 | 4.4 | 9.6 | 100 | 10.516
67 | 95 | 0 | 13.6933 | 4.4 | 9.7 | 100 | 10.582
67 | 96 | 0 | 13.6933 | 4.4 | 9.8 | 100 | 10.648
67 | 97 | 0 | 13.6933 | 4.4 | 9.9 | 100 | 10.714
67 | 98 | 0 | 13.6933 | 4.4 | 10 | 100 | 10.78
67 | 99 | 0 | 13.6933 | 4.5 | 3 | 100 | 6.85
67 | 100 | 0 | 13.6933 | 4.5 | 3.1 | 100 | 6.92
67 | 101 | 0 | 13.6933 | 4.5 | 3.2 | 100 | 6.99
67 | 102 | 0 | 13.6933 | 4.5 | 3.3 | 100 | 7.06
67 | 103 | 0 | 13.6933 | 4.5 | 3.4 | 100 | 7.13
67 | 104 | 0 | 13.6933 | 4.5 | 3.5 | 100 | 7.2
67 | 105 | 0 | 13.6933 | 4.5 | 3.6 | 100 | 7.27
67 | 106 | 0 | 13.6933 | 4.5 | 3.7 | 100 | 7.34
67 | 107 | 0 | 13.6933 | 4.5 | 3.8 | 100 | 7.41
67 | 108 | 0 | 13.6933 | 4.5 | 3.9 | 100 | 7.48
67 | 109 | 0 | 13.6933 | 4.5 | 4 | 100 | 7.55
67 | 110 | 0 | 13.6933 | 4.5 | 4.1 | 100 | 7.62
67 | 111 | 0 | 13.6933 | 4.5 | 4.2 | 100 | 7.69
67 | 112 | 0 | 13.6933 | 4.5 | 4.3 | 100 | 7.76
67 | 113 | 0 | 13.6933 | 4.5 | 4.4 | 100 | 7.83
67 | 114 | 0 | 13.6933 | 4.5 | 4.5 | 100 | 7.9
67 | 115 | 0 | 13.6933 | 4.5 | 4.6 | 100 | 7.97
67 | 116 | 0 | 13.6933 | 4.5 | 4.7 | 100 | 8.04
67 | 117 | 0 | 13.6933 | 4.5 | 4.8 | 100 | 8.11
67 | 118 | 0 | 13.6933 | 4.5 | 4.9 | 100 | 8.18
67 | 119 | 0 | 13.6933 | 4.5 | 5 | 100 | 8.25
67 | 120 | 0 | 13.6933 | 4.5 | 5.1 | 100 | 8.3375
67 | 121 | 0 | 13.6933 | 4.5 | 5.2 | 100 | 8.425
67 | 122 | 0 | 13.6933 | 4.5 | 5.3 | 100 | 8.5125
67 | 123 | 0 | 13.6933 | 4.5 | 5.4 | 100 | 8.6
67 | 124 | 0 | 13.6933 | 4.5 | 5.5 | 100 | 8.6875
67 | 125 | 0 | 13.6933 | 4.5 | 5.6 | 100 | 8.775
67 | 126 | 0 | 13.6933 | 4.5 | 5.7 | 100 | 8.8625
67 | 127 | 0 | 13.6933 | 4.5 | 5.8 | 100 | 8.95
67 | 128 | 0 | 13.6933 | 4.5 | 5.9 | 100 | 9.0375
67 | 129 | 0 | 13.6933 | 4.5 | 6 | 100 | 9.125
67 | 130 | 0 | 13.6933 | 4.5 | 6.1 | 100 | 9.2125
67 | 131 | 0 | 13.6933 | 4.5 | 6.2 | 100 | 9.3
67 | 132 | 0 | 13.6933 | 4.5 | 6.3 | 100 | 9.3875
67 | 133 | 0 | 13.6933 | 4.5 | 6.4 | 100 | 9.475
67 | 134 | 0 | 13.6933 | 4.5 | 6.5 | 100 | 9.5625
67 | 135 | 0 | 13.6933 | 4.5 | 6.6 | 100 | 9.65
67 | 136 | 0 | 13.6933 | 4.5 | 6.7 | 100 | 9.7375
67 | 137 | 0 | 13.6933 | 4.5 | 6.8 | 100 | 9.825
67 | 138 | 0 | 13.6933 | 4.5 | 6.9 | 100 | 9.9125
67 | 139 | 0 | 13.6933 | 4.5 | 7 | 100 | 10
67 | 140 | 0 | 13.6933 | 4.5 | 7.1 | 100 | 10.0075
67 | 141 | 0 | 13.6933 | 4.5 | 7.2 | 100 | 10.015
67 | 142 | 0 | 13.6933 | 4.5 | 7.3 | 100 | 10.0225
67 | 143 | 0 | 13.6933 | 4.5 | 7.4 | 100 | 10.03
67 | 144 | 0 | 13.6933 | 4.5 | 7.5 | 100 | 10.0375
67 | 145 | 0 | 13.6933 | 4.5 | 7.6 | 100 | 10.045
67 | 146 | 0 | 13.6933 | 4.5 | 7.7 | 100 | 10.0525
67 | 147 | 0 | 13.6933 | 4.5 | 7.8 | 100 | 10.06
67 | 148 | 0 | 13.6933 | 4.5 | 7.9 | 100 | 10.0675
67 | 149 | 0 | 13.6933 | 4.5 | 8 | 100 | 10.075
67 | 150 | 0 | 13.6933 | 4.5 | 8.1 | 100 | 10.0825
68 | 45 | 0 | 13.7067 | 4.5 | 8.2 | 100 | 10.09
68 | 46 | 0 | 13.7067 | 4.5 | 8.3 | 100 | 10.0975
68 | 47 | 0 | 13.7067 | 4.5 | 8.4 | 100 | 10.105
68 | 48 | 0 | 13.7067 | 4.5 | 8.5 | 100 | 10.1125
68 | 49 | 0 | 13.7067 | 4.5 | 8.6 | 100 | 10.12
68 | 50 | 0 | 13.7067 | 4.5 | 8.7 | 100 | 10.1275
68 | 51 | 0 | 13.7067 | 4.5 | 8.8 | 100 | 10.135
68 | 52 | 0 | 13.7067 | 4.5 | 8.9 | 100 | 10.1425
68 | 53 | 0 | 13.7067 | 4.5 | 9 | 100 | 10.15
68 | 54 | 0 | 13.7067 | 4.5 | 9.1 | 100 | 10.215
68 | 55 | 0 | 13.7067 | 4.5 | 9.2 | 100 | 10.28
68 | 56 | 0 | 13.7067 | 4.5 | 9.3 | 100 | 10.345
68 | 57 | 0 | 13.7067 | 4.5 | 9.4 | 100 | 10.41
68 | 58 | 0 | 13.7067 | 4.5 | 9.5 | 100 | 10.475
68 | 59 | 0 | 13.7067 | 4.5 | 9.6 | 100 | 10.54
68 | 60 | 0 | 13.7067 | 4.5 | 9.7 | 100 | 10.605
68 | 61 | 0 | 13.7067 | 4.5 | 9.8 | 100 | 10.67
68 | 62 | 0 | 13.7067 | 4.5 | 9.9 | 100 | 10.735
68 | 63 | 0 | 13.7067 | 4.5 | 10 | 100 | 10.8
68 | 64 | 0 | 13.7067 | 4.6 | 3 | 100 | 6.86
68 | 65 | 0 | 13.7067 | 4.6 | 3.1 | 100 | 6.93
68 | 66 | 0 | 13.7067 | 4.6 | 3.2 | 100 | 7
68 | 67 | 0 | 13.7067 | 4.6 | 3.3 | 100 | 7.07
68 | 68 | 0 | 13.7067 | 4.6 | 3.4 | 100 | 7.14
68 | 69 | 0 | 13.7067 | 4.6 | 3.5 | 100 | 7.21
68 | 70 | 0 | 13.7067 | 4.6 | 3.6 | 100 | 7.28
68 | 71 | 0 | 13.7067 | 4.6 | 3.7 | 100 | 7.35
68 | 72 | 0 | 13.7067 | 4.6 | 3.8 | 100 | 7.42
68 | 73 | 0 | 13.7067 | 4.6 | 3.9 | 100 | 7.49
68 | 74 | 0 | 13.7067 | 4.6 | 4 | 100 | 7.56
68 | 75 | 0 | 13.7067 | 4.6 | 4.1 | 100 | 7.63
68 | 76 | 0 | 13.7067 | 4.6 | 4.2 | 100 | 7.7
68 | 77 | 0 | 13.7067 | 4.6 | 4.3 | 100 | 7.77
68 | 78 | 0 | 13.7067 | 4.6 | 4.4 | 100 | 7.84
68 | 79 | 0 | 13.7067 | 4.6 | 4.5 | 100 | 7.91
68 | 80 | 0 | 13.7067 | 4.6 | 4.6 | 100 | 7.98
68 | 81 | 0 | 13.7067 | 4.6 | 4.7 | 100 | 8.05
68 | 82 | 0 | 13.7067 | 4.6 | 4.8 | 100 | 8.12
68 | 83 | 0 | 13.7067 | 4.6 | 4.9 | 100 | 8.19
68 | 84 | 0 | 13.7067 | 4.6 | 5 | 100 | 8.26
68 | 85 | 0 | 13.7067 | 4.6 | 5.1 | 100 | 8.348
68 | 86 | 0 | 13.7067 | 4.6 | 5.2 | 100 | 8.436
68 | 87 | 0 | 13.7067 | 4.6 | 5.3 | 100 | 8.524
68 | 88 | 0 | 13.7067 | 4.6 | 5.4 | 100 | 8.612
68 | 89 | 0 | 13.7067 | 4.6 | 5.5 | 100 | 8.7
68 | 90 | 0 | 13.7067 | 4.6 | 5.6 | 100 | 8.788
68 | 91 | 0 | 13.7067 | 4.6 | 5.7 | 100 | 8.876
68 | 92 | 0 | 13.7067 | 4.6 | 5.8 | 100 | 8.964
68 | 93 | 0 | 13.7067 | 4.6 | 5.9 | 100 | 9.052
68 | 94 | 0 | 13.7067 | 4.6 | 6 | 100 | 9.14
68 | 95 | 0 | 13.7067 | 4.6 | 6.1 | 100 | 9.228
68 | 96 | 0 | 13.7067 | 4.6 | 6.2 | 100 | 9.316
68 | 97 | 0 | 13.7067 | 4.6 | 6.3 | 100 | 9.404
68 | 98 | 0 | 13.7067 | 4.6 | 6.4 | 100 | 9.492
68 | 99 | 0 | 13.7067 | 4.6 | 6.5 | 100 | 9.58
68 | 100 | 0 | 13.7067 | 4.6 | 6.6 | 100 | 9.668
68 | 101 | 0 | 13.7067 | 4.6 | 6.7 | 100 | 9.756
68 | 102 | 0 | 13.7067 | 4.6 | 6.8 | 100 | 9.844
68 | 103 | 0 | 13.7067 | 4.6 | 6.9 | 100 | 9.932
68 | 104 | 0 | 13.7067 | 4.6 | 7 | 100 | 10.02
68 | 105 | 0 | 13.7067 | 4.6 | 7.1 | 100 | 10.028
68 | 106 | 0 | 13.7067 | 4.6 | 7.2 | 100 | 10.036
68 | 107 | 0 | 13.7067 | 4.6 | 7.3 | 100 | 10.044
68 | 108 | 0 | 13.7067 | 4.6 | 7.4 | 100 | 10.052
68 | 109 | 0 | 13.7067 | 4.6 | 7.5 | 100 | 10.06
68 | 110 | 0 | 13.7067 | 4.6 | 7.6 | 100 | 10.068
68 | 111 | 0 | 13.7067 | 4.6 | 7.7 | 100 | 10.076
68 | 112 | 0 | 13.7067 | 4.6 | 7.8 | 100 | 10.084
68 | 113 | 0 | 13.7067 | 4.6 | 7.9 | 100 | 10.092
68 | 114 | 0 | 13.7067 | 4.6 | 8 | 100 | 10.1
68 | 115 | 0 | 13.7067 | 4.6 | 8.1 | 100 | 10.108
68 | 116 | 0 | 13.7067 | 4.6 | 8.2 | 100 | 10.116
68 | 117 | 0 | 13.7067 | 4.6 | 8.3 | 100 | 10.124
68 | 118 | 0 | 13.7067 | 4.6 | 8.4 | 100 | 10.132
68 | 119 | 0 | 13.7067 | 4.6 | 8.5 | 100 | 10.14
68 | 120 | 0 | 13.7067 | 4.6 | 8.6 | 100 | 10.148
68 | 121 | 0 | 13.7067 | 4.6 | 8.7 | 100 | 10.156
68 | 122 | 0 | 13.7067 | 4.6 | 8.8 | 100 | 10.164
68 | 123 | 0 | 13.7067 | 4.6 | 8.9 | 100 | 10.172
68 | 124 | 0 | 13.7067 | 4.6 | 9 | 100 | 10.18
68 | 125 | 0 | 13.7067 | 4.6 | 9.1 | 100 | 10.244
68 | 126 | 0 | 13.7067 | 4.6 | 9.2 | 100 | 10.308
68 | 127 | 0 | 13.7067 | 4.6 | 9.3 | 100 | 10.372
68 | 128 | 0 | 13.7067 | 4.6 | 9.4 | 100 | 10.436
68 | 129 | 0 | 13.7067 | 4.6 | 9.5 | 100 | 10.5
68 | 130 | 0 | 13.7067 | 4.6 | 9.6 | 100 | 10.564
68 | 131 | 0 | 13.7067 | 4.6 | 9.7 | 100 | 10.628
68 | 132 | 0 | 13.7067 | 4.6 | 9.8 | 100 | 10.692
68 | 133 | 0 | 13.7067 | 4.6 | 9.9 | 100 | 10.756
68 | 134 | 0 | 13.7067 | 4.6 | 10 | 100 | 10.82
68 | 135 | 0 | 13.7067 | 4.7 | 3 | 100 | 6.87
68 | 136 | 0 | 13.7067 | 4.7 | 3.1 | 100 | 6.94
68 | 137 | 0 | 13.7067 | 4.7 | 3.2 | 100 | 7.01
68 | 138 | 0 | 13.7067 | 4.7 | 3.3 | 100 | 7.08
68 | 139 | 0 | 13.7067 | 4.7 | 3.4 | 100 | 7.15
68 | 140 | 0 | 13.7067 | 4.7 | 3.5 | 100 | 7.22
68 | 141 | 0 | 13.7067 | 4.7 | 3.6 | 100 | 7.29
68 | 142 | 0 | 13.7067 | 4.7 | 3.7 | 100 | 7.36
68 | 143 | 0 | 13.7067 | 4.7 | 3.8 | 100 | 7.43
68 | 144 | 0 | 13.7067 | 4.7 | 3.9 | 100 | 7.5
68 | 145 | 0 | 13.7067 | 4.7 | 4 | 100 | 7.57
68 | 146 | 0 | 13.7067 | 4.7 | 4.1 | 100 | 7.64
68 | 147 | 0 | 13.7067 | 4.7 | 4.2 | 100 | 7.71
68 | 148 | 0 | 13.7067 | 4.7 | 4.3 | 100 | 7.78
68 | 149 | 0 | 13.7067 | 4.7 | 4.4 | 100 | 7.85
68 | 150 | 0 | 13.7067 | 4.7 | 4.5 | 100 | 7.92
69 | 45 | 0 | 13.72 | 4.7 | 4.6 | 100 | 7.99
69 | 46 | 0 | 13.72 | 4.7 | 4.7 | 100 | 8.06
69 | 47 | 0 | 13.72 | 4.7 | 4.8 | 100 | 8.13
69 | 48 | 0 | 13.72 | 4.7 | 4.9 | 100 | 8.2
69 | 49 | 0 | 13.72 | 4.7 | 5 | 100 | 8.27
69 | 50 | 0 | 13.72 | 4.7 | 5.1 | 100 | 8.3585
69 | 51 | 0 | 13.72 | 4.7 | 5.2 | 100 | 8.447
69 | 52 | 0 | 13.72 | 4.7 | 5.3 | 100 | 8.5355
69 | 53 | 0 | 13.72 | 4.7 | 5.4 | 100 | 8.624
69 | 54 | 0 | 13.72 | 4.7 | 5.5 | 100 | 8.7125
69 | 55 | 0 | 13.72 | 4.7 | 5.6 | 100 | 8.801
69 | 56 | 0 | 13.72 | 4.7 | 5.7 | 100 | 8.8895
69 | 57 | 0 | 13.72 | 4.7 | 5.8 | 100 | 8.978
69 | 58 | 0 | 13.72 | 4.7 | 5.9 | 100 | 9.0665
69 | 59 | 0 | 13.72 | 4.7 | 6 | 100 | 9.155
69 | 60 | 0 | 13.72 | 4.7 | 6.1 | 100 | 9.2435
69 | 61 | 0 | 13.72 | 4.7 | 6.2 | 100 | 9.332
69 | 62 | 0 | 13.72 | 4.7 | 6.3 | 100 | 9.4205
69 | 63 | 0 | 13.72 | 4.7 | 6.4 | 100 | 9.509
69 | 64 | 0 | 13.72 | 4.7 | 6.5 | 100 | 9.5975
69 | 65 | 0 | 13.72 | 4.7 | 6.6 | 100 | 9.686
69 | 66 | 0 | 13.72 | 4.7 | 6.7 | 100 | 9.7745
69 | 67 | 0 | 13.72 | 4.7 | 6.8 | 100 | 9.863
69 | 68 | 0 | 13.72 | 4.7 | 6.9 | 100 | 9.9515
69 | 69 | 0 | 13.72 | 4.7 | 7 | 100 | 10.04
69 | 70 | 0 | 13.72 | 4.7 | 7.1 | 100 | 10.0485
69 | 71 | 0 | 13.72 | 4.7 | 7.2 | 100 | 10.057
69 | 72 | 0 | 13.72 | 4.7 | 7.3 | 100 | 10.0655
69 | 73 | 0 | 13.72 | 4.7 | 7.4 | 100 | 10.074
69 | 74 | 0 | 13.72 | 4.7 | 7.5 | 100 | 10.0825
69 | 75 | 0 | 13.72 | 4.7 | 7.6 | 100 | 10.091
69 | 76 | 0 | 13.72 | 4.7 | 7.7 | 100 | 10.0995
69 | 77 | 0 | 13.72 | 4.7 | 7.8 | 100 | 10.108
69 | 78 | 0 | 13.72 | 4.7 | 7.9 | 100 | 10.1165
69 | 79 | 0 | 13.72 | 4.7 | 8 | 100 | 10.125
69 | 80 | 0 | 13.72 | 4.7 | 8.1 | 100 | 10.1335
69 | 81 | 0 | 13.72 | 4.7 | 8.2 | 100 | 10.142
69 | 82 | 0 | 13.72 | 4.7 | 8.3 | 100 | 10.1505
69 | 83 | 0 | 13.72 | 4.7 | 8.4 | 100 | 10.159
69 | 84 | 0 | 13.72 | 4.7 | 8.5 | 100 | 10.1675
69 | 85 | 0 | 13.72 | 4.7 | 8.6 | 100 | 10.176
69 | 86 | 0 | 13.72 | 4.7 | 8.7 | 100 | 10.1845
69 | 87 | 0 | 13.72 | 4.7 | 8.8 | 100 | 10.193
69 | 88 | 0 | 13.72 | 4.7 | 8.9 | 100 | 10.2015
69 | 89 | 0 | 13.72 | 4.7 | 9 | 100 | 10.21
69 | 90 | 0 | 13.72 | 4.7 | 9.1 | 100 | 10.273
69 | 91 | 0 | 13.72 | 4.7 | 9.2 | 100 | 10.336
69 | 92 | 0 | 13.72 | 4.7 | 9.3 | 100 | 10.399
69 | 93 | 0 | 13.72 | 4.7 | 9.4 | 100 | 10.462
69 | 94 | 0 | 13.72 | 4.7 | 9.5 | 100 | 10.525
69 | 95 | 0 | 13.72 | 4.7 | 9.6 | 100 | 10.588
69 | 96 | 0 | 13.72 | 4.7 | 9.7 | 100 | 10.651
69 | 97 | 0 | 13.72 | 4.7 | 9.8 | 100 | 10.714
69 | 98 | 0 | 13.72 | 4.7 | 9.9 | 100 | 10.777
69 | 99 | 0 | 13.72 | 4.7 | 10 | 100 | 10.84
69 | 100 | 0 | 13.72 | 4.8 | 3 | 100 | 6.88
69 | 101 | 0 | 13.72 | 4.8 | 3.1 | 100 | 6.95
69 | 102 | 0 | 13.72 | 4.8 | 3.2 | 100 | 7.02
69 | 103 | 0 | 13.72 | 4.8 | 3.3 | 100 | 7.09
69 | 104 | 0 | 13.72 | 4.8 | 3.4 | 100 | 7.16
69 | 105 | 0 | 13.72 | 4.8 | 3.5 | 100 | 7.23
69 | 106 | 0 | 13.72 | 4.8 | 3.6 | 100 | 7.3
69 | 107 | 0 | 13.72 | 4.8 | 3.7 | 100 | 7.37
69 | 108 | 0 | 13.72 | 4.8 | 3.8 | 100 | 7.44
69 | 109 | 0 | 13.72 | 4.8 | 3.9 | 100 | 7.51
69 | 110 | 0 | 13.72 | 4.8 | 4 | 100 | 7.58
69 | 111 | 0 | 13.72 | 4.8 | 4.1 | 100 | 7.65
69 | 112 | 0 | 13.72 | 4.8 | 4.2 | 100 | 7.72
69 | 113 | 0 | 13.72 | 4.8 | 4.3 | 100 | 7.79
69 | 114 | 0 | 13.72 | 4.8 | 4.4 | 100 | 7.86
69 | 115 | 0 | 13.72 | 4.8 | 4.5 | 100 | 7.93
69 | 116 | 0 | 13.72 | 4.8 | 4.6 | 100 | 8
69 | 117 | 0 | 13.72 | 4.8 | 4.7 | 100 | 8.07
69 | 118 | 0 | 13.72 | 4.8 | 4.8 | 100 | 8.14
69 | 119 | 0 | 13.72 | 4.8 | 4.9 | 100 | 8.21
69 | 120 | 0 | 13.72 | 4.8 | 5 | 100 | 8.28
69 | 121 | 0 | 13.72 | 4.8 | 5.1 | 100 | 8.369
69 | 122 | 0 | 13.72 | 4.8 | 5.2 | 100 | 8.458
69 | 123 | 0 | 13.72 | 4.8 | 5.3 | 100 | 8.547
69 | 124 | 0 | 13.72 | 4.8 | 5.4 | 100 | 8.636
69 | 125 | 0 | 13.72 | 4.8 | 5.5 | 100 | 8.725
69 | 126 | 0 | 13.72 | 4.8 | 5.6 | 100 | 8.814
69 | 127 | 0 | 13.72 | 4.8 | 5.7 | 100 | 8.903
69 | 128 | 0 | 13.72 | 4.8 | 5.8 | 100 | 8.992
69 | 129 | 0 | 13.72 | 4.8 | 5.9 | 100 | 9.081
69 | 130 | 0 | 13.72 | 4.8 | 6 | 100 | 9.17
69 | 131 | 0 | 13.72 | 4.8 | 6.1 | 100 | 9.259
69 | 132 | 0 | 13.72 | 4.8 | 6.2 | 100 | 9.348
69 | 133 | 0 | 13.72 | 4.8 | 6.3 | 100 | 9.437
69 | 134 | 0 | 13.72 | 4.8 | 6.4 | 100 | 9.526
69 | 135 | 0 | 13.72 | 4.8 | 6.5 | 100 | 9.615
69 | 136 | 0 | 13.72 | 4.8 | 6.6 | 100 | 9.704
69 | 137 | 0 | 13.72 | 4.8 | 6.7 | 100 | 9.793
69 | 138 | 0 | 13.72 | 4.8 | 6.8 | 100 | 9.882
69 | 139 | 0 | 13.72 | 4.8 | 6.9 | 100 | 9.971
69 | 140 | 0 | 13.72 | 4.8 | 7 | 100 | 10.06
69 | 141 | 0 | 13.72 | 4.8 | 7.1 | 100 | 10.069
69 | 142 | 0 | 13.72 | 4.8 | 7.2 | 100 | 10.078
69 | 143 | 0 | 13.72 | 4.8 | 7.3 | 100 | 10.087
69 | 144 | 0 | 13.72 | 4.8 | 7.4 | 100 | 10.096
69 | 145 | 0 | 13.72 | 4.8 | 7.5 | 100 | 10.105
69 | 146 | 0 | 13.72 | 4.8 | 7.6 | 100 | 10.114
69 | 147 | 0 | 13.72 | 4.8 | 7.7 | 100 | 10.123
69 | 148 | 0 | 13.72 | 4.8 | 7.8 | 100 | 10.132
69 | 149 | 0 | 13.72 | 4.8 | 7.9 | 100 | 10.141
69 | 150 | 0 | 13.72 | 4.8 | 8 | 100 | 10.15
70 | 45 | 0 | 13.7333 | 4.8 | 8.1 | 100 | 10.159
70 | 46 | 0 | 13.7333 | 4.8 | 8.2 | 100 | 10.168
70 | 47 | 0 | 13.7333 | 4.8 | 8.3 | 100 | 10.177
70 | 48 | 0 | 13.7333 | 4.8 | 8.4 | 100 | 10.186
70 | 49 | 0 | 13.7333 | 4.8 | 8.5 | 100 | 10.195
70 | 50 | 0 | 13.7333 | 4.8 | 8.6 | 100 | 10.204
70 | 51 | 0 | 13.7333 | 4.8 | 8.7 | 100 | 10.213
70 | 52 | 0 | 13.7333 | 4.8 | 8.8 | 100 | 10.222
70 | 53 | 0 | 13.7333 | 4.8 | 8.9 | 100 | 10.231
70 | 54 | 0 | 13.7333 | 4.8 | 9 | 100 | 10.24
70 | 55 | 0 | 13.7333 | 4.8 | 9.1 | 100 | 10.302
70 | 56 | 0 | 13.7333 | 4.8 | 9.2 | 100 | 10.364
70 | 57 | 0 | 13.7333 | 4.8 | 9.3 | 100 | 10.426
70 | 58 | 0 | 13.7333 | 4.8 | 9.4 | 100 | 10.488
70 | 59 | 0 | 13.7333 | 4.8 | 9.5 | 100 | 10.55
70 | 60 | 0 | 13.7333 | 4.8 | 9.6 | 100 | 10.612
70 | 61 | 0 | 13.7333 | 4.8 | 9.7 | 100 | 10.674
70 | 62 | 0 | 13.7333 | 4.8 | 9.8 | 100 | 10.736
70 | 63 | 0 | 13.7333 | 4.8 | 9.9 | 100 | 10.798
70 | 64 | 0 | 13.7333 | 4.8 | 10 | 100 | 10.86
70 | 65 | 0 | 13.7333 | 4.9 | 3 | 100 | 6.89
70 | 66 | 0 | 13.7333 | 4.9 | 3.1 | 100 | 6.96
70 | 67 | 0 | 13.7333 | 4.9 | 3.2 | 100 | 7.03
70 | 68 | 0 | 13.7333 | 4.9 | 3.3 | 100 | 7.1
70 | 69 | 0 | 13.7333 | 4.9 | 3.4 | 100 | 7.17
70 | 70 | 0 | 13.7333 | 4.9 | 3.5 | 100 | 7.24
70 | 71 | 0 | 13.7333 | 4.9 | 3.6 | 100 | 7.31
70 | 72 | 0 | 13.7333 | 4.9 | 3.7 | 100 | 7.38
70 | 73 | 0 | 13.7333 | 4.9 | 3.8 | 100 | 7.45
70 | 74 | 0 | 13.7333 | 4.9 | 3.9 | 100 | 7.52
70 | 75 | 0 | 13.7333 | 4.9 | 4 | 100 | 7.59
70 | 76 | 0 | 13.7333 | 4.9 | 4.1 | 100 | 7.66
70 | 77 | 0 | 13.7333 | 4.9 | 4.2 | 100 | 7.73
70 | 78 | 0 | 13.7333 | 4.9 | 4.3 | 100 | 7.8
70 | 79 | 0 | 13.7333 | 4.9 | 4.4 | 100 | 7.87
70 | 80 | 0 | 13.7333 | 4.9 | 4.5 | 100 | 7.94
70 | 81 | 0 | 13.7333 | 4.9 | 4.6 | 100 | 8.01
70 | 82 | 0 | 13.7333 | 4.9 | 4.7 | 100 | 8.08
70 | 83 | 0 | 13.7333 | 4.9 | 4.8 | 100 | 8.15
70 | 84 | 0 | 13.7333 | 4.9 | 4.9 | 100 | 8.22
70 | 85 | 0 | 13.7333 | 4.9 | 5 | 100 | 8.29
70 | 86 | 0 | 13.7333 | 4.9 | 5.1 | 100 | 8.3795
70 | 87 | 0 | 13.7333 | 4.9 | 5.2 | 100 | 8.469
70 | 88 | 0 | 13.7333 | 4.9 | 5.3 | 100 | 8.5585
70 | 89 | 0 | 13.7333 | 4.9 | 5.4 | 100 | 8.648
70 | 90 | 0 | 13.7333 | 4.9 | 5.5 | 100 | 8.7375
70 | 91 | 0 | 13.7333 | 4.9 | 5.6 | 100 | 8.827
70 | 92 | 0 | 13.7333 | 4.9 | 5.7 | 100 | 8.9165
70 | 93 | 0 | 13.7333 | 4.9 | 5.8 | 100 | 9.006
70 | 94 | 0 | 13.7333 | 4.9 | 5.9 | 100 | 9.0955
70 | 95 | 0 | 13.7333 | 4.9 | 6 | 100 | 9.185
70 | 96 | 0 | 13.7333 | 4.9 | 6.1 | 100 | 9.2745
70 | 97 | 0 | 13.7333 | 4.9 | 6.2 | 100 | 9.364
70 | 98 | 0 | 13.7333 | 4.9 | 6.3 | 100 | 9.4535
70 | 99 | 0 | 13.7333 | 4.9 | 6.4 | 100 | 9.543
70 | 100 | 0 | 13.7333 | 4.9 | 6.5 | 100 | 9.6325
70 | 101 | 0 | 13.7333 | 4.9 | 6.6 | 100 | 9.722
70 | 102 | 0 | 13.7333 | 4.9 | 6.7 | 100 | 9.8115
70 | 103 | 0 | 13.7333 | 4.9 | 6.8 | 100 | 9.901
70 | 104 | 0 | 13.7333 | 4.9 | 6.9 | 100 | 9.9905
70 | 105 | 0 | 13.7333 | 4.9 | 7 | 100 | 10.08
70 | 106 | 0 | 13.7333 | 4.9 | 7.1 | 100 | 10.0895
70 | 107 | 0 | 13.7333 | 4.9 | 7.2 | 100 | 10.099
70 | 108 | 0 | 13.7333 | 4.9 | 7.3 | 100 | 10.1085
70 | 109 | 0 | 13.7333 | 4.9 | 7.4 | 100 | 10.118
70 | 110 | 0 | 13.7333 | 4.9 | 7.5 | 100 | 10.1275
70 | 111 | 0 | 13.7333 | 4.9 | 7.6 | 100 | 10.137
70 | 112 | 0 | 13.7333 | 4.9 | 7.7 | 100 | 10.1465
70 | 113 | 0 | 13.7333 | 4.9 | 7.8 | 100 | 10.156
70 | 114 | 0 | 13.7333 | 4.9 | 7.9 | 100 | 10.1655
70 | 115 | 0 | 13.7333 | 4.9 | 8 | 100 | 10.175
70 | 116 | 0 | 13.7333 | 4.9 | 8.1 | 100 | 10.1845
70 | 117 | 0 | 13.7333 | 4.9 | 8.2 | 100 | 10.194
70 | 118 | 0 | 13.7333 | 4.9 | 8.3 | 100 | 10.2035
70 | 119 | 0 | 13.7333 | 4.9 | 8.4 | 100 | 10.213
70 | 120 | 0 | 13.7333 | 4.9 | 8.5 | 100 | 10.2225
70 | 121 | 0 | 13.7333 | 4.9 | 8.6 | 100 | 10.232
70 | 122 | 0 | 13.7333 | 4.9 | 8.7 | 100 | 10.2415
70 | 123 | 0 | 13.7333 | 4.9 | 8.8 | 100 | 10.251
70 | 124 | 0 | 13.7333 | 4.9 | 8.9 | 100 | 10.2605
70 | 125 | 0 | 13.7333 | 4.9 | 9 | 100 | 10.27
70 | 126 | 0 | 13.7333 | 4.9 | 9.1 | 100 | 10.331
70 | 127 | 0 | 13.7333 | 4.9 | 9.2 | 100 | 10.392
70 | 128 | 0 | 13.7333 | 4.9 | 9.3 | 100 | 10.453
70 | 129 | 0 | 13.7333 | 4.9 | 9.4 | 100 | 10.514
70 | 130 | 0 | 13.7333 | 4.9 | 9.5 | 100 | 10.575
70 | 131 | 0 | 13.7333 | 4.9 | 9.6 | 100 | 10.636
70 | 132 | 0 | 13.7333 | 4.9 | 9.7 | 100 | 10.697
70 | 133 | 0 | 13.7333 | 4.9 | 9.8 | 100 | 10.758
70 | 134 | 0 | 13.7333 | 4.9 | 9.9 | 100 | 10.819
70 | 135 | 0 | 13.7333 | 4.9 | 10 | 100 | 10.88
70 | 136 | 0 | 13.7333 | 5 | 3 | 100 | 6.9
70 | 137 | 0 | 13.7333 | 5 | 3.1 | 100 | 6.97
70 | 138 | 0 | 13.7333 | 5 | 3.2 | 100 | 7.04
70 | 139 | 0 | 13.7333 | 5 | 3.3 | 100 | 7.11
70 | 140 | 0 | 13.7333 | 5 | 3.4 | 100 | 7.18
70 | 141 | 0 | 13.7333 | 5 | 3.5 | 100 | 7.25
70 | 142 | 0 | 13.7333 | 5 | 3.6 | 100 | 7.32
70 | 143 | 0 | 13.7333 | 5 | 3.7 | 100 | 7.39
70 | 144 | 0 | 13.7333 | 5 | 3.8 | 100 | 7.46
70 | 145 | 0 | 13.7333 | 5 | 3.9 | 100 | 7.53
70 | 146 | 0 | 13.7333 | 5 | 4 | 100 | 7.6
70 | 147 | 0 | 13.7333 | 5 | 4.1 | 100 | 7.67
70 | 148 | 0 | 13.7333 | 5 | 4.2 | 100 | 7.74
70 | 149 | 0 | 13.7333 | 5 | 4.3 | 100 | 7.81
70 | 150 | 0 | 13.7333 | 5 | 4.4 | 100 | 7.88
71 | 45 | 0 | 13.7467 | 5 | 4.5 | 100 | 7.95
71 | 46 | 0 | 13.7467 | 5 | 4.6 | 100 | 8.02
71 | 47 | 0 | 13.7467 | 5 | 4.7 | 100 | 8.09
71 | 48 | 0 | 13.7467 | 5 | 4.8 | 100 | 8.16
71 | 49 | 0 | 13.7467 | 5 | 4.9 | 100 | 8.23
71 | 50 | 0 | 13.7467 | 5 | 5 | 100 | 8.3
71 | 51 | 0 | 13.7467 | 5 | 5.1 | 100 | 8.39
71 | 52 | 0 | 13.7467 | 5 | 5.2 | 100 | 8.48
71 | 53 | 0 | 13.7467 | 5 | 5.3 | 100 | 8.57
71 | 54 | 0 | 13.7467 | 5 | 5.4 | 100 | 8.66
71 | 55 | 0 | 13.7467 | 5 | 5.5 | 100 | 8.75
71 | 56 | 0 | 13.7467 | 5 | 5.6 | 100 | 8.84
71 | 57 | 0 | 13.7467 | 5 | 5.7 | 100 | 8.93
71 | 58 | 0 | 13.7467 | 5 | 5.8 | 100 | 9.02
71 | 59 | 0 | 13.7467 | 5 | 5.9 | 100 | 9.11
71 | 60 | 0 | 13.7467 | 5 | 6 | 100 | 9.2
71 | 61 | 0 | 13.7467 | 5 | 6.1 | 100 | 9.29
71 | 62 | 0 | 13.7467 | 5 | 6.2 | 100 | 9.38
71 | 63 | 0 | 13.7467 | 5 | 6.3 | 100 | 9.47
71 | 64 | 0 | 13.7467 | 5 | 6.4 | 100 | 9.56
71 | 65 | 0 | 13.7467 | 5 | 6.5 | 100 | 9.65
71 | 66 | 0 | 13.7467 | 5 | 6.6 | 100 | 9.74
71 | 67 | 0 | 13.7467 | 5 | 6.7 | 100 | 9.83
71 | 68 | 0 | 13.7467 | 5 | 6.8 | 100 | 9.92
71 | 69 | 0 | 13.7467 | 5 | 6.9 | 100 | 10.01
71 | 70 | 0 | 13.7467 | 5 | 7 | 100 | 10.1
71 | 71 | 0 | 13.7467 | 5 | 7.1 | 100 | 10.11
71 | 72 | 0 | 13.7467 | 5 | 7.2 | 100 | 10.12
71 | 73 | 0 | 13.7467 | 5 | 7.3 | 100 | 10.13
71 | 74 | 0 | 13.7467 | 5 | 7.4 | 100 | 10.14
71 | 75 | 0 | 13.7467 | 5 | 7.5 | 100 | 10.15
71 | 76 | 0 | 13.7467 | 5 | 7.6 | 100 | 10.16
71 | 77 | 0 | 13.7467 | 5 | 7.7 | 100 | 10.17
71 | 78 | 0 | 13.7467 | 5 | 7.8 | 100 | 10.18
71 | 79 | 0 | 13.7467 | 5 | 7.9 | 100 | 10.19
71 | 80 | 0 | 13.7467 | 5 | 8 | 100 | 10.2
71 | 81 | 0 | 13.7467 | 5 | 8.1 | 100 | 10.21
71 | 82 | 0 | 13.7467 | 5 | 8.2 | 100 | 10.22
71 | 83 | 0 | 13.7467 | 5 | 8.3 | 100 | 10.23
71 | 84 | 0 | 13.7467 | 5 | 8.4 | 100 | 10.24
71 | 85 | 0 | 13.7467 | 5 | 8.5 | 100 | 10.25
71 | 86 | 0 | 13.7467 | 5 | 8.6 | 100 | 10.26
71 | 87 | 0 | 13.7467 | 5 | 8.7 | 100 | 10.27
71 | 88 | 0 | 13.7467 | 5 | 8.8 | 100 | 10.28
71 | 89 | 0 | 13.7467 | 5 | 8.9 | 100 | 10.29
71 | 90 | 0 | 13.7467 | 5 | 9 | 100 | 10.3
71 | 91 | 0 | 13.7467 | 5 | 9.1 | 100 | 10.36
71 | 92 | 0 | 13.7467 | 5 | 9.2 | 100 | 10.42
71 | 93 | 0 | 13.7467 | 5 | 9.3 | 100 | 10.48
71 | 94 | 0 | 13.7467 | 5 | 9.4 | 100 | 10.54
71 | 95 | 0 | 13.7467 | 5 | 9.5 | 100 | 10.6
71 | 96 | 0 | 13.7467 | 5 | 9.6 | 100 | 10.66
71 | 97 | 0 | 13.7467 | 5 | 9.7 | 100 | 10.72
71 | 98 | 0 | 13.7467 | 5 | 9.8 | 100 | 10.78
71 | 99 | 0 | 13.7467 | 5 | 9.9 | 100 | 10.84
71 | 100 | 0 | 13.7467 | 5 | 10 | 100 | 10.9
71 | 101 | 0 | 13.7467 | 2 | 3 | 135 | 4.6
71 | 102 | 0 | 13.7467 | 2 | 3.1 | 135 | 4.705
71 | 103 | 0 | 13.7467 | 2 | 3.2 | 135 | 4.81
71 | 104 | 0 | 13.7467 | 2 | 3.3 | 135 | 4.915
71 | 105 | 0 | 13.7467 | 2 | 3.4 | 135 | 5.02
71 | 106 | 0 | 13.7467 | 2 | 3.5 | 135 | 5.125
71 | 107 | 0 | 13.7467 | 2 | 3.6 | 135 | 5.23
71 | 108 | 0 | 13.7467 | 2 | 3.7 | 135 | 5.335
71 | 109 | 0 | 13.7467 | 2 | 3.8 | 135 | 5.44
71 | 110 | 0 | 13.7467 | 2 | 3.9 | 135 | 5.545
71 | 111 | 0 | 13.7467 | 2 | 4 | 135 | 5.65
71 | 112 | 0 | 13.7467 | 2 | 4.1 | 135 | 5.755
71 | 113 | 0 | 13.7467 | 2 | 4.2 | 135 | 5.86
71 | 114 | 0 | 13.7467 | 2 | 4.3 | 135 | 5.965
71 | 115 | 0 | 13.7467 | 2 | 4.4 | 135 | 6.07
71 | 116 | 0 | 13.7467 | 2 | 4.5 | 135 | 6.175
71 | 117 | 0 | 13.7467 | 2 | 4.6 | 135 | 6.28
71 | 118 | 0 | 13.7467 | 2 | 4.7 | 135 | 6.385
71 | 119 | 0 | 13.7467 | 2 | 4.8 | 135 | 6.49
71 | 120 | 0 | 13.7467 | 2 | 4.9 | 135 | 6.595
71 | 121 | 0 | 13.7467 | 2 | 5 | 135 | 6.7
71 | 122 | 0 | 13.7467 | 2 | 5.1 | 135 | 6.725
71 | 123 | 0 | 13.7467 | 2 | 5.2 | 135 | 6.75
71 | 124 | 0 | 13.7467 | 2 | 5.3 | 135 | 6.775
71 | 125 | 0 | 13.7467 | 2 | 5.4 | 135 | 6.8
71 | 126 | 0 | 13.7467 | 2 | 5.5 | 135 | 6.825
71 | 127 | 0 | 13.7467 | 2 | 5.6 | 135 | 6.85
71 | 128 | 0 | 13.7467 | 2 | 5.7 | 135 | 6.875
71 | 129 | 0 | 13.7467 | 2 | 5.8 | 135 | 6.9
71 | 130 | 0 | 13.7467 | 2 | 5.9 | 135 | 6.925
71 | 131 | 0 | 13.7467 | 2 | 6 | 135 | 6.95
71 | 132 | 0 | 13.7467 | 2 | 6.1 | 135 | 6.975
71 | 133 | 0 | 13.7467 | 2 | 6.2 | 135 | 7
71 | 134 | 0 | 13.7467 | 2 | 6.3 | 135 | 7.025
71 | 135 | 0 | 13.7467 | 2 | 6.4 | 135 | 7.05
71 | 136 | 0 | 13.7467 | 2 | 6.5 | 135 | 7.075
71 | 137 | 0 | 13.7467 | 2 | 6.6 | 135 | 7.1
71 | 138 | 0 | 13.7467 | 2 | 6.7 | 135 | 7.125
71 | 139 | 0 | 13.7467 | 2 | 6.8 | 135 | 7.15
71 | 140 | 0 | 13.7467 | 2 | 6.9 | 135 | 7.175
71 | 141 | 0 | 13.7467 | 2 | 7 | 135 | 7.2
71 | 142 | 0 | 13.7467 | 2 | 7.1 | 135 | 7.255
71 | 143 | 0 | 13.7467 | 2 | 7.2 | 135 | 7.31
71 | 144 | 0 | 13.7467 | 2 | 7.3 | 135 | 7.365
71 | 145 | 0 | 13.7467 | 2 | 7.4 | 135 | 7.42
71 | 146 | 0 | 13.7467 | 2 | 7.5 | 135 | 7.475
71 | 147 | 0 | 13.7467 | 2 | 7.6 | 135 | 7.53
71 | 148 | 0 | 13.7467 | 2 | 7.7 | 135 | 7.585
71 | 149 | 0 | 13.7467 | 2 | 7.8 | 135 | 7.64
71 | 150 | 0 | 13.7467 | 2 | 7.9 | 135 | 7.695
72 | 45 | 0 | 13.76 | 2 | 8 | 135 | 7.75
72 | 46 | 0 | 13.76 | 2 | 8.1 | 135 | 7.805
72 | 47 | 0 | 13.76 | 2 | 8.2 | 135 | 7.86
72 | 48 | 0 | 13.76 | 2 | 8.3 | 135 | 7.915
72 | 49 | 0 | 13.76 | 2 | 8.4 | 135 | 7.97
72 | 50 | 0 | 13.76 | 2 | 8.5 | 135 | 8.025
72 | 51 | 0 | 13.76 | 2 | 8.6 | 135 | 8.08
72 | 52 | 0 | 13.76 | 2 | 8.7 | 135 | 8.135
72 | 53 | 0 | 13.76 | 2 | 8.8 | 135 | 8.19
72 | 54 | 0 | 13.76 | 2 | 8.9 | 135 | 8.245
72 | 55 | 0 | 13.76 | 2 | 9 | 135 | 8.3
72 | 56 | 0 | 13.76 | 2 | 9.1 | 135 | 8.42
72 | 57 | 0 | 13.76 | 2 | 9.2 | 135 | 8.54
72 | 58 | 0 | 13.76 | 2 | 9.3 | 135 | 8.66
72 | 59 | 0 | 13.76 | 2 | 9.4 | 135 | 8.78
72 | 60 | 0 | 13.76 | 2 | 9.5 | 135 | 8.9
72 | 61 | 0 | 13.76 | 2 | 9.6 | 135 | 9.02
72 | 62 | 0 | 13.76 | 2 | 9.7 | 135 | 9.14
72 | 63 | 0 | 13.76 | 2 | 9.8 | 135 | 9.26
72 | 64 | 0 | 13.76 | 2 | 9.9 | 135 | 9.38
72 | 65 | 0 | 13.76 | 2 | 10 | 135 | 9.5
72 | 66 | 0 | 13.76 | 2.1 | 3 | 135 | 4.62
72 | 67 | 0 | 13.76 | 2.1 | 3.1 | 135 | 4.7255
72 | 68 | 0 | 13.76 | 2.1 | 3.2 | 135 | 4.831
72 | 69 | 0 | 13.76 | 2.1 | 3.3 | 135 | 4.9365
72 | 70 | 0 | 13.76 | 2.1 | 3.4 | 135 | 5.042
72 | 71 | 0 | 13.76 | 2.1 | 3.5 | 135 | 5.1475
72 | 72 | 0 | 13.76 | 2.1 | 3.6 | 135 | 5.253
72 | 73 | 0 | 13.76 | 2.1 | 3.7 | 135 | 5.3585
72 | 74 | 0 | 13.76 | 2.1 | 3.8 | 135 | 5.464
72 | 75 | 0 | 13.76 | 2.1 | 3.9 | 135 | 5.5695
72 | 76 | 0 | 13.76 | 2.1 | 4 | 135 | 5.675
72 | 77 | 0 | 13.76 | 2.1 | 4.1 | 135 | 5.7805
72 | 78 | 0 | 13.76 | 2.1 | 4.2 | 135 | 5.886
72 | 79 | 0 | 13.76 | 2.1 | 4.3 | 135 | 5.9915
72 | 80 | 0 | 13.76 | 2.1 | 4.4 | 135 | 6.097
72 | 81 | 0 | 13.76 | 2.1 | 4.5 | 135 | 6.2025
72 | 82 | 0 | 13.76 | 2.1 | 4.6 | 135 | 6.308
72 | 83 | 0 | 13.76 | 2.1 | 4.7 | 135 | 6.4135
72 | 84 | 0 | 13.76 | 2.1 | 4.8 | 135 | 6.519
72 | 85 | 0 | 13.76 | 2.1 | 4.9 | 135 | 6.6245
72 | 86 | 0 | 13.76 | 2.1 | 5 | 135 | 6.73
72 | 87 | 0 | 13.76 | 2.1 | 5.1 | 135 | 6.7555
72 | 88 | 0 | 13.76 | 2.1 | 5.2 | 135 | 6.781
72 | 89 | 0 | 13.76 | 2.1 | 5.3 | 135 | 6.8065
72 | 90 | 0 | 13.76 | 2.1 | 5.4 | 135 | 6.832
72 | 91 | 0 | 13.76 | 2.1 | 5.5 | 135 | 6.8575
72 | 92 | 0 | 13.76 | 2.1 | 5.6 | 135 | 6.883
72 | 93 | 0 | 13.76 | 2.1 | 5.7 | 135 | 6.9085
72 | 94 | 0 | 13.76 | 2.1 | 5.8 | 135 | 6.934
72 | 95 | 0 | 13.76 | 2.1 | 5.9 | 135 | 6.9595
72 | 96 | 0 | 13.76 | 2.1 | 6 | 135 | 6.985
72 | 97 | 0 | 13.76 | 2.1 | 6.1 | 135 | 7.0105
72 | 98 | 0 | 13.76 | 2.1 | 6.2 | 135 | 7.036
72 | 99 | 0 | 13.76 | 2.1 | 6.3 | 135 | 7.0615
72 | 100 | 0 | 13.76 | 2.1 | 6.4 | 135 | 7.087
72 | 101 | 0 | 13.76 | 2.1 | 6.5 | 135 | 7.1125
72 | 102 | 0 | 13.76 | 2.1 | 6.6 | 135 | 7.138
72 | 103 | 0 | 13.76 | 2.1 | 6.7 | 135 | 7.1635
72 | 104 | 0 | 13.76 | 2.1 | 6.8 | 135 | 7.189
72 | 105 | 0 | 13.76 | 2.1 | 6.9 | 135 | 7.2145
72 | 106 | 0 | 13.76 | 2.1 | 7 | 135 | 7.24
72 | 107 | 0 | 13.76 | 2.1 | 7.1 | 135 | 7.294
72 | 108 | 0 | 13.76 | 2.1 | 7.2 | 135 | 7.348
72 | 109 | 0 | 13.76 | 2.1 | 7.3 | 135 | 7.402
72 | 110 | 0 | 13.76 | 2.1 | 7.4 | 135 | 7.456
72 | 111 | 0 | 13.76 | 2.1 | 7.5 | 135 | 7.51
72 | 112 | 0 | 13.76 | 2.1 | 7.6 | 135 | 7.564
72 | 113 | 0 | 13.76 | 2.1 | 7.7 | 135 | 7.618
72 | 114 | 0 | 13.76 | 2.1 | 7.8 | 135 | 7.672
72 | 115 | 0 | 13.76 | 2.1 | 7.9 | 135 | 7.726
72 | 116 | 0 | 13.76 | 2.1 | 8 | 135 | 7.78
72 | 117 | 0 | 13.76 | 2.1 | 8.1 | 135 | 7.834
72 | 118 | 0 | 13.76 | 2.1 | 8.2 | 135 | 7.888
72 | 119 | 0 | 13.76 | 2.1 | 8.3 | 135 | 7.942
72 | 120 | 0 | 13.76 | 2.1 | 8.4 | 135 | 7.996
72 | 121 | 0 | 13.76 | 2.1 | 8.5 | 135 | 8.05
72 | 122 | 0 | 13.76 | 2.1 | 8.6 | 135 | 8.104
72 | 123 | 0 | 13.76 | 2.1 | 8.7 | 135 | 8.158
72 | 124 | 0 | 13.76 | 2.1 | 8.8 | 135 | 8.212
72 | 125 | 0 | 13.76 | 2.1 | 8.9 | 135 | 8.266
72 | 126 | 0 | 13.76 | 2.1 | 9 | 135 | 8.32
72 | 127 | 0 | 13.76 | 2.1 | 9.1 | 135 | 8.44
72 | 128 | 0 | 13.76 | 2.1 | 9.2 | 135 | 8.56
72 | 129 | 0 | 13.76 | 2.1 | 9.3 | 135 | 8.68
72 | 130 | 0 | 13.76 | 2.1 | 9.4 | 135 | 8.8
72 | 131 | 0 | 13.76 | 2.1 | 9.5 | 135 | 8.92
72 | 132 | 0 | 13.76 | 2.1 | 9.6 | 135 | 9.04
72 | 133 | 0 | 13.76 | 2.1 | 9.7 | 135 | 9.16
72 | 134 | 0 | 13.76 | 2.1 | 9.8 | 135 | 9.28
72 | 135 | 0 | 13.76 | 2.1 | 9.9 | 135 | 9.4
72 | 136 | 0 | 13.76 | 2.1 | 10 | 135 | 9.52
72 | 137 | 0 | 13.76 | 2.2 | 3 | 135 | 4.64
72 | 138 | 0 | 13.76 | 2.2 | 3.1 | 135 | 4.746
72 | 139 | 0 | 13.76 | 2.2 | 3.2 | 135 | 4.852
72 | 140 | 0 | 13.76 | 2.2 | 3.3 | 135 | 4.958
72 | 141 | 0 | 13.76 | 2.2 | 3.4 | 135 | 5.064
72 | 142 | 0 | 13.76 | 2.2 | 3.5 | 135 | 5.17
72 | 143 | 0 | 13.76 | 2.2 | 3.6 | 135 | 5.276
72 | 144 | 0 | 13.76 | 2.2 | 3.7 | 135 | 5.382
72 | 145 | 0 | 13.76 | 2.2 | 3.8 | 135 | 5.488
72 | 146 | 0 | 13.76 | 2.2 | 3.9 | 135 | 5.594
72 | 147 | 0 | 13.76 | 2.2 | 4 | 135 | 5.7
72 | 148 | 0 | 13.76 | 2.2 | 4.1 | 135 | 5.806
72 | 149 | 0 | 13.76 | 2.2 | 4.2 | 135 | 5.912
72 | 150 | 0 | 13.76 | 2.2 | 4.3 | 135 | 6.018
73 | 45 | 0 | 13.7733 | 2.2 | 4.4 | 135 | 6.124
73 | 46 | 0 | 13.7733 | 2.2 | 4.5 | 135 | 6.23
73 | 47 | 0 | 13.7733 | 2.2 | 4.6 | 135 | 6.336
73 | 48 | 0 | 13.7733 | 2.2 | 4.7 | 135 | 6.442
73 | 49 | 0 | 13.7733 | 2.2 | 4.8 | 135 | 6.548
73 | 50 | 0 | 13.7733 | 2.2 | 4.9 | 135 | 6.654
73 | 51 | 0 | 13.7733 | 2.2 | 5 | 135 | 6.76
73 | 52 | 0 | 13.7733 | 2.2 | 5.1 | 135 | 6.786
73 | 53 | 0 | 13.7733 | 2.2 | 5.2 | 135 | 6.812
73 | 54 | 0 | 13.7733 | 2.2 | 5.3 | 135 | 6.838
73 | 55 | 0 | 13.7733 | 2.2 | 5.4 | 135 | 6.864
73 | 56 | 0 | 13.7733 | 2.2 | 5.5 | 135 | 6.89
73 | 57 | 0 | 13.7733 | 2.2 | 5.6 | 135 | 6.916
73 | 58 | 0 | 13.7733 | 2.2 | 5.7 | 135 | 6.942
73 | 59 | 0 | 13.7733 | 2.2 | 5.8 | 135 | 6.968
73 | 60 | 0 | 13.7733 | 2.2 | 5.9 | 135 | 6.994
73 | 61 | 0 | 13.7733 | 2.2 | 6 | 135 | 7.02
73 | 62 | 0 | 13.7733 | 2.2 | 6.1 | 135 | 7.046
73 | 63 | 0 | 13.7733 | 2.2 | 6.2 | 135 | 7.072
73 | 64 | 0 | 13.7733 | 2.2 | 6.3 | 135 | 7.098
73 | 65 | 0 | 13.7733 | 2.2 | 6.4 | 135 | 7.124
73 | 66 | 0 | 13.7733 | 2.2 | 6.5 | 135 | 7.15
73 | 67 | 0 | 13.7733 | 2.2 | 6.6 | 135 | 7.176
73 | 68 | 0 | 13.7733 | 2.2 | 6.7 | 135 | 7.202
73 | 69 | 0 | 13.7733 | 2.2 | 6.8 | 135 | 7.228
73 | 70 | 0 | 13.7733 | 2.2 | 6.9 | 135 | 7.254
73 | 71 | 0 | 13.7733 | 2.2 | 7 | 135 | 7.28
73 | 72 | 0 | 13.7733 | 2.2 | 7.1 | 135 | 7.333
73 | 73 | 0 | 13.7733 | 2.2 | 7.2 | 135 | 7.386
73 | 74 | 0 | 13.7733 | 2.2 | 7.3 | 135 | 7.439
73 | 75 | 0 | 13.7733 | 2.2 | 7.4 | 135 | 7.492
73 | 76 | 0 | 13.7733 | 2.2 | 7.5 | 135 | 7.545
73 | 77 | 0 | 13.7733 | 2.2 | 7.6 | 135 | 7.598
73 | 78 | 0 | 13.7733 | 2.2 | 7.7 | 135 | 7.651
73 | 79 | 0 | 13.7733 | 2.2 | 7.8 | 135 | 7.704
73 | 80 | 0 | 13.7733 | 2.2 | 7.9 | 135 | 7.757
73 | 81 | 0 | 13.7733 | 2.2 | 8 | 135 | 7.81
73 | 82 | 0 | 13.7733 | 2.2 | 8.1 | 135 | 7.863
73 | 83 | 0 | 13.7733 | 2.2 | 8.2 | 135 | 7.916
73 | 84 | 0 | 13.7733 | 2.2 | 8.3 | 135 | 7.969
73 | 85 | 0 | 13.7733 | 2.2 | 8.4 | 135 | 8.022
73 | 86 | 0 | 13.7733 | 2.2 | 8.5 | 135 | 8.075
73 | 87 | 0 | 13.7733 | 2.2 | 8.6 | 135 | 8.128
73 | 88 | 0 | 13.7733 | 2.2 | 8.7 | 135 | 8.181
73 | 89 | 0 | 13.7733 | 2.2 | 8.8 | 135 | 8.234
73 | 90 | 0 | 13.7733 | 2.2 | 8.9 | 135 | 8.287
73 | 91 | 0 | 13.7733 | 2.2 | 9 | 135 | 8.34
73 | 92 | 0 | 13.7733 | 2.2 | 9.1 | 135 | 8.46
73 | 93 | 0 | 13.7733 | 2.2 | 9.2 | 135 | 8.58
73 | 94 | 0 | 13.7733 | 2.2 | 9.3 | 135 | 8.7
73 | 95 | 0 | 13.7733 | 2.2 | 9.4 | 135 | 8.82
73 | 96 | 0 | 13.7733 | 2.2 | 9.5 | 135 | 8.94
73 | 97 | 0 | 13.7733 | 2.2 | 9.6 | 135 | 9.06
73 | 98 | 0 | 13.7733 | 2.2 | 9.7 | 135 | 9.18
73 | 99 | 0 | 13.7733 | 2.2 | 9.8 | 135 | 9.3
73 | 100 | 0 | 13.7733 | 2.2 | 9.9 | 135 | 9.42
73 | 101 | 0 | 13.7733 | 2.2 | 10 | 135 | 9.54
73 | 102 | 0 | 13.7733 | 2.3 | 3 | 135 | 4.66
73 | 103 | 0 | 13.7733 | 2.3 | 3.1 | 135 | 4.7665
73 | 104 | 0 | 13.7733 | 2.3 | 3.2 | 135 | 4.873
73 | 105 | 0 | 13.7733 | 2.3 | 3.3 | 135 | 4.9795
73 | 106 | 0 | 13.7733 | 2.3 | 3.4 | 135 | 5.086
73 | 107 | 0 | 13.7733 | 2.3 | 3.5 | 135 | 5.1925
73 | 108 | 0 | 13.7733 | 2.3 | 3.6 | 135 | 5.299
73 | 109 | 0 | 13.7733 | 2.3 | 3.7 | 135 | 5.4055
73 | 110 | 0 | 13.7733 | 2.3 | 3.8 | 135 | 5.512
73 | 111 | 0 | 13.7733 | 2.3 | 3.9 | 135 | 5.6185
73 | 112 | 0 | 13.7733 | 2.3 | 4 | 135 | 5.725
73 | 113 | 0 | 13.7733 | 2.3 | 4.1 | 135 | 5.8315
73 | 114 | 0 | 13.7733 | 2.3 | 4.2 | 135 | 5.938
73 | 115 | 0 | 13.7733 | 2.3 | 4.3 | 135 | 6.0445
73 | 116 | 0 | 13.7733 | 2.3 | 4.4 | 135 | 6.151
73 | 117 | 0 | 13.7733 | 2.3 | 4.5 | 135 | 6.2575
73 | 118 | 0 | 13.7733 | 2.3 | 4.6 | 135 | 6.364
73 | 119 | 0 | 13.7733 | 2.3 | 4.7 | 135 | 6.4705
73 | 120 | 0 | 13.7733 | 2.3 | 4.8 | 135 | 6.577
73 | 121 | 0 | 13.7733 | 2.3 | 4.9 | 135 | 6.6835
73 | 122 | 0 | 13.7733 | 2.3 | 5 | 135 | 6.79
73 | 123 | 0 | 13.7733 | 2.3 | 5.1 | 135 | 6.8165
73 | 124 | 0 | 13.7733 | 2.3 | 5.2 | 135 | 6.843
73 | 125 | 0 | 13.7733 | 2.3 | 5.3 | 135 | 6.8695
73 | 126 | 0 | 13.7733 | 2.3 | 5.4 | 135 | 6.896
73 | 127 | 0 | 13.7733 | 2.3 | 5.5 | 135 | 6.9225
73 | 128 | 0 | 13.7733 | 2.3 | 5.6 | 135 | 6.949
73 | 129 | 0 | 13.7733 | 2.3 | 5.7 | 135 | 6.9755
73 | 130 | 0 | 13.7733 | 2.3 | 5.8 | 135 | 7.002
73 | 131 | 0 | 13.7733 | 2.3 | 5.9 | 135 | 7.0285
73 | 132 | 0 | 13.7733 | 2.3 | 6 | 135 | 7.055
73 | 133 | 0 | 13.7733 | 2.3 | 6.1 | 135 | 7.0815
73 | 134 | 0 | 13.7733 | 2.3 | 6.2 | 135 | 7.108
73 | 135 | 0 | 13.7733 | 2.3 | 6.3 | 135 | 7.1345
73 | 136 | 0 | 13.7733 | 2.3 | 6.4 | 135 | 7.161
73 | 137 | 0 | 13.7733 | 2.3 | 6.5 | 135 | 7.1875
73 | 138 | 0 | 13.7733 | 2.3 | 6.6 | 135 | 7.214
73 | 139 | 0 | 13.7733 | 2.3 | 6.7 | 135 | 7.2405
73 | 140 | 0 | 13.7733 | 2.3 | 6.8 | 135 | 7.267
73 | 141 | 0 | 13.7733 | 2.3 | 6.9 | 135 | 7.2935
73 | 142 | 0 | 13.7733 | 2.3 | 7 | 135 | 7.32
73 | 143 | 0 | 13.7733 | 2.3 | 7.1 | 135 | 7.372
73 | 144 | 0 | 13.7733 | 2.3 | 7.2 | 135 | 7.424
73 | 145 | 0 | 13.7733 | 2.3 | 7.3 | 135 | 7.476
73 | 146 | 0 | 13.7733 | 2.3 | 7.4 | 135 | 7.528
73 | 147 | 0 | 13.7733 | 2.3 | 7.5 | 135 | 7.58
73 | 148 | 0 | 13.7733 | 2.3 | 7.6 | 135 | 7.632
73 | 149 | 0 | 13.7733 | 2.3 | 7.7 | 135 | 7.684
73 | 150 | 0 | 13.7733 | 2.3 | 7.8 | 135 | 7.736
74 | 45 | 0 | 13.7867 | 2.3 | 7.9 | 135 | 7.788
74 | 46 | 0 | 13.7867 | 2.3 | 8 | 135 | 7.84
74 | 47 | 0 | 13.7867 | 2.3 | 8.1 | 135 | 7.892
74 | 48 | 0 | 13.7867 | 2.3 | 8.2 | 135 | 7.944
74 | 49 | 0 | 13.7867 | 2.3 | 8.3 | 135 | 7.996
74 | 50 | 0 | 13.7867 | 2.3 | 8.4 | 135 | 8.048
74 | 51 | 0 | 13.7867 | 2.3 | 8.5 | 135 | 8.1
74 | 52 | 0 | 13.7867 | 2.3 | 8.6 | 135 | 8.152
74 | 53 | 0 | 13.7867 | 2.3 | 8.7 | 135 | 8.204
74 | 54 | 0 | 13.7867 | 2.3 | 8.8 | 135 | 8.256
74 | 55 | 0 | 13.7867 | 2.3 | 8.9 | 135 | 8.308
74 | 56 | 0 | 13.7867 | 2.3 | 9 | 135 | 8.36
74 | 57 | 0 | 13.7867 | 2.3 | 9.1 | 135 | 8.48
74 | 58 | 0 | 13.7867 | 2.3 | 9.2 | 135 | 8.6
74 | 59 | 0 | 13.7867 | 2.3 | 9.3 | 135 | 8.72
74 | 60 | 0 | 13.7867 | 2.3 | 9.4 | 135 | 8.84
74 | 61 | 0 | 13.7867 | 2.3 | 9.5 | 135 | 8.96
74 | 62 | 0 | 13.7867 | 2.3 | 9.6 | 135 | 9.08
74 | 63 | 0 | 13.7867 | 2.3 | 9.7 | 135 | 9.2
74 | 64 | 0 | 13.7867 | 2.3 | 9.8 | 135 | 9.32
74 | 65 | 0 | 13.7867 | 2.3 | 9.9 | 135 | 9.44
74 | 66 | 0 | 13.7867 | 2.3 | 10 | 135 | 9.56
74 | 67 | 0 | 13.7867 | 2.4 | 3 | 135 | 4.68
74 | 68 | 0 | 13.7867 | 2.4 | 3.1 | 135 | 4.787
74 | 69 | 0 | 13.7867 | 2.4 | 3.2 | 135 | 4.894
74 | 70 | 0 | 13.7867 | 2.4 | 3.3 | 135 | 5.001
74 | 71 | 0 | 13.7867 | 2.4 | 3.4 | 135 | 5.108
74 | 72 | 0 | 13.7867 | 2.4 | 3.5 | 135 | 5.215
74 | 73 | 0 | 13.7867 | 2.4 | 3.6 | 135 | 5.322
74 | 74 | 0 | 13.7867 | 2.4 | 3.7 | 135 | 5.429
74 | 75 | 0 | 13.7867 | 2.4 | 3.8 | 135 | 5.536
74 | 76 | 0 | 13.7867 | 2.4 | 3.9 | 135 | 5.643
74 | 77 | 0 | 13.7867 | 2.4 | 4 | 135 | 5.75
74 | 78 | 0 | 13.7867 | 2.4 | 4.1 | 135 | 5.857
74 | 79 | 0 | 13.7867 | 2.4 | 4.2 | 135 | 5.964
74 | 80 | 0 | 13.7867 | 2.4 | 4.3 | 135 | 6.071
74 | 81 | 0 | 13.7867 | 2.4 | 4.4 | 135 | 6.178
74 | 82 | 0 | 13.7867 | 2.4 | 4.5 | 135 | 6.285
74 | 83 | 0 | 13.7867 | 2.4 | 4.6 | 135 | 6.392
74 | 84 | 0 | 13.7867 | 2.4 | 4.7 | 135 | 6.499
74 | 85 | 0 | 13.7867 | 2.4 | 4.8 | 135 | 6.606
74 | 86 | 0 | 13.7867 | 2.4 | 4.9 | 135 | 6.713
74 | 87 | 0 | 13.7867 | 2.4 | 5 | 135 | 6.82
74 | 88 | 0 | 13.7867 | 2.4 | 5.1 | 135 | 6.847
74 | 89 | 0 | 13.7867 | 2.4 | 5.2 | 135 | 6.874
74 | 90 | 0 | 13.7867 | 2.4 | 5.3 | 135 | 6.901
74 | 91 | 0 | 13.7867 | 2.4 | 5.4 | 135 | 6.928
74 | 92 | 0 | 13.7867 | 2.4 | 5.5 | 135 | 6.955
74 | 93 | 0 | 13.7867 | 2.4 | 5.6 | 135 | 6.982
74 | 94 | 0 | 13.7867 | 2.4 | 5.7 | 135 | 7.009
74 | 95 | 0 | 13.7867 | 2.4 | 5.8 | 135 | 7.036
74 | 96 | 0 | 13.7867 | 2.4 | 5.9 | 135 | 7.063
74 | 97 | 0 | 13.7867 | 2.4 | 6 | 135 | 7.09
74 | 98 | 0 | 13.7867 | 2.4 | 6.1 | 135 | 7.117
74 | 99 | 0 | 13.7867 | 2.4 | 6.2 | 135 | 7.144
74 | 100 | 0 | 13.7867 | 2.4 | 6.3 | 135 | 7.171
74 | 101 | 0 | 13.7867 | 2.4 | 6.4 | 135 | 7.198
74 | 102 | 0 | 13.7867 | 2.4 | 6.5 | 135 | 7.225
74 | 103 | 0 | 13.7867 | 2.4 | 6.6 | 135 | 7.252
74 | 104 | 0 | 13.7867 | 2.4 | 6.7 | 135 | 7.279
74 | 105 | 0 | 13.7867 | 2.4 | 6.8 | 135 | 7.306
74 | 106 | 0 | 13.7867 | 2.4 | 6.9 | 135 | 7.333
74 | 107 | 0 | 13.7867 | 2.4 | 7 | 135 | 7.36
74 | 108 | 0 | 13.7867 | 2.4 | 7.1 | 135 | 7.411
74 | 109 | 0 | 13.7867 | 2.4 | 7.2 | 135 | 7.462
74 | 110 | 0 | 13.7867 | 2.4 | 7.3 | 135 | 7.513
74 | 111 | 0 | 13.7867 | 2.4 | 7.4 | 135 | 7.564
74 | 112 | 0 | 13.7867 | 2.4 | 7.5 | 135 | 7.615
74 | 113 | 0 | 13.7867 | 2.4 | 7.6 | 135 | 7.666
74 | 114 | 0 | 13.7867 | 2.4 | 7.7 | 135 | 7.717
74 | 115 | 0 | 13.7867 | 2.4 | 7.8 | 135 | 7.768
74 | 116 | 0 | 13.7867 | 2.4 | 7.9 | 135 | 7.819
74 | 117 | 0 | 13.7867 | 2.4 | 8 | 135 | 7.87
74 | 118 | 0 | 13.7867 | 2.4 | 8.1 | 135 | 7.921
74 | 119 | 0 | 13.7867 | 2.4 | 8.2 | 135 | 7.972
74 | 120 | 0 | 13.7867 | 2.4 | 8.3 | 135 | 8.023
74 | 121 | 0 | 13.7867 | 2.4 | 8.4 | 135 | 8.074
74 | 122 | 0 | 13.7867 | 2.4 | 8.5 | 135 | 8.125
74 | 123 | 0 | 13.7867 | 2.4 | 8.6 | 135 | 8.176
74 | 124 | 0 | 13.7867 | 2.4 | 8.7 | 135 | 8.227
74 | 125 | 0 | 13.7867 | 2.4 | 8.8 | 135 | 8.278
74 | 126 | 0 | 13.7867 | 2.4 | 8.9 | 135 | 8.329
74 | 127 | 0 | 13.7867 | 2.4 | 9 | 135 | 8.38
74 | 128 | 0 | 13.7867 | 2.4 | 9.1 | 135 | 8.5
74 | 129 | 0 | 13.7867 | 2.4 | 9.2 | 135 | 8.62
74 | 130 | 0 | 13.7867 | 2.4 | 9.3 | 135 | 8.74
74 | 131 | 0 | 13.7867 | 2.4 | 9.4 | 135 | 8.86
74 | 132 | 0 | 13.7867 | 2.4 | 9.5 | 135 | 8.98
74 | 133 | 0 | 13.7867 | 2.4 | 9.6 | 135 | 9.1
74 | 134 | 0 | 13.7867 | 2.4 | 9.7 | 135 | 9.22
74 | 135 | 0 | 13.7867 | 2.4 | 9.8 | 135 | 9.34
74 | 136 | 0 | 13.7867 | 2.4 | 9.9 | 135 | 9.46
74 | 137 | 0 | 13.7867 | 2.4 | 10 | 135 | 9.58
74 | 138 | 0 | 13.7867 | 2.5 | 3 | 135 | 4.7
74 | 139 | 0 | 13.7867 | 2.5 | 3.1 | 135 | 4.8075
74 | 140 | 0 | 13.7867 | 2.5 | 3.2 | 135 | 4.915
74 | 141 | 0 | 13.7867 | 2.5 | 3.3 | 135 | 5.0225
74 | 142 | 0 | 13.7867 | 2.5 | 3.4 | 135 | 5.13
74 | 143 | 0 | 13.7867 | 2.5 | 3.5 | 135 | 5.2375
74 | 144 | 0 | 13.7867 | 2.5 | 3.6 | 135 | 5.345
74 | 145 | 0 | 13.7867 | 2.5 | 3.7 | 135 | 5.4525
74 | 146 | 0 | 13.7867 | 2.5 | 3.8 | 135 | 5.56
74 | 147 | 0 | 13.7867 | 2.5 | 3.9 | 135 | 5.6675
74 | 148 | 0 | 13.7867 | 2.5 | 4 | 135 | 5.775
74 | 149 | 0 | 13.7867 | 2.5 | 4.1 | 135 | 5.8825
74 | 150 | 0 | 13.7867 | 2.5 | 4.2 | 135 | 5.99
75 | 45 | 0 | 13.8 | 2.5 | 4.3 | 135 | 6.0975
75 | 46 | 0 | 13.8 | 2.5 | 4.4 | 135 | 6.205
75 | 47 | 0 | 13.8 | 2.5 | 4.5 | 135 | 6.3125
75 | 48 | 0 | 13.8 | 2.5 | 4.6 | 135 | 6.42
75 | 49 | 0 | 13.8 | 2.5 | 4.7 | 135 | 6.5275
75 | 50 | 0 | 13.8 | 2.5 | 4.8 | 135 | 6.635
75 | 51 | 0 | 13.8 | 2.5 | 4.9 | 135 | 6.7425
75 | 52 | 0 | 13.8 | 2.5 | 5 | 135 | 6.85
75 | 53 | 0 | 13.8 | 2.5 | 5.1 | 135 | 6.8775
75 | 54 | 0 | 13.8 | 2.5 | 5.2 | 135 | 6.905
75 | 55 | 0 | 13.8 | 2.5 | 5.3 | 135 | 6.9325
75 | 56 | 0 | 13.8 | 2.5 | 5.4 | 135 | 6.96
75 | 57 | 0 | 13.8 | 2.5 | 5.5 | 135 | 6.9875
75 | 58 | 0 | 13.8 | 2.5 | 5.6 | 135 | 7.015
75 | 59 | 0 | 13.8 | 2.5 | 5.7 | 135 | 7.0425
75 | 60 | 0 | 13.8 | 2.5 | 5.8 | 135 | 7.07
75 | 61 | 0 | 13.8 | 2.5 | 5.9 | 135 | 7.0975
75 | 62 | 0 | 13.8 | 2.5 | 6 | 135 | 7.125
75 | 63 | 0 | 13.8 | 2.5 | 6.1 | 135 | 7.1525
75 | 64 | 0 | 13.8 | 2.5 | 6.2 | 135 | 7.18
75 | 65 | 0 | 13.8 | 2.5 | 6.3 | 135 | 7.2075
75 | 66 | 0 | 13.8 | 2.5 | 6.4 | 135 | 7.235
75 | 67 | 0 | 13.8 | 2.5 | 6.5 | 135 | 7.2625
75 | 68 | 0 | 13.8 | 2.5 | 6.6 | 135 | 7.29
75 | 69 | 0 | 13.8 | 2.5 | 6.7 | 135 | 7.3175
75 | 70 | 0 | 13.8 | 2.5 | 6.8 | 135 | 7.345
75 | 71 | 0 | 13.8 | 2.5 | 6.9 | 135 | 7.3725
75 | 72 | 0 | 13.8 | 2.5 | 7 | 135 | 7.4
75 | 73 | 0 | 13.8 | 2.5 | 7.1 | 135 | 7.45
75 | 74 | 0 | 13.8 | 2.5 | 7.2 | 135 | 7.5
75 | 75 | 0 | 13.8 | 2.5 | 7.3 | 135 | 7.55
75 | 76 | 0 | 13.8 | 2.5 | 7.4 | 135 | 7.6
75 | 77 | 0 | 13.8 | 2.5 | 7.5 | 135 | 7.65
75 | 78 | 0 | 13.8 | 2.5 | 7.6 | 135 | 7.7
75 | 79 | 0 | 13.8 | 2.5 | 7.7 | 135 | 7.75
75 | 80 | 0 | 13.8 | 2.5 | 7.8 | 135 | 7.8
75 | 81 | 0 | 13.8 | 2.5 | 7.9 | 135 | 7.85
75 | 82 | 0 | 13.8 | 2.5 | 8 | 135 | 7.9
75 | 83 | 0 | 13.8 | 2.5 | 8.1 | 135 | 7.95
75 | 84 | 0 | 13.8 | 2.5 | 8.2 | 135 | 8
75 | 85 | 0 | 13.8 | 2.5 | 8.3 | 135 | 8.05
75 | 86 | 0 | 13.8 | 2.5 | 8.4 | 135 | 8.1
75 | 87 | 0 | 13.8 | 2.5 | 8.5 | 135 | 8.15
75 | 88 | 0 | 13.8 | 2.5 | 8.6 | 135 | 8.2
75 | 89 | 0 | 13.8 | 2.5 | 8.7 | 135 | 8.25
75 | 90 | 0 | 13.8 | 2.5 | 8.8 | 135 | 8.3
75 | 91 | 0 | 13.8 | 2.5 | 8.9 | 135 | 8.35
75 | 92 | 0 | 13.8 | 2.5 | 9 | 135 | 8.4
75 | 93 | 0 | 13.8 | 2.5 | 9.1 | 135 | 8.52
75 | 94 | 0 | 13.8 | 2.5 | 9.2 | 135 | 8.64
75 | 95 | 0 | 13.8 | 2.5 | 9.3 | 135 | 8.76
75 | 96 | 0 | 13.8 | 2.5 | 9.4 | 135 | 8.88
75 | 97 | 0 | 13.8 | 2.5 | 9.5 | 135 | 9
75 | 98 | 0 | 13.8 | 2.5 | 9.6 | 135 | 9.12
75 | 99 | 0 | 13.8 | 2.5 | 9.7 | 135 | 9.24
75 | 100 | 0 | 13.8 | 2.5 | 9.8 | 135 | 9.36
75 | 101 | 0 | 13.8 | 2.5 | 9.9 | 135 | 9.48
75 | 102 | 0 | 13.8 | 2.5 | 10 | 135 | 9.6
75 | 103 | 0 | 13.8 | 2.6 | 3 | 135 | 4.72
75 | 104 | 0 | 13.8 | 2.6 | 3.1 | 135 | 4.828
75 | 105 | 0 | 13.8 | 2.6 | 3.2 | 135 | 4.936
75 | 106 | 0 | 13.8 | 2.6 | 3.3 | 135 | 5.044
75 | 107 | 0 | 13.8 | 2.6 | 3.4 | 135 | 5.152
75 | 108 | 0 | 13.8 | 2.6 | 3.5 | 135 | 5.26
75 | 109 | 0 | 13.8 | 2.6 | 3.6 | 135 | 5.368
75 | 110 | 0 | 13.8 | 2.6 | 3.7 | 135 | 5.476
75 | 111 | 0 | 13.8 | 2.6 | 3.8 | 135 | 5.584
75 | 112 | 0 | 13.8 | 2.6 | 3.9 | 135 | 5.692
75 | 113 | 0 | 13.8 | 2.6 | 4 | 135 | 5.8
75 | 114 | 0 | 13.8 | 2.6 | 4.1 | 135 | 5.908
75 | 115 | 0 | 13.8 | 2.6 | 4.2 | 135 | 6.016
75 | 116 | 0 | 13.8 | 2.6 | 4.3 | 135 | 6.124
75 | 117 | 0 | 13.8 | 2.6 | 4.4 | 135 | 6.232
75 | 118 | 0 | 13.8 | 2.6 | 4.5 | 135 | 6.34
75 | 119 | 0 | 13.8 | 2.6 | 4.6 | 135 | 6.448
75 | 120 | 0 | 13.8 | 2.6 | 4.7 | 135 | 6.556
75 | 121 | 0 | 13.8 | 2.6 | 4.8 | 135 | 6.664
75 | 122 | 0 | 13.8 | 2.6 | 4.9 | 135 | 6.772
75 | 123 | 0 | 13.8 | 2.6 | 5 | 135 | 6.88
75 | 124 | 0 | 13.8 | 2.6 | 5.1 | 135 | 6.908
75 | 125 | 0 | 13.8 | 2.6 | 5.2 | 135 | 6.936
75 | 126 | 0 | 13.8 | 2.6 | 5.3 | 135 | 6.964
75 | 127 | 0 | 13.8 | 2.6 | 5.4 | 135 | 6.992
75 | 128 | 0 | 13.8 | 2.6 | 5.5 | 135 | 7.02
75 | 129 | 0 | 13.8 | 2.6 | 5.6 | 135 | 7.048
75 | 130 | 0 | 13.8 | 2.6 | 5.7 | 135 | 7.076
75 | 131 | 0 | 13.8 | 2.6 | 5.8 | 135 | 7.104
75 | 132 | 0 | 13.8 | 2.6 | 5.9 | 135 | 7.132
75 | 133 | 0 | 13.8 | 2.6 | 6 | 135 | 7.16
75 | 134 | 0 | 13.8 | 2.6 | 6.1 | 135 | 7.188
75 | 135 | 0 | 13.8 | 2.6 | 6.2 | 135 | 7.216
75 | 136 | 0 | 13.8 | 2.6 | 6.3 | 135 | 7.244
75 | 137 | 0 | 13.8 | 2.6 | 6.4 | 135 | 7.272
75 | 138 | 0 | 13.8 | 2.6 | 6.5 | 135 | 7.3
75 | 139 | 0 | 13.8 | 2.6 | 6.6 | 135 | 7.328
75 | 140 | 0 | 13.8 | 2.6 | 6.7 | 135 | 7.356
75 | 141 | 0 | 13.8 | 2.6 | 6.8 | 135 | 7.384
75 | 142 | 0 | 13.8 | 2.6 | 6.9 | 135 | 7.412
75 | 143 | 0 | 13.8 | 2.6 | 7 | 135 | 7.44
75 | 144 | 0 | 13.8 | 2.6 | 7.1 | 135 | 7.489
75 | 145 | 0 | 13.8 | 2.6 | 7.2 | 135 | 7.538
75 | 146 | 0 | 13.8 | 2.6 | 7.3 | 135 | 7.587
75 | 147 | 0 | 13.8 | 2.6 | 7.4 | 135 | 7.636
75 | 148 | 0 | 13.8 | 2.6 | 7.5 | 135 | 7.685
75 | 149 | 0 | 13.8 | 2.6 | 7.6 | 135 | 7.734
75 | 150 | 0 | 13.8 | 2.6 | 7.7 | 135 | 7.783
30 | 45 | 55 | 10 | 2.6 | 7.8 | 135 | 7.832
30 | 46 | 55 | 10.06 | 2.6 | 7.9 | 135 | 7.881
30 | 47 | 55 | 10.12 | 2.6 | 8 | 135 | 7.93
30 | 48 | 55 | 10.18 | 2.6 | 8.1 | 135 | 7.979
30 | 49 | 55 | 10.24 | 2.6 | 8.2 | 135 | 8.028
30 | 50 | 55 | 10.3 | 2.6 | 8.3 | 135 | 8.077
30 | 51 | 55 | 10.36 | 2.6 | 8.4 | 135 | 8.126
30 | 52 | 55 | 10.42 | 2.6 | 8.5 | 135 | 8.175
30 | 53 | 55 | 10.48 | 2.6 | 8.6 | 135 | 8.224
30 | 54 | 55 | 10.54 | 2.6 | 8.7 | 135 | 8.273
30 | 55 | 55 | 10.6 | 2.6 | 8.8 | 135 | 8.322
30 | 56 | 55 | 10.66 | 2.6 | 8.9 | 135 | 8.371
30 | 57 | 55 | 10.72 | 2.6 | 9 | 135 | 8.42
30 | 58 | 55 | 10.78 | 2.6 | 9.1 | 135 | 8.54
30 | 59 | 55 | 10.84 | 2.6 | 9.2 | 135 | 8.66
30 | 60 | 55 | 10.9 | 2.6 | 9.3 | 135 | 8.78
30 | 61 | 55 | 10.96 | 2.6 | 9.4 | 135 | 8.9
30 | 62 | 55 | 11.02 | 2.6 | 9.5 | 135 | 9.02
30 | 63 | 55 | 11.08 | 2.6 | 9.6 | 135 | 9.14
30 | 64 | 55 | 11.14 | 2.6 | 9.7 | 135 | 9.26
30 | 65 | 55 | 11.2 | 2.6 | 9.8 | 135 | 9.38
30 | 66 | 55 | 11.26 | 2.6 | 9.9 | 135 | 9.5
30 | 67 | 55 | 11.32 | 2.6 | 10 | 135 | 9.62
30 | 68 | 55 | 11.38 | 2.7 | 3 | 135 | 4.74
30 | 69 | 55 | 11.44 | 2.7 | 3.1 | 135 | 4.8485
30 | 70 | 55 | 11.5 | 2.7 | 3.2 | 135 | 4.957
30 | 71 | 55 | 11.56 | 2.7 | 3.3 | 135 | 5.0655
30 | 72 | 55 | 11.62 | 2.7 | 3.4 | 135 | 5.174
30 | 73 | 55 | 11.68 | 2.7 | 3.5 | 135 | 5.2825
30 | 74 | 55 | 11.74 | 2.7 | 3.6 | 135 | 5.391
30 | 75 | 55 | 11.8 | 2.7 | 3.7 | 135 | 5.4995
30 | 76 | 55 | 11.848 | 2.7 | 3.8 | 135 | 5.608
30 | 77 | 55 | 11.896 | 2.7 | 3.9 | 135 | 5.7165
30 | 78 | 55 | 11.944 | 2.7 | 4 | 135 | 5.825
30 | 79 | 55 | 11.992 | 2.7 | 4.1 | 135 | 5.9335
30 | 80 | 55 | 12.04 | 2.7 | 4.2 | 135 | 6.042
30 | 81 | 55 | 12.088 | 2.7 | 4.3 | 135 | 6.1505
30 | 82 | 55 | 12.136 | 2.7 | 4.4 | 135 | 6.259
30 | 83 | 55 | 12.184 | 2.7 | 4.5 | 135 | 6.3675
30 | 84 | 55 | 12.232 | 2.7 | 4.6 | 135 | 6.476
30 | 85 | 55 | 12.28 | 2.7 | 4.7 | 135 | 6.5845
30 | 86 | 55 | 12.328 | 2.7 | 4.8 | 135 | 6.693
30 | 87 | 55 | 12.376 | 2.7 | 4.9 | 135 | 6.8015
30 | 88 | 55 | 12.424 | 2.7 | 5 | 135 | 6.91
30 | 89 | 55 | 12.472 | 2.7 | 5.1 | 135 | 6.9385
30 | 90 | 55 | 12.52 | 2.7 | 5.2 | 135 | 6.967
30 | 91 | 55 | 12.568 | 2.7 | 5.3 | 135 | 6.9955
30 | 92 | 55 | 12.616 | 2.7 | 5.4 | 135 | 7.024
30 | 93 | 55 | 12.664 | 2.7 | 5.5 | 135 | 7.0525
30 | 94 | 55 | 12.712 | 2.7 | 5.6 | 135 | 7.081
30 | 95 | 55 | 12.76 | 2.7 | 5.7 | 135 | 7.1095
30 | 96 | 55 | 12.808 | 2.7 | 5.8 | 135 | 7.138
30 | 97 | 55 | 12.856 | 2.7 | 5.9 | 135 | 7.1665
30 | 98 | 55 | 12.904 | 2.7 | 6 | 135 | 7.195
30 | 99 | 55 | 12.952 | 2.7 | 6.1 | 135 | 7.2235
30 | 100 | 55 | 13 | 2.7 | 6.2 | 135 | 7.252
30 | 101 | 55 | 13.044 | 2.7 | 6.3 | 135 | 7.2805
30 | 102 | 55 | 13.088 | 2.7 | 6.4 | 135 | 7.309
30 | 103 | 55 | 13.132 | 2.7 | 6.5 | 135 | 7.3375
30 | 104 | 55 | 13.176 | 2.7 | 6.6 | 135 | 7.366
30 | 105 | 55 | 13.22 | 2.7 | 6.7 | 135 | 7.3945
30 | 106 | 55 | 13.264 | 2.7 | 6.8 | 135 | 7.423
30 | 107 | 55 | 13.308 | 2.7 | 6.9 | 135 | 7.4515
30 | 108 | 55 | 13.352 | 2.7 | 7 | 135 | 7.48
30 | 109 | 55 | 13.396 | 2.7 | 7.1 | 135 | 7.528
30 | 110 | 55 | 13.44 | 2.7 | 7.2 | 135 | 7.576
30 | 111 | 55 | 13.484 | 2.7 | 7.3 | 135 | 7.624
30 | 112 | 55 | 13.528 | 2.7 | 7.4 | 135 | 7.672
30 | 113 | 55 | 13.572 | 2.7 | 7.5 | 135 | 7.72
30 | 114 | 55 | 13.616 | 2.7 | 7.6 | 135 | 7.768
30 | 115 | 55 | 13.66 | 2.7 | 7.7 | 135 | 7.816
30 | 116 | 55 | 13.704 | 2.7 | 7.8 | 135 | 7.864
30 | 117 | 55 | 13.748 | 2.7 | 7.9 | 135 | 7.912
30 | 118 | 55 | 13.792 | 2.7 | 8 | 135 | 7.96
30 | 119 | 55 | 13.836 | 2.7 | 8.1 | 135 | 8.008
30 | 120 | 55 | 13.88 | 2.7 | 8.2 | 135 | 8.056
30 | 121 | 55 | 13.924 | 2.7 | 8.3 | 135 | 8.104
30 | 122 | 55 | 13.968 | 2.7 | 8.4 | 135 | 8.152
30 | 123 | 55 | 14.012 | 2.7 | 8.5 | 135 | 8.2
30 | 124 | 55 | 14.056 | 2.7 | 8.6 | 135 | 8.248
30 | 125 | 55 | 14.1 | 2.7 | 8.7 | 135 | 8.296
30 | 126 | 55 | 14.144 | 2.7 | 8.8 | 135 | 8.344
30 | 127 | 55 | 14.188 | 2.7 | 8.9 | 135 | 8.392
30 | 128 | 55 | 14.232 | 2.7 | 9 | 135 | 8.44
30 | 129 | 55 | 14.276 | 2.7 | 9.1 | 135 | 8.56
30 | 130 | 55 | 14.32 | 2.7 | 9.2 | 135 | 8.68
30 | 131 | 55 | 14.364 | 2.7 | 9.3 | 135 | 8.8
30 | 132 | 55 | 14.408 | 2.7 | 9.4 | 135 | 8.92
30 | 133 | 55 | 14.452 | 2.7 | 9.5 | 135 | 9.04
30 | 134 | 55 | 14.496 | 2.7 | 9.6 | 135 | 9.16
30 | 135 | 55 | 14.54 | 2.7 | 9.7 | 135 | 9.28
30 | 136 | 55 | 14.584 | 2.7 | 9.8 | 135 | 9.4
30 | 137 | 55 | 14.628 | 2.7 | 9.9 | 135 | 9.52
30 | 138 | 55 | 14.672 | 2.7 | 10 | 135 | 9.64
30 | 139 | 55 | 14.716 | 2.8 | 3 | 135 | 4.76
30 | 140 | 55 | 14.76 | 2.8 | 3.1 | 135 | 4.869
30 | 141 | 55 | 14.804 | 2.8 | 3.2 | 135 | 4.978
30 | 142 | 55 | 14.848 | 2.8 | 3.3 | 135 | 5.087
30 | 143 | 55 | 14.892 | 2.8 | 3.4 | 135 | 5.196
30 | 144 | 55 | 14.936 | 2.8 | 3.5 | 135 | 5.305
30 | 145 | 55 | 14.98 | 2.8 | 3.6 | 135 | 5.414
30 | 146 | 55 | 15.024 | 2.8 | 3.7 | 135 | 5.523
30 | 147 | 55 | 15.068 | 2.8 | 3.8 | 135 | 5.632
30 | 148 | 55 | 15.112 | 2.8 | 3.9 | 135 | 5.741
30 | 149 | 55 | 15.156 | 2.8 | 4 | 135 | 5.85
30 | 150 | 55 | 15.2 | 2.8 | 4.1 | 135 | 5.959
31 | 45 | 55 | 10 | 2.8 | 4.2 | 135 | 6.068
31 | 46 | 55 | 10.0604 | 2.8 | 4.3 | 135 | 6.177
31 | 47 | 55 | 10.1209 | 2.8 | 4.4 | 135 | 6.286
31 | 48 | 55 | 10.1813 | 2.8 | 4.5 | 135 | 6.395
31 | 49 | 55 | 10.2418 | 2.8 | 4.6 | 135 | 6.504
31 | 50 | 55 | 10.3022 | 2.8 | 4.7 | 135 | 6.613
31 | 51 | 55 | 10.3627 | 2.8 | 4.8 | 135 | 6.722
31 | 52 | 55 | 10.4231 | 2.8 | 4.9 | 135 | 6.831
31 | 53 | 55 | 10.4836 | 2.8 | 5 | 135 | 6.94
31 | 54 | 55 | 10.544 | 2.8 | 5.1 | 135 | 6.969
31 | 55 | 55 | 10.6044 | 2.8 | 5.2 | 135 | 6.998
31 | 56 | 55 | 10.6649 | 2.8 | 5.3 | 135 | 7.027
31 | 57 | 55 | 10.7253 | 2.8 | 5.4 | 135 | 7.056
31 | 58 | 55 | 10.7858 | 2.8 | 5.5 | 135 | 7.085
31 | 59 | 55 | 10.8462 | 2.8 | 5.6 | 135 | 7.114
31 | 60 | 55 | 10.9067 | 2.8 | 5.7 | 135 | 7.143
31 | 61 | 55 | 10.9671 | 2.8 | 5.8 | 135 | 7.172
31 | 62 | 55 | 11.0276 | 2.8 | 5.9 | 135 | 7.201
31 | 63 | 55 | 11.088 | 2.8 | 6 | 135 | 7.23
31 | 64 | 55 | 11.1484 | 2.8 | 6.1 | 135 | 7.259
31 | 65 | 55 | 11.2089 | 2.8 | 6.2 | 135 | 7.288
31 | 66 | 55 | 11.2693 | 2.8 | 6.3 | 135 | 7.317
31 | 67 | 55 | 11.3298 | 2.8 | 6.4 | 135 | 7.346
31 | 68 | 55 | 11.3902 | 2.8 | 6.5 | 135 | 7.375
31 | 69 | 55 | 11.4507 | 2.8 | 6.6 | 135 | 7.404
31 | 70 | 55 | 11.5111 | 2.8 | 6.7 | 135 | 7.433
31 | 71 | 55 | 11.5716 | 2.8 | 6.8 | 135 | 7.462
31 | 72 | 55 | 11.632 | 2.8 | 6.9 | 135 | 7.491
31 | 73 | 55 | 11.6924 | 2.8 | 7 | 135 | 7.52
31 | 74 | 55 | 11.7529 | 2.8 | 7.1 | 135 | 7.567
31 | 75 | 55 | 11.8133 | 2.8 | 7.2 | 135 | 7.614
31 | 76 | 55 | 11.8613 | 2.8 | 7.3 | 135 | 7.661
31 | 77 | 55 | 11.9093 | 2.8 | 7.4 | 135 | 7.708
31 | 78 | 55 | 11.9573 | 2.8 | 7.5 | 135 | 7.755
31 | 79 | 55 | 12.0053 | 2.8 | 7.6 | 135 | 7.802
31 | 80 | 55 | 12.0533 | 2.8 | 7.7 | 135 | 7.849
31 | 81 | 55 | 12.1013 | 2.8 | 7.8 | 135 | 7.896
31 | 82 | 55 | 12.1493 | 2.8 | 7.9 | 135 | 7.943
31 | 83 | 55 | 12.1973 | 2.8 | 8 | 135 | 7.99
31 | 84 | 55 | 12.2453 | 2.8 | 8.1 | 135 | 8.037
31 | 85 | 55 | 12.2933 | 2.8 | 8.2 | 135 | 8.084
31 | 86 | 55 | 12.3413 | 2.8 | 8.3 | 135 | 8.131
31 | 87 | 55 | 12.3893 | 2.8 | 8.4 | 135 | 8.178
31 | 88 | 55 | 12.4373 | 2.8 | 8.5 | 135 | 8.225
31 | 89 | 55 | 12.4853 | 2.8 | 8.6 | 135 | 8.272
31 | 90 | 55 | 12.5333 | 2.8 | 8.7 | 135 | 8.319
31 | 91 | 55 | 12.5813 | 2.8 | 8.8 | 135 | 8.366
31 | 92 | 55 | 12.6293 | 2.8 | 8.9 | 135 | 8.413
31 | 93 | 55 | 12.6773 | 2.8 | 9 | 135 | 8.46
31 | 94 | 55 | 12.7253 | 2.8 | 9.1 | 135 | 8.58
31 | 95 | 55 | 12.7733 | 2.8 | 9.2 | 135 | 8.7
31 | 96 | 55 | 12.8213 | 2.8 | 9.3 | 135 | 8.82
31 | 97 | 55 | 12.8693 | 2.8 | 9.4 | 135 | 8.94
31 | 98 | 55 | 12.9173 | 2.8 | 9.5 | 135 | 9.06
31 | 99 | 55 | 12.9653 | 2.8 | 9.6 | 135 | 9.18
31 | 100 | 55 | 13.0133 | 2.8 | 9.7 | 135 | 9.3
31 | 101 | 55 | 13.0571 | 2.8 | 9.8 | 135 | 9.42
31 | 102 | 55 | 13.1008 | 2.8 | 9.9 | 135 | 9.54
31 | 103 | 55 | 13.1445 | 2.8 | 10 | 135 | 9.66
31 | 104 | 55 | 13.1883 | 2.9 | 3 | 135 | 4.78
31 | 105 | 55 | 13.232 | 2.9 | 3.1 | 135 | 4.8895
31 | 106 | 55 | 13.2757 | 2.9 | 3.2 | 135 | 4.999
31 | 107 | 55 | 13.3195 | 2.9 | 3.3 | 135 | 5.1085
31 | 108 | 55 | 13.3632 | 2.9 | 3.4 | 135 | 5.218
31 | 109 | 55 | 13.4069 | 2.9 | 3.5 | 135 | 5.3275
31 | 110 | 55 | 13.4507 | 2.9 | 3.6 | 135 | 5.437
31 | 111 | 55 | 13.4944 | 2.9 | 3.7 | 135 | 5.5465
31 | 112 | 55 | 13.5381 | 2.9 | 3.8 | 135 | 5.656
31 | 113 | 55 | 13.5819 | 2.9 | 3.9 | 135 | 5.7655
31 | 114 | 55 | 13.6256 | 2.9 | 4 | 135 | 5.875
31 | 115 | 55 | 13.6693 | 2.9 | 4.1 | 135 | 5.9845
31 | 116 | 55 | 13.7131 | 2.9 | 4.2 | 135 | 6.094
31 | 117 | 55 | 13.7568 | 2.9 | 4.3 | 135 | 6.2035
31 | 118 | 55 | 13.8005 | 2.9 | 4.4 | 135 | 6.313
31 | 119 | 55 | 13.8443 | 2.9 | 4.5 | 135 | 6.4225
31 | 120 | 55 | 13.888 | 2.9 | 4.6 | 135 | 6.532
31 | 121 | 55 | 13.9317 | 2.9 | 4.7 | 135 | 6.6415
31 | 122 | 55 | 13.9755 | 2.9 | 4.8 | 135 | 6.751
31 | 123 | 55 | 14.0192 | 2.9 | 4.9 | 135 | 6.8605
31 | 124 | 55 | 14.0629 | 2.9 | 5 | 135 | 6.97
31 | 125 | 55 | 14.1067 | 2.9 | 5.1 | 135 | 6.9995
31 | 126 | 55 | 14.1507 | 2.9 | 5.2 | 135 | 7.029
31 | 127 | 55 | 14.1947 | 2.9 | 5.3 | 135 | 7.0585
31 | 128 | 55 | 14.2387 | 2.9 | 5.4 | 135 | 7.088
31 | 129 | 55 | 14.2827 | 2.9 | 5.5 | 135 | 7.1175
31 | 130 | 55 | 14.3267 | 2.9 | 5.6 | 135 | 7.147
31 | 131 | 55 | 14.3707 | 2.9 | 5.7 | 135 | 7.1765
31 | 132 | 55 | 14.4147 | 2.9 | 5.8 | 135 | 7.206
31 | 133 | 55 | 14.4587 | 2.9 | 5.9 | 135 | 7.2355
31 | 134 | 55 | 14.5027 | 2.9 | 6 | 135 | 7.265
31 | 135 | 55 | 14.5467 | 2.9 | 6.1 | 135 | 7.2945
31 | 136 | 55 | 14.5907 | 2.9 | 6.2 | 135 | 7.324
31 | 137 | 55 | 14.6347 | 2.9 | 6.3 | 135 | 7.3535
31 | 138 | 55 | 14.6787 | 2.9 | 6.4 | 135 | 7.383
31 | 139 | 55 | 14.7227 | 2.9 | 6.5 | 135 | 7.4125
31 | 140 | 55 | 14.7667 | 2.9 | 6.6 | 135 | 7.442
31 | 141 | 55 | 14.8107 | 2.9 | 6.7 | 135 | 7.4715
31 | 142 | 55 | 14.8547 | 2.9 | 6.8 | 135 | 7.501
31 | 143 | 55 | 14.8987 | 2.9 | 6.9 | 135 | 7.5305
31 | 144 | 55 | 14.9427 | 2.9 | 7 | 135 | 7.56
31 | 145 | 55 | 14.9867 | 2.9 | 7.1 | 135 | 7.606
31 | 146 | 55 | 15.0307 | 2.9 | 7.2 | 135 | 7.652
31 | 147 | 55 | 15.0747 | 2.9 | 7.3 | 135 | 7.698
31 | 148 | 55 | 15.1187 | 2.9 | 7.4 | 135 | 7.744
31 | 149 | 55 | 15.1627 | 2.9 | 7.5 | 135 | 7.79
31 | 150 | 55 | 15.2067 | 2.9 | 7.6 | 135 | 7.836
32 | 45 | 55 | 10 | 2.9 | 7.7 | 135 | 7.882
32 | 46 | 55 | 10.0609 | 2.9 | 7.8 | 135 | 7.928
32 | 47 | 55 | 10.1218 | 2.9 | 7.9 | 135 | 7.974
32 | 48 | 55 | 10.1827 | 2.9 | 8 | 135 | 8.02
32 | 49 | 55 | 10.2436 | 2.9 | 8.1 | 135 | 8.066
32 | 50 | 55 | 10.3044 | 2.9 | 8.2 | 135 | 8.112
32 | 51 | 55 | 10.3653 | 2.9 | 8.3 | 135 | 8.158
32 | 52 | 55 | 10.4262 | 2.9 | 8.4 | 135 | 8.204
32 | 53 | 55 | 10.4871 | 2.9 | 8.5 | 135 | 8.25
32 | 54 | 55 | 10.548 | 2.9 | 8.6 | 135 | 8.296
32 | 55 | 55 | 10.6089 | 2.9 | 8.7 | 135 | 8.342
32 | 56 | 55 | 10.6698 | 2.9 | 8.8 | 135 | 8.388
32 | 57 | 55 | 10.7307 | 2.9 | 8.9 | 135 | 8.434
32 | 58 | 55 | 10.7916 | 2.9 | 9 | 135 | 8.48
32 | 59 | 55 | 10.8524 | 2.9 | 9.1 | 135 | 8.6
32 | 60 | 55 | 10.9133 | 2.9 | 9.2 | 135 | 8.72
32 | 61 | 55 | 10.9742 | 2.9 | 9.3 | 135 | 8.84
32 | 62 | 55 | 11.0351 | 2.9 | 9.4 | 135 | 8.96
32 | 63 | 55 | 11.096 | 2.9 | 9.5 | 135 | 9.08
32 | 64 | 55 | 11.1569 | 2.9 | 9.6 | 135 | 9.2
32 | 65 | 55 | 11.2178 | 2.9 | 9.7 | 135 | 9.32
32 | 66 | 55 | 11.2787 | 2.9 | 9.8 | 135 | 9.44
32 | 67 | 55 | 11.3396 | 2.9 | 9.9 | 135 | 9.56
32 | 68 | 55 | 11.4004 | 2.9 | 10 | 135 | 9.68
32 | 69 | 55 | 11.4613 | 3 | 3 | 135 | 4.8
32 | 70 | 55 | 11.5222 | 3 | 3.1 | 135 | 4.91
32 | 71 | 55 | 11.5831 | 3 | 3.2 | 135 | 5.02
32 | 72 | 55 | 11.644 | 3 | 3.3 | 135 | 5.13
32 | 73 | 55 | 11.7049 | 3 | 3.4 | 135 | 5.24
32 | 74 | 55 | 11.7658 | 3 | 3.5 | 135 | 5.35
32 | 75 | 55 | 11.8267 | 3 | 3.6 | 135 | 5.46
32 | 76 | 55 | 11.8747 | 3 | 3.7 | 135 | 5.57
32 | 77 | 55 | 11.9227 | 3 | 3.8 | 135 | 5.68
32 | 78 | 55 | 11.9707 | 3 | 3.9 | 135 | 5.79
32 | 79 | 55 | 12.0187 | 3 | 4 | 135 | 5.9
32 | 80 | 55 | 12.0667 | 3 | 4.1 | 135 | 6.01
32 | 81 | 55 | 12.1147 | 3 | 4.2 | 135 | 6.12
32 | 82 | 55 | 12.1627 | 3 | 4.3 | 135 | 6.23
32 | 83 | 55 | 12.2107 | 3 | 4.4 | 135 | 6.34
32 | 84 | 55 | 12.2587 | 3 | 4.5 | 135 | 6.45
32 | 85 | 55 | 12.3067 | 3 | 4.6 | 135 | 6.56
32 | 86 | 55 | 12.3547 | 3 | 4.7 | 135 | 6.67
32 | 87 | 55 | 12.4027 | 3 | 4.8 | 135 | 6.78
32 | 88 | 55 | 12.4507 | 3 | 4.9 | 135 | 6.89
32 | 89 | 55 | 12.4987 | 3 | 5 | 135 | 7
32 | 90 | 55 | 12.5467 | 3 | 5.1 | 135 | 7.03
32 | 91 | 55 | 12.5947 | 3 | 5.2 | 135 | 7.06
32 | 92 | 55 | 12.6427 | 3 | 5.3 | 135 | 7.09
32 | 93 | 55 | 12.6907 | 3 | 5.4 | 135 | 7.12
32 | 94 | 55 | 12.7387 | 3 | 5.5 | 135 | 7.15
32 | 95 | 55 | 12.7867 | 3 | 5.6 | 135 | 7.18
32 | 96 | 55 | 12.8347 | 3 | 5.7 | 135 | 7.21
32 | 97 | 55 | 12.8827 | 3 | 5.8 | 135 | 7.24
32 | 98 | 55 | 12.9307 | 3 | 5.9 | 135 | 7.27
32 | 99 | 55 | 12.9787 | 3 | 6 | 135 | 7.3
32 | 100 | 55 | 13.0267 | 3 | 6.1 | 135 | 7.33
32 | 101 | 55 | 13.0701 | 3 | 6.2 | 135 | 7.36
32 | 102 | 55 | 13.1136 | 3 | 6.3 | 135 | 7.39
32 | 103 | 55 | 13.1571 | 3 | 6.4 | 135 | 7.42
32 | 104 | 55 | 13.2005 | 3 | 6.5 | 135 | 7.45
32 | 105 | 55 | 13.244 | 3 | 6.6 | 135 | 7.48
32 | 106 | 55 | 13.2875 | 3 | 6.7 | 135 | 7.51
32 | 107 | 55 | 13.3309 | 3 | 6.8 | 135 | 7.54
32 | 108 | 55 | 13.3744 | 3 | 6.9 | 135 | 7.57
32 | 109 | 55 | 13.4179 | 3 | 7 | 135 | 7.6
32 | 110 | 55 | 13.4613 | 3 | 7.1 | 135 | 7.645
32 | 111 | 55 | 13.5048 | 3 | 7.2 | 135 | 7.69
32 | 112 | 55 | 13.5483 | 3 | 7.3 | 135 | 7.735
32 | 113 | 55 | 13.5917 | 3 | 7.4 | 135 | 7.78
32 | 114 | 55 | 13.6352 | 3 | 7.5 | 135 | 7.825
32 | 115 | 55 | 13.6787 | 3 | 7.6 | 135 | 7.87
32 | 116 | 55 | 13.7221 | 3 | 7.7 | 135 | 7.915
32 | 117 | 55 | 13.7656 | 3 | 7.8 | 135 | 7.96
32 | 118 | 55 | 13.8091 | 3 | 7.9 | 135 | 8.005
32 | 119 | 55 | 13.8525 | 3 | 8 | 135 | 8.05
32 | 120 | 55 | 13.896 | 3 | 8.1 | 135 | 8.095
32 | 121 | 55 | 13.9395 | 3 | 8.2 | 135 | 8.14
32 | 122 | 55 | 13.9829 | 3 | 8.3 | 135 | 8.185
32 | 123 | 55 | 14.0264 | 3 | 8.4 | 135 | 8.23
32 | 124 | 55 | 14.0699 | 3 | 8.5 | 135 | 8.275
32 | 125 | 55 | 14.1133 | 3 | 8.6 | 135 | 8.32
32 | 126 | 55 | 14.1573 | 3 | 8.7 | 135 | 8.365
32 | 127 | 55 | 14.2013 | 3 | 8.8 | 135 | 8.41
32 | 128 | 55 | 14.2453 | 3 | 8.9 | 135 | 8.455
32 | 129 | 55 | 14.2893 | 3 | 9 | 135 | 8.5
32 | 130 | 55 | 14.3333 | 3 | 9.1 | 135 | 8.62
32 | 131 | 55 | 14.3773 | 3 | 9.2 | 135 | 8.74
32 | 132 | 55 | 14.4213 | 3 | 9.3 | 135 | 8.86
32 | 133 | 55 | 14.4653 | 3 | 9.4 | 135 | 8.98
32 | 134 | 55 | 14.5093 | 3 | 9.5 | 135 | 9.1
32 | 135 | 55 | 14.5533 | 3 | 9.6 | 135 | 9.22
32 | 136 | 55 | 14.5973 | 3 | 9.7 | 135 | 9.34
32 | 137 | 55 | 14.6413 | 3 | 9.8 | 135 | 9.46
32 | 138 | 55 | 14.6853 | 3 | 9.9 | 135 | 9.58
32 | 139 | 55 | 14.7293 | 3 | 10 | 135 | 9.7
32 | 140 | 55 | 14.7733 | 3.1 | 3 | 135 | 4.8
32 | 141 | 55 | 14.8173 | 3.1 | 3.1 | 135 | 4.911
32 | 142 | 55 | 14.8613 | 3.1 | 3.2 | 135 | 5.022
32 | 143 | 55 | 14.9053 | 3.1 | 3.3 | 135 | 5.133
32 | 144 | 55 | 14.9493 | 3.1 | 3.4 | 135 | 5.244
32 | 145 | 55 | 14.9933 | 3.1 | 3.5 | 135 | 5.355
32 | 146 | 55 | 15.0373 | 3.1 | 3.6 | 135 | 5.466
32 | 147 | 55 | 15.0813 | 3.1 | 3.7 | 135 | 5.577
32 | 148 | 55 | 15.1253 | 3.1 | 3.8 | 135 | 5.688
32 | 149 | 55 | 15.1693 | 3.1 | 3.9 | 135 | 5.799
32 | 150 | 55 | 15.2133 | 3.1 | 4 | 135 | 5.91
33 | 45 | 55 | 10 | 3.1 | 4.1 | 135 | 6.021
33 | 46 | 55 | 10.0613 | 3.1 | 4.2 | 135 | 6.132
33 | 47 | 55 | 10.1227 | 3.1 | 4.3 | 135 | 6.243
33 | 48 | 55 | 10.184 | 3.1 | 4.4 | 135 | 6.354
33 | 49 | 55 | 10.2453 | 3.1 | 4.5 | 135 | 6.465
33 | 50 | 55 | 10.3067 | 3.1 | 4.6 | 135 | 6.576
33 | 51 | 55 | 10.368 | 3.1 | 4.7 | 135 | 6.687
33 | 52 | 55 | 10.4293 | 3.1 | 4.8 | 135 | 6.798
33 | 53 | 55 | 10.4907 | 3.1 | 4.9 | 135 | 6.909
33 | 54 | 55 | 10.552 | 3.1 | 5 | 135 | 7.02
33 | 55 | 55 | 10.6133 | 3.1 | 5.1 | 135 | 7.05
33 | 56 | 55 | 10.6747 | 3.1 | 5.2 | 135 | 7.08
33 | 57 | 55 | 10.736 | 3.1 | 5.3 | 135 | 7.11
33 | 58 | 55 | 10.7973 | 3.1 | 5.4 | 135 | 7.14
33 | 59 | 55 | 10.8587 | 3.1 | 5.5 | 135 | 7.17
33 | 60 | 55 | 10.92 | 3.1 | 5.6 | 135 | 7.2
33 | 61 | 55 | 10.9813 | 3.1 | 5.7 | 135 | 7.23
33 | 62 | 55 | 11.0427 | 3.1 | 5.8 | 135 | 7.26
33 | 63 | 55 | 11.104 | 3.1 | 5.9 | 135 | 7.29
33 | 64 | 55 | 11.1653 | 3.1 | 6 | 135 | 7.32
33 | 65 | 55 | 11.2267 | 3.1 | 6.1 | 135 | 7.35
33 | 66 | 55 | 11.288 | 3.1 | 6.2 | 135 | 7.38
33 | 67 | 55 | 11.3493 | 3.1 | 6.3 | 135 | 7.41
33 | 68 | 55 | 11.4107 | 3.1 | 6.4 | 135 | 7.44
33 | 69 | 55 | 11.472 | 3.1 | 6.5 | 135 | 7.47
33 | 70 | 55 | 11.5333 | 3.1 | 6.6 | 135 | 7.5
33 | 71 | 55 | 11.5947 | 3.1 | 6.7 | 135 | 7.53
33 | 72 | 55 | 11.656 | 3.1 | 6.8 | 135 | 7.56
33 | 73 | 55 | 11.7173 | 3.1 | 6.9 | 135 | 7.59
33 | 74 | 55 | 11.7787 | 3.1 | 7 | 135 | 7.62
33 | 75 | 55 | 11.84 | 3.1 | 7.1 | 135 | 7.6645
33 | 76 | 55 | 11.888 | 3.1 | 7.2 | 135 | 7.709
33 | 77 | 55 | 11.936 | 3.1 | 7.3 | 135 | 7.7535
33 | 78 | 55 | 11.984 | 3.1 | 7.4 | 135 | 7.798
33 | 79 | 55 | 12.032 | 3.1 | 7.5 | 135 | 7.8425
33 | 80 | 55 | 12.08 | 3.1 | 7.6 | 135 | 7.887
33 | 81 | 55 | 12.128 | 3.1 | 7.7 | 135 | 7.9315
33 | 82 | 55 | 12.176 | 3.1 | 7.8 | 135 | 7.976
33 | 83 | 55 | 12.224 | 3.1 | 7.9 | 135 | 8.0205
33 | 84 | 55 | 12.272 | 3.1 | 8 | 135 | 8.065
33 | 85 | 55 | 12.32 | 3.1 | 8.1 | 135 | 8.1095
33 | 86 | 55 | 12.368 | 3.1 | 8.2 | 135 | 8.154
33 | 87 | 55 | 12.416 | 3.1 | 8.3 | 135 | 8.1985
33 | 88 | 55 | 12.464 | 3.1 | 8.4 | 135 | 8.243
33 | 89 | 55 | 12.512 | 3.1 | 8.5 | 135 | 8.2875
33 | 90 | 55 | 12.56 | 3.1 | 8.6 | 135 | 8.332
33 | 91 | 55 | 12.608 | 3.1 | 8.7 | 135 | 8.3765
33 | 92 | 55 | 12.656 | 3.1 | 8.8 | 135 | 8.421
33 | 93 | 55 | 12.704 | 3.1 | 8.9 | 135 | 8.4655
33 | 94 | 55 | 12.752 | 3.1 | 9 | 135 | 8.51
33 | 95 | 55 | 12.8 | 3.1 | 9.1 | 135 | 8.63
33 | 96 | 55 | 12.848 | 3.1 | 9.2 | 135 | 8.75
33 | 97 | 55 | 12.896 | 3.1 | 9.3 | 135 | 8.87
33 | 98 | 55 | 12.944 | 3.1 | 9.4 | 135 | 8.99
33 | 99 | 55 | 12.992 | 3.1 | 9.5 | 135 | 9.11
33 | 100 | 55 | 13.04 | 3.1 | 9.6 | 135 | 9.23
33 | 101 | 55 | 13.0832 | 3.1 | 9.7 | 135 | 9.35
33 | 102 | 55 | 13.1264 | 3.1 | 9.8 | 135 | 9.47
33 | 103 | 55 | 13.1696 | 3.1 | 9.9 | 135 | 9.59
33 | 104 | 55 | 13.2128 | 3.1 | 10 | 135 | 9.71
33 | 105 | 55 | 13.256 | 3.2 | 3 | 135 | 4.8
33 | 106 | 55 | 13.2992 | 3.2 | 3.1 | 135 | 4.912
33 | 107 | 55 | 13.3424 | 3.2 | 3.2 | 135 | 5.024
33 | 108 | 55 | 13.3856 | 3.2 | 3.3 | 135 | 5.136
33 | 109 | 55 | 13.4288 | 3.2 | 3.4 | 135 | 5.248
33 | 110 | 55 | 13.472 | 3.2 | 3.5 | 135 | 5.36
33 | 111 | 55 | 13.5152 | 3.2 | 3.6 | 135 | 5.472
33 | 112 | 55 | 13.5584 | 3.2 | 3.7 | 135 | 5.584
33 | 113 | 55 | 13.6016 | 3.2 | 3.8 | 135 | 5.696
33 | 114 | 55 | 13.6448 | 3.2 | 3.9 | 135 | 5.808
33 | 115 | 55 | 13.688 | 3.2 | 4 | 135 | 5.92
33 | 116 | 55 | 13.7312 | 3.2 | 4.1 | 135 | 6.032
33 | 117 | 55 | 13.7744 | 3.2 | 4.2 | 135 | 6.144
33 | 118 | 55 | 13.8176 | 3.2 | 4.3 | 135 | 6.256
33 | 119 | 55 | 13.8608 | 3.2 | 4.4 | 135 | 6.368
33 | 120 | 55 | 13.904 | 3.2 | 4.5 | 135 | 6.48
33 | 121 | 55 | 13.9472 | 3.2 | 4.6 | 135 | 6.592
33 | 122 | 55 | 13.9904 | 3.2 | 4.7 | 135 | 6.704
33 | 123 | 55 | 14.0336 | 3.2 | 4.8 | 135 | 6.816
33 | 124 | 55 | 14.0768 | 3.2 | 4.9 | 135 | 6.928
33 | 125 | 55 | 14.12 | 3.2 | 5 | 135 | 7.04
33 | 126 | 55 | 14.164 | 3.2 | 5.1 | 135 | 7.07
33 | 127 | 55 | 14.208 | 3.2 | 5.2 | 135 | 7.1
33 | 128 | 55 | 14.252 | 3.2 | 5.3 | 135 | 7.13
33 | 129 | 55 | 14.296 | 3.2 | 5.4 | 135 | 7.16
33 | 130 | 55 | 14.34 | 3.2 | 5.5 | 135 | 7.19
33 | 131 | 55 | 14.384 | 3.2 | 5.6 | 135 | 7.22
33 | 132 | 55 | 14.428 | 3.2 | 5.7 | 135 | 7.25
33 | 133 | 55 | 14.472 | 3.2 | 5.8 | 135 | 7.28
33 | 134 | 55 | 14.516 | 3.2 | 5.9 | 135 | 7.31
33 | 135 | 55 | 14.56 | 3.2 | 6 | 135 | 7.34
33 | 136 | 55 | 14.604 | 3.2 | 6.1 | 135 | 7.37
33 | 137 | 55 | 14.648 | 3.2 | 6.2 | 135 | 7.4
33 | 138 | 55 | 14.692 | 3.2 | 6.3 | 135 | 7.43
33 | 139 | 55 | 14.736 | 3.2 | 6.4 | 135 | 7.46
33 | 140 | 55 | 14.78 | 3.2 | 6.5 | 135 | 7.49
33 | 141 | 55 | 14.824 | 3.2 | 6.6 | 135 | 7.52
33 | 142 | 55 | 14.868 | 3.2 | 6.7 | 135 | 7.55
33 | 143 | 55 | 14.912 | 3.2 | 6.8 | 135 | 7.58
33 | 144 | 55 | 14.956 | 3.2 | 6.9 | 135 | 7.61
33 | 145 | 55 | 15 | 3.2 | 7 | 135 | 7.64
33 | 146 | 55 | 15.044 | 3.2 | 7.1 | 135 | 7.684
33 | 147 | 55 | 15.088 | 3.2 | 7.2 | 135 | 7.728
33 | 148 | 55 | 15.132 | 3.2 | 7.3 | 135 | 7.772
33 | 149 | 55 | 15.176 | 3.2 | 7.4 | 135 | 7.816
33 | 150 | 55 | 15.22 | 3.2 | 7.5 | 135 | 7.86
34 | 45 | 55 | 10 | 3.2 | 7.6 | 135 | 7.904
34 | 46 | 55 | 10.0618 | 3.2 | 7.7 | 135 | 7.948
34 | 47 | 55 | 10.1236 | 3.2 | 7.8 | 135 | 7.992
34 | 48 | 55 | 10.1853 | 3.2 | 7.9 | 135 | 8.036
34 | 49 | 55 | 10.2471 | 3.2 | 8 | 135 | 8.08
34 | 50 | 55 | 10.3089 | 3.2 | 8.1 | 135 | 8.124
34 | 51 | 55 | 10.3707 | 3.2 | 8.2 | 135 | 8.168
34 | 52 | 55 | 10.4324 | 3.2 | 8.3 | 135 | 8.212
34 | 53 | 55 | 10.4942 | 3.2 | 8.4 | 135 | 8.256
34 | 54 | 55 | 10.556 | 3.2 | 8.5 | 135 | 8.3
34 | 55 | 55 | 10.6178 | 3.2 | 8.6 | 135 | 8.344
34 | 56 | 55 | 10.6796 | 3.2 | 8.7 | 135 | 8.388
34 | 57 | 55 | 10.7413 | 3.2 | 8.8 | 135 | 8.432
34 | 58 | 55 | 10.8031 | 3.2 | 8.9 | 135 | 8.476
34 | 59 | 55 | 10.8649 | 3.2 | 9 | 135 | 8.52
34 | 60 | 55 | 10.9267 | 3.2 | 9.1 | 135 | 8.64
34 | 61 | 55 | 10.9884 | 3.2 | 9.2 | 135 | 8.76
34 | 62 | 55 | 11.0502 | 3.2 | 9.3 | 135 | 8.88
34 | 63 | 55 | 11.112 | 3.2 | 9.4 | 135 | 9
34 | 64 | 55 | 11.1738 | 3.2 | 9.5 | 135 | 9.12
34 | 65 | 55 | 11.2356 | 3.2 | 9.6 | 135 | 9.24
34 | 66 | 55 | 11.2973 | 3.2 | 9.7 | 135 | 9.36
34 | 67 | 55 | 11.3591 | 3.2 | 9.8 | 135 | 9.48
34 | 68 | 55 | 11.4209 | 3.2 | 9.9 | 135 | 9.6
34 | 69 | 55 | 11.4827 | 3.2 | 10 | 135 | 9.72
34 | 70 | 55 | 11.5444 | 3.3 | 3 | 135 | 4.8
34 | 71 | 55 | 11.6062 | 3.3 | 3.1 | 135 | 4.913
34 | 72 | 55 | 11.668 | 3.3 | 3.2 | 135 | 5.026
34 | 73 | 55 | 11.7298 | 3.3 | 3.3 | 135 | 5.139
34 | 74 | 55 | 11.7916 | 3.3 | 3.4 | 135 | 5.252
34 | 75 | 55 | 11.8533 | 3.3 | 3.5 | 135 | 5.365
34 | 76 | 55 | 11.9013 | 3.3 | 3.6 | 135 | 5.478
34 | 77 | 55 | 11.9493 | 3.3 | 3.7 | 135 | 5.591
34 | 78 | 55 | 11.9973 | 3.3 | 3.8 | 135 | 5.704
34 | 79 | 55 | 12.0453 | 3.3 | 3.9 | 135 | 5.817
34 | 80 | 55 | 12.0933 | 3.3 | 4 | 135 | 5.93
34 | 81 | 55 | 12.1413 | 3.3 | 4.1 | 135 | 6.043
34 | 82 | 55 | 12.1893 | 3.3 | 4.2 | 135 | 6.156
34 | 83 | 55 | 12.2373 | 3.3 | 4.3 | 135 | 6.269
34 | 84 | 55 | 12.2853 | 3.3 | 4.4 | 135 | 6.382
34 | 85 | 55 | 12.3333 | 3.3 | 4.5 | 135 | 6.495
34 | 86 | 55 | 12.3813 | 3.3 | 4.6 | 135 | 6.608
34 | 87 | 55 | 12.4293 | 3.3 | 4.7 | 135 | 6.721
34 | 88 | 55 | 12.4773 | 3.3 | 4.8 | 135 | 6.834
34 | 89 | 55 | 12.5253 | 3.3 | 4.9 | 135 | 6.947
34 | 90 | 55 | 12.5733 | 3.3 | 5 | 135 | 7.06
34 | 91 | 55 | 12.6213 | 3.3 | 5.1 | 135 | 7.09
34 | 92 | 55 | 12.6693 | 3.3 | 5.2 | 135 | 7.12
34 | 93 | 55 | 12.7173 | 3.3 | 5.3 | 135 | 7.15
34 | 94 | 55 | 12.7653 | 3.3 | 5.4 | 135 | 7.18
34 | 95 | 55 | 12.8133 | 3.3 | 5.5 | 135 | 7.21
34 | 96 | 55 | 12.8613 | 3.3 | 5.6 | 135 | 7.24
34 | 97 | 55 | 12.9093 | 3.3 | 5.7 | 135 | 7.27
34 | 98 | 55 | 12.9573 | 3.3 | 5.8 | 135 | 7.3
34 | 99 | 55 | 13.0053 | 3.3 | 5.9 | 135 | 7.33
34 | 100 | 55 | 13.0533 | 3.3 | 6 | 135 | 7.36
34 | 101 | 55 | 13.0963 | 3.3 | 6.1 | 135 | 7.39
34 | 102 | 55 | 13.1392 | 3.3 | 6.2 | 135 | 7.42
34 | 103 | 55 | 13.1821 | 3.3 | 6.3 | 135 | 7.45
34 | 104 | 55 | 13.2251 | 3.3 | 6.4 | 135 | 7.48
34 | 105 | 55 | 13.268 | 3.3 | 6.5 | 135 | 7.51
34 | 106 | 55 | 13.3109 | 3.3 | 6.6 | 135 | 7.54
34 | 107 | 55 | 13.3539 | 3.3 | 6.7 | 135 | 7.57
34 | 108 | 55 | 13.3968 | 3.3 | 6.8 | 135 | 7.6
34 | 109 | 55 | 13.4397 | 3.3 | 6.9 | 135 | 7.63
34 | 110 | 55 | 13.4827 | 3.3 | 7 | 135 | 7.66
34 | 111 | 55 | 13.5256 | 3.3 | 7.1 | 135 | 7.7035
34 | 112 | 55 | 13.5685 | 3.3 | 7.2 | 135 | 7.747
34 | 113 | 55 | 13.6115 | 3.3 | 7.3 | 135 | 7.7905
34 | 114 | 55 | 13.6544 | 3.3 | 7.4 | 135 | 7.834
34 | 115 | 55 | 13.6973 | 3.3 | 7.5 | 135 | 7.8775
34 | 116 | 55 | 13.7403 | 3.3 | 7.6 | 135 | 7.921
34 | 117 | 55 | 13.7832 | 3.3 | 7.7 | 135 | 7.9645
34 | 118 | 55 | 13.8261 | 3.3 | 7.8 | 135 | 8.008
34 | 119 | 55 | 13.8691 | 3.3 | 7.9 | 135 | 8.0515
34 | 120 | 55 | 13.912 | 3.3 | 8 | 135 | 8.095
34 | 121 | 55 | 13.9549 | 3.3 | 8.1 | 135 | 8.1385
34 | 122 | 55 | 13.9979 | 3.3 | 8.2 | 135 | 8.182
34 | 123 | 55 | 14.0408 | 3.3 | 8.3 | 135 | 8.2255
34 | 124 | 55 | 14.0837 | 3.3 | 8.4 | 135 | 8.269
34 | 125 | 55 | 14.1267 | 3.3 | 8.5 | 135 | 8.3125
34 | 126 | 55 | 14.1707 | 3.3 | 8.6 | 135 | 8.356
34 | 127 | 55 | 14.2147 | 3.3 | 8.7 | 135 | 8.3995
34 | 128 | 55 | 14.2587 | 3.3 | 8.8 | 135 | 8.443
34 | 129 | 55 | 14.3027 | 3.3 | 8.9 | 135 | 8.4865
34 | 130 | 55 | 14.3467 | 3.3 | 9 | 135 | 8.53
34 | 131 | 55 | 14.3907 | 3.3 | 9.1 | 135 | 8.65
34 | 132 | 55 | 14.4347 | 3.3 | 9.2 | 135 | 8.77
34 | 133 | 55 | 14.4787 | 3.3 | 9.3 | 135 | 8.89
34 | 134 | 55 | 14.5227 | 3.3 | 9.4 | 135 | 9.01
34 | 135 | 55 | 14.5667 | 3.3 | 9.5 | 135 | 9.13
34 | 136 | 55 | 14.6107 | 3.3 | 9.6 | 135 | 9.25
34 | 137 | 55 | 14.6547 | 3.3 | 9.7 | 135 | 9.37
34 | 138 | 55 | 14.6987 | 3.3 | 9.8 | 135 | 9.49
34 | 139 | 55 | 14.7427 | 3.3 | 9.9 | 135 | 9.61
34 | 140 | 55 | 14.7867 | 3.3 | 10 | 135 | 9.73
34 | 141 | 55 | 14.8307 | 3.4 | 3 | 135 | 4.8
34 | 142 | 55 | 14.8747 | 3.4 | 3.1 | 135 | 4.914
34 | 143 | 55 | 14.9187 | 3.4 | 3.2 | 135 | 5.028
34 | 144 | 55 | 14.9627 | 3.4 | 3.3 | 135 | 5.142
34 | 145 | 55 | 15.0067 | 3.4 | 3.4 | 135 | 5.256
34 | 146 | 55 | 15.0507 | 3.4 | 3.5 | 135 | 5.37
34 | 147 | 55 | 15.0947 | 3.4 | 3.6 | 135 | 5.484
34 | 148 | 55 | 15.1387 | 3.4 | 3.7 | 135 | 5.598
34 | 149 | 55 | 15.1827 | 3.4 | 3.8 | 135 | 5.712
34 | 150 | 55 | 15.2267 | 3.4 | 3.9 | 135 | 5.826
35 | 45 | 55 | 10 | 3.4 | 4 | 135 | 5.94
35 | 46 | 55 | 10.0622 | 3.4 | 4.1 | 135 | 6.054
35 | 47 | 55 | 10.1244 | 3.4 | 4.2 | 135 | 6.168
35 | 48 | 55 | 10.1867 | 3.4 | 4.3 | 135 | 6.282
35 | 49 | 55 | 10.2489 | 3.4 | 4.4 | 135 | 6.396
35 | 50 | 55 | 10.3111 | 3.4 | 4.5 | 135 | 6.51
35 | 51 | 55 | 10.3733 | 3.4 | 4.6 | 135 | 6.624
35 | 52 | 55 | 10.4356 | 3.4 | 4.7 | 135 | 6.738
35 | 53 | 55 | 10.4978 | 3.4 | 4.8 | 135 | 6.852
35 | 54 | 55 | 10.56 | 3.4 | 4.9 | 135 | 6.966
35 | 55 | 55 | 10.6222 | 3.4 | 5 | 135 | 7.08
35 | 56 | 55 | 10.6844 | 3.4 | 5.1 | 135 | 7.11
35 | 57 | 55 | 10.7467 | 3.4 | 5.2 | 135 | 7.14
35 | 58 | 55 | 10.8089 | 3.4 | 5.3 | 135 | 7.17
35 | 59 | 55 | 10.8711 | 3.4 | 5.4 | 135 | 7.2
35 | 60 | 55 | 10.9333 | 3.4 | 5.5 | 135 | 7.23
35 | 61 | 55 | 10.9956 | 3.4 | 5.6 | 135 | 7.26
35 | 62 | 55 | 11.0578 | 3.4 | 5.7 | 135 | 7.29
35 | 63 | 55 | 11.12 | 3.4 | 5.8 | 135 | 7.32
35 | 64 | 55 | 11.1822 | 3.4 | 5.9 | 135 | 7.35
35 | 65 | 55 | 11.2444 | 3.4 | 6 | 135 | 7.38
35 | 66 | 55 | 11.3067 | 3.4 | 6.1 | 135 | 7.41
35 | 67 | 55 | 11.3689 | 3.4 | 6.2 | 135 | 7.44
35 | 68 | 55 | 11.4311 | 3.4 | 6.3 | 135 | 7.47
35 | 69 | 55 | 11.4933 | 3.4 | 6.4 | 135 | 7.5
35 | 70 | 55 | 11.5556 | 3.4 | 6.5 | 135 | 7.53
35 | 71 | 55 | 11.6178 | 3.4 | 6.6 | 135 | 7.56
35 | 72 | 55 | 11.68 | 3.4 | 6.7 | 135 | 7.59
35 | 73 | 55 | 11.7422 | 3.4 | 6.8 | 135 | 7.62
35 | 74 | 55 | 11.8044 | 3.4 | 6.9 | 135 | 7.65
35 | 75 | 55 | 11.8667 | 3.4 | 7 | 135 | 7.68
35 | 76 | 55 | 11.9147 | 3.4 | 7.1 | 135 | 7.723
35 | 77 | 55 | 11.9627 | 3.4 | 7.2 | 135 | 7.766
35 | 78 | 55 | 12.0107 | 3.4 | 7.3 | 135 | 7.809
35 | 79 | 55 | 12.0587 | 3.4 | 7.4 | 135 | 7.852
35 | 80 | 55 | 12.1067 | 3.4 | 7.5 | 135 | 7.895
35 | 81 | 55 | 12.1547 | 3.4 | 7.6 | 135 | 7.938
35 | 82 | 55 | 12.2027 | 3.4 | 7.7 | 135 | 7.981
35 | 83 | 55 | 12.2507 | 3.4 | 7.8 | 135 | 8.024
35 | 84 | 55 | 12.2987 | 3.4 | 7.9 | 135 | 8.067
35 | 85 | 55 | 12.3467 | 3.4 | 8 | 135 | 8.11
35 | 86 | 55 | 12.3947 | 3.4 | 8.1 | 135 | 8.153
35 | 87 | 55 | 12.4427 | 3.4 | 8.2 | 135 | 8.196
35 | 88 | 55 | 12.4907 | 3.4 | 8.3 | 135 | 8.239
35 | 89 | 55 | 12.5387 | 3.4 | 8.4 | 135 | 8.282
35 | 90 | 55 | 12.5867 | 3.4 | 8.5 | 135 | 8.325
35 | 91 | 55 | 12.6347 | 3.4 | 8.6 | 135 | 8.368
35 | 92 | 55 | 12.6827 | 3.4 | 8.7 | 135 | 8.411
35 | 93 | 55 | 12.7307 | 3.4 | 8.8 | 135 | 8.454
35 | 94 | 55 | 12.7787 | 3.4 | 8.9 | 135 | 8.497
35 | 95 | 55 | 12.8267 | 3.4 | 9 | 135 | 8.54
35 | 96 | 55 | 12.8747 | 3.4 | 9.1 | 135 | 8.66
35 | 97 | 55 | 12.9227 | 3.4 | 9.2 | 135 | 8.78
35 | 98 | 55 | 12.9707 | 3.4 | 9.3 | 135 | 8.9
35 | 99 | 55 | 13.0187 | 3.4 | 9.4 | 135 | 9.02
35 | 100 | 55 | 13.0667 | 3.4 | 9.5 | 135 | 9.14
35 | 101 | 55 | 13.1093 | 3.4 | 9.6 | 135 | 9.26
35 | 102 | 55 | 13.152 | 3.4 | 9.7 | 135 | 9.38
35 | 103 | 55 | 13.1947 | 3.4 | 9.8 | 135 | 9.5
35 | 104 | 55 | 13.2373 | 3.4 | 9.9 | 135 | 9.62
35 | 105 | 55 | 13.28 | 3.4 | 10 | 135 | 9.74
35 | 106 | 55 | 13.3227 | 3.5 | 3 | 135 | 4.8
35 | 107 | 55 | 13.3653 | 3.5 | 3.1 | 135 | 4.915
35 | 108 | 55 | 13.408 | 3.5 | 3.2 | 135 | 5.03
35 | 109 | 55 | 13.4507 | 3.5 | 3.3 | 135 | 5.145
35 | 110 | 55 | 13.4933 | 3.5 | 3.4 | 135 | 5.26
35 | 111 | 55 | 13.536 | 3.5 | 3.5 | 135 | 5.375
35 | 112 | 55 | 13.5787 | 3.5 | 3.6 | 135 | 5.49
35 | 113 | 55 | 13.6213 | 3.5 | 3.7 | 135 | 5.605
35 | 114 | 55 | 13.664 | 3.5 | 3.8 | 135 | 5.72
35 | 115 | 55 | 13.7067 | 3.5 | 3.9 | 135 | 5.835
35 | 116 | 55 | 13.7493 | 3.5 | 4 | 135 | 5.95
35 | 117 | 55 | 13.792 | 3.5 | 4.1 | 135 | 6.065
35 | 118 | 55 | 13.8347 | 3.5 | 4.2 | 135 | 6.18
35 | 119 | 55 | 13.8773 | 3.5 | 4.3 | 135 | 6.295
35 | 120 | 55 | 13.92 | 3.5 | 4.4 | 135 | 6.41
35 | 121 | 55 | 13.9627 | 3.5 | 4.5 | 135 | 6.525
35 | 122 | 55 | 14.0053 | 3.5 | 4.6 | 135 | 6.64
35 | 123 | 55 | 14.048 | 3.5 | 4.7 | 135 | 6.755
35 | 124 | 55 | 14.0907 | 3.5 | 4.8 | 135 | 6.87
35 | 125 | 55 | 14.1333 | 3.5 | 4.9 | 135 | 6.985
35 | 126 | 55 | 14.1773 | 3.5 | 5 | 135 | 7.1
35 | 127 | 55 | 14.2213 | 3.5 | 5.1 | 135 | 7.13
35 | 128 | 55 | 14.2653 | 3.5 | 5.2 | 135 | 7.16
35 | 129 | 55 | 14.3093 | 3.5 | 5.3 | 135 | 7.19
35 | 130 | 55 | 14.3533 | 3.5 | 5.4 | 135 | 7.22
35 | 131 | 55 | 14.3973 | 3.5 | 5.5 | 135 | 7.25
35 | 132 | 55 | 14.4413 | 3.5 | 5.6 | 135 | 7.28
35 | 133 | 55 | 14.4853 | 3.5 | 5.7 | 135 | 7.31
35 | 134 | 55 | 14.5293 | 3.5 | 5.8 | 135 | 7.34
35 | 135 | 55 | 14.5733 | 3.5 | 5.9 | 135 | 7.37
35 | 136 | 55 | 14.6173 | 3.5 | 6 | 135 | 7.4
35 | 137 | 55 | 14.6613 | 3.5 | 6.1 | 135 | 7.43
35 | 138 | 55 | 14.7053 | 3.5 | 6.2 | 135 | 7.46
35 | 139 | 55 | 14.7493 | 3.5 | 6.3 | 135 | 7.49
35 | 140 | 55 | 14.7933 | 3.5 | 6.4 | 135 | 7.52
35 | 141 | 55 | 14.8373 | 3.5 | 6.5 | 135 | 7.55
35 | 142 | 55 | 14.8813 | 3.5 | 6.6 | 135 | 7.58
35 | 143 | 55 | 14.9253 | 3.5 | 6.7 | 135 | 7.61
35 | 144 | 55 | 14.9693 | 3.5 | 6.8 | 135 | 7.64
35 | 145 | 55 | 15.0133 | 3.5 | 6.9 | 135 | 7.67
35 | 146 | 55 | 15.0573 | 3.5 | 7 | 135 | 7.7
35 | 147 | 55 | 15.1013 | 3.5 | 7.1 | 135 | 7.7425
35 | 148 | 55 | 15.1453 | 3.5 | 7.2 | 135 | 7.785
35 | 149 | 55 | 15.1893 | 3.5 | 7.3 | 135 | 7.8275
35 | 150 | 55 | 15.2333 | 3.5 | 7.4 | 135 | 7.87
36 | 45 | 55 | 10 | 3.5 | 7.5 | 135 | 7.9125
36 | 46 | 55 | 10.0627 | 3.5 | 7.6 | 135 | 7.955
36 | 47 | 55 | 10.1253 | 3.5 | 7.7 | 135 | 7.9975
36 | 48 | 55 | 10.188 | 3.5 | 7.8 | 135 | 8.04
36 | 49 | 55 | 10.2507 | 3.5 | 7.9 | 135 | 8.0825
36 | 50 | 55 | 10.3133 | 3.5 | 8 | 135 | 8.125
36 | 51 | 55 | 10.376 | 3.5 | 8.1 | 135 | 8.1675
36 | 52 | 55 | 10.4387 | 3.5 | 8.2 | 135 | 8.21
36 | 53 | 55 | 10.5013 | 3.5 | 8.3 | 135 | 8.2525
36 | 54 | 55 | 10.564 | 3.5 | 8.4 | 135 | 8.295
36 | 55 | 55 | 10.6267 | 3.5 | 8.5 | 135 | 8.3375
36 | 56 | 55 | 10.6893 | 3.5 | 8.6 | 135 | 8.38
36 | 57 | 55 | 10.752 | 3.5 | 8.7 | 135 | 8.4225
36 | 58 | 55 | 10.8147 | 3.5 | 8.8 | 135 | 8.465
36 | 59 | 55 | 10.8773 | 3.5 | 8.9 | 135 | 8.5075
36 | 60 | 55 | 10.94 | 3.5 | 9 | 135 | 8.55
36 | 61 | 55 | 11.0027 | 3.5 | 9.1 | 135 | 8.67
36 | 62 | 55 | 11.0653 | 3.5 | 9.2 | 135 | 8.79
36 | 63 | 55 | 11.128 | 3.5 | 9.3 | 135 | 8.91
36 | 64 | 55 | 11.1907 | 3.5 | 9.4 | 135 | 9.03
36 | 65 | 55 | 11.2533 | 3.5 | 9.5 | 135 | 9.15
36 | 66 | 55 | 11.316 | 3.5 | 9.6 | 135 | 9.27
36 | 67 | 55 | 11.3787 | 3.5 | 9.7 | 135 | 9.39
36 | 68 | 55 | 11.4413 | 3.5 | 9.8 | 135 | 9.51
36 | 69 | 55 | 11.504 | 3.5 | 9.9 | 135 | 9.63
36 | 70 | 55 | 11.5667 | 3.5 | 10 | 135 | 9.75
36 | 71 | 55 | 11.6293 | 3.6 | 3 | 135 | 4.8
36 | 72 | 55 | 11.692 | 3.6 | 3.1 | 135 | 4.916
36 | 73 | 55 | 11.7547 | 3.6 | 3.2 | 135 | 5.032
36 | 74 | 55 | 11.8173 | 3.6 | 3.3 | 135 | 5.148
36 | 75 | 55 | 11.88 | 3.6 | 3.4 | 135 | 5.264
36 | 76 | 55 | 11.928 | 3.6 | 3.5 | 135 | 5.38
36 | 77 | 55 | 11.976 | 3.6 | 3.6 | 135 | 5.496
36 | 78 | 55 | 12.024 | 3.6 | 3.7 | 135 | 5.612
36 | 79 | 55 | 12.072 | 3.6 | 3.8 | 135 | 5.728
36 | 80 | 55 | 12.12 | 3.6 | 3.9 | 135 | 5.844
36 | 81 | 55 | 12.168 | 3.6 | 4 | 135 | 5.96
36 | 82 | 55 | 12.216 | 3.6 | 4.1 | 135 | 6.076
36 | 83 | 55 | 12.264 | 3.6 | 4.2 | 135 | 6.192
36 | 84 | 55 | 12.312 | 3.6 | 4.3 | 135 | 6.308
36 | 85 | 55 | 12.36 | 3.6 | 4.4 | 135 | 6.424
36 | 86 | 55 | 12.408 | 3.6 | 4.5 | 135 | 6.54
36 | 87 | 55 | 12.456 | 3.6 | 4.6 | 135 | 6.656
36 | 88 | 55 | 12.504 | 3.6 | 4.7 | 135 | 6.772
36 | 89 | 55 | 12.552 | 3.6 | 4.8 | 135 | 6.888
36 | 90 | 55 | 12.6 | 3.6 | 4.9 | 135 | 7.004
36 | 91 | 55 | 12.648 | 3.6 | 5 | 135 | 7.12
36 | 92 | 55 | 12.696 | 3.6 | 5.1 | 135 | 7.15
36 | 93 | 55 | 12.744 | 3.6 | 5.2 | 135 | 7.18
36 | 94 | 55 | 12.792 | 3.6 | 5.3 | 135 | 7.21
36 | 95 | 55 | 12.84 | 3.6 | 5.4 | 135 | 7.24
36 | 96 | 55 | 12.888 | 3.6 | 5.5 | 135 | 7.27
36 | 97 | 55 | 12.936 | 3.6 | 5.6 | 135 | 7.3
36 | 98 | 55 | 12.984 | 3.6 | 5.7 | 135 | 7.33
36 | 99 | 55 | 13.032 | 3.6 | 5.8 | 135 | 7.36
36 | 100 | 55 | 13.08 | 3.6 | 5.9 | 135 | 7.39
36 | 101 | 55 | 13.1224 | 3.6 | 6 | 135 | 7.42
36 | 102 | 55 | 13.1648 | 3.6 | 6.1 | 135 | 7.45
36 | 103 | 55 | 13.2072 | 3.6 | 6.2 | 135 | 7.48
36 | 104 | 55 | 13.2496 | 3.6 | 6.3 | 135 | 7.51
36 | 105 | 55 | 13.292 | 3.6 | 6.4 | 135 | 7.54
36 | 106 | 55 | 13.3344 | 3.6 | 6.5 | 135 | 7.57
36 | 107 | 55 | 13.3768 | 3.6 | 6.6 | 135 | 7.6
36 | 108 | 55 | 13.4192 | 3.6 | 6.7 | 135 | 7.63
36 | 109 | 55 | 13.4616 | 3.6 | 6.8 | 135 | 7.66
36 | 110 | 55 | 13.504 | 3.6 | 6.9 | 135 | 7.69
36 | 111 | 55 | 13.5464 | 3.6 | 7 | 135 | 7.72
36 | 112 | 55 | 13.5888 | 3.6 | 7.1 | 135 | 7.762
36 | 113 | 55 | 13.6312 | 3.6 | 7.2 | 135 | 7.804
36 | 114 | 55 | 13.6736 | 3.6 | 7.3 | 135 | 7.846
36 | 115 | 55 | 13.716 | 3.6 | 7.4 | 135 | 7.888
36 | 116 | 55 | 13.7584 | 3.6 | 7.5 | 135 | 7.93
36 | 117 | 55 | 13.8008 | 3.6 | 7.6 | 135 | 7.972
36 | 118 | 55 | 13.8432 | 3.6 | 7.7 | 135 | 8.014
36 | 119 | 55 | 13.8856 | 3.6 | 7.8 | 135 | 8.056
36 | 120 | 55 | 13.928 | 3.6 | 7.9 | 135 | 8.098
36 | 121 | 55 | 13.9704 | 3.6 | 8 | 135 | 8.14
36 | 122 | 55 | 14.0128 | 3.6 | 8.1 | 135 | 8.182
36 | 123 | 55 | 14.0552 | 3.6 | 8.2 | 135 | 8.224
36 | 124 | 55 | 14.0976 | 3.6 | 8.3 | 135 | 8.266
36 | 125 | 55 | 14.14 | 3.6 | 8.4 | 135 | 8.308
36 | 126 | 55 | 14.184 | 3.6 | 8.5 | 135 | 8.35
36 | 127 | 55 | 14.228 | 3.6 | 8.6 | 135 | 8.392
36 | 128 | 55 | 14.272 | 3.6 | 8.7 | 135 | 8.434
36 | 129 | 55 | 14.316 | 3.6 | 8.8 | 135 | 8.476
36 | 130 | 55 | 14.36 | 3.6 | 8.9 | 135 | 8.518
36 | 131 | 55 | 14.404 | 3.6 | 9 | 135 | 8.56
36 | 132 | 55 | 14.448 | 3.6 | 9.1 | 135 | 8.68
36 | 133 | 55 | 14.492 | 3.6 | 9.2 | 135 | 8.8
36 | 134 | 55 | 14.536 | 3.6 | 9.3 | 135 | 8.92
36 | 135 | 55 | 14.58 | 3.6 | 9.4 | 135 | 9.04
36 | 136 | 55 | 14.624 | 3.6 | 9.5 | 135 | 9.16
36 | 137 | 55 | 14.668 | 3.6 | 9.6 | 135 | 9.28
36 | 138 | 55 | 14.712 | 3.6 | 9.7 | 135 | 9.4
36 | 139 | 55 | 14.756 | 3.6 | 9.8 | 135 | 9.52
36 | 140 | 55 | 14.8 | 3.6 | 9.9 | 135 | 9.64
36 | 141 | 55 | 14.844 | 3.6 | 10 | 135 | 9.76
36 | 142 | 55 | 14.888 | 3.7 | 3 | 135 | 4.8
36 | 143 | 55 | 14.932 | 3.7 | 3.1 | 135 | 4.917
36 | 144 | 55 | 14.976 | 3.7 | 3.2 | 135 | 5.034
36 | 145 | 55 | 15.02 | 3.7 | 3.3 | 135 | 5.151
36 | 146 | 55 | 15.064 | 3.7 | 3.4 | 135 | 5.268
36 | 147 | 55 | 15.108 | 3.7 | 3.5 | 135 | 5.385
36 | 148 | 55 | 15.152 | 3.7 | 3.6 | 135 | 5.502
36 | 149 | 55 | 15.196 | 3.7 | 3.7 | 135 | 5.619
36 | 150 | 55 | 15.24 | 3.7 | 3.8 | 135 | 5.736
37 | 45 | 55 | 10 | 3.7 | 3.9 | 135 | 5.853
37 | 46 | 55 | 10.0631 | 3.7 | 4 | 135 | 5.97
37 | 47 | 55 | 10.1262 | 3.7 | 4.1 | 135 | 6.087
37 | 48 | 55 | 10.1893 | 3.7 | 4.2 | 135 | 6.204
37 | 49 | 55 | 10.2524 | 3.7 | 4.3 | 135 | 6.321
37 | 50 | 55 | 10.3156 | 3.7 | 4.4 | 135 | 6.438
37 | 51 | 55 | 10.3787 | 3.7 | 4.5 | 135 | 6.555
37 | 52 | 55 | 10.4418 | 3.7 | 4.6 | 135 | 6.672
37 | 53 | 55 | 10.5049 | 3.7 | 4.7 | 135 | 6.789
37 | 54 | 55 | 10.568 | 3.7 | 4.8 | 135 | 6.906
37 | 55 | 55 | 10.6311 | 3.7 | 4.9 | 135 | 7.023
37 | 56 | 55 | 10.6942 | 3.7 | 5 | 135 | 7.14
37 | 57 | 55 | 10.7573 | 3.7 | 5.1 | 135 | 7.17
37 | 58 | 55 | 10.8204 | 3.7 | 5.2 | 135 | 7.2
37 | 59 | 55 | 10.8836 | 3.7 | 5.3 | 135 | 7.23
37 | 60 | 55 | 10.9467 | 3.7 | 5.4 | 135 | 7.26
37 | 61 | 55 | 11.0098 | 3.7 | 5.5 | 135 | 7.29
37 | 62 | 55 | 11.0729 | 3.7 | 5.6 | 135 | 7.32
37 | 63 | 55 | 11.136 | 3.7 | 5.7 | 135 | 7.35
37 | 64 | 55 | 11.1991 | 3.7 | 5.8 | 135 | 7.38
37 | 65 | 55 | 11.2622 | 3.7 | 5.9 | 135 | 7.41
37 | 66 | 55 | 11.3253 | 3.7 | 6 | 135 | 7.44
37 | 67 | 55 | 11.3884 | 3.7 | 6.1 | 135 | 7.47
37 | 68 | 55 | 11.4516 | 3.7 | 6.2 | 135 | 7.5
37 | 69 | 55 | 11.5147 | 3.7 | 6.3 | 135 | 7.53
37 | 70 | 55 | 11.5778 | 3.7 | 6.4 | 135 | 7.56
37 | 71 | 55 | 11.6409 | 3.7 | 6.5 | 135 | 7.59
37 | 72 | 55 | 11.704 | 3.7 | 6.6 | 135 | 7.62
37 | 73 | 55 | 11.7671 | 3.7 | 6.7 | 135 | 7.65
37 | 74 | 55 | 11.8302 | 3.7 | 6.8 | 135 | 7.68
37 | 75 | 55 | 11.8933 | 3.7 | 6.9 | 135 | 7.71
37 | 76 | 55 | 11.9413 | 3.7 | 7 | 135 | 7.74
37 | 77 | 55 | 11.9893 | 3.7 | 7.1 | 135 | 7.7815
37 | 78 | 55 | 12.0373 | 3.7 | 7.2 | 135 | 7.823
37 | 79 | 55 | 12.0853 | 3.7 | 7.3 | 135 | 7.8645
37 | 80 | 55 | 12.1333 | 3.7 | 7.4 | 135 | 7.906
37 | 81 | 55 | 12.1813 | 3.7 | 7.5 | 135 | 7.9475
37 | 82 | 55 | 12.2293 | 3.7 | 7.6 | 135 | 7.989
37 | 83 | 55 | 12.2773 | 3.7 | 7.7 | 135 | 8.0305
37 | 84 | 55 | 12.3253 | 3.7 | 7.8 | 135 | 8.072
37 | 85 | 55 | 12.3733 | 3.7 | 7.9 | 135 | 8.1135
37 | 86 | 55 | 12.4213 | 3.7 | 8 | 135 | 8.155
37 | 87 | 55 | 12.4693 | 3.7 | 8.1 | 135 | 8.1965
37 | 88 | 55 | 12.5173 | 3.7 | 8.2 | 135 | 8.238
37 | 89 | 55 | 12.5653 | 3.7 | 8.3 | 135 | 8.2795
37 | 90 | 55 | 12.6133 | 3.7 | 8.4 | 135 | 8.321
37 | 91 | 55 | 12.6613 | 3.7 | 8.5 | 135 | 8.3625
37 | 92 | 55 | 12.7093 | 3.7 | 8.6 | 135 | 8.404
37 | 93 | 55 | 12.7573 | 3.7 | 8.7 | 135 | 8.4455
37 | 94 | 55 | 12.8053 | 3.7 | 8.8 | 135 | 8.487
37 | 95 | 55 | 12.8533 | 3.7 | 8.9 | 135 | 8.5285
37 | 96 | 55 | 12.9013 | 3.7 | 9 | 135 | 8.57
37 | 97 | 55 | 12.9493 | 3.7 | 9.1 | 135 | 8.69
37 | 98 | 55 | 12.9973 | 3.7 | 9.2 | 135 | 8.81
37 | 99 | 55 | 13.0453 | 3.7 | 9.3 | 135 | 8.93
37 | 100 | 55 | 13.0933 | 3.7 | 9.4 | 135 | 9.05
37 | 101 | 55 | 13.1355 | 3.7 | 9.5 | 135 | 9.17
37 | 102 | 55 | 13.1776 | 3.7 | 9.6 | 135 | 9.29
37 | 103 | 55 | 13.2197 | 3.7 | 9.7 | 135 | 9.41
37 | 104 | 55 | 13.2619 | 3.7 | 9.8 | 135 | 9.53
37 | 105 | 55 | 13.304 | 3.7 | 9.9 | 135 | 9.65
37 | 106 | 55 | 13.3461 | 3.7 | 10 | 135 | 9.77
37 | 107 | 55 | 13.3883 | 3.8 | 3 | 135 | 4.8
37 | 108 | 55 | 13.4304 | 3.8 | 3.1 | 135 | 4.918
37 | 109 | 55 | 13.4725 | 3.8 | 3.2 | 135 | 5.036
37 | 110 | 55 | 13.5147 | 3.8 | 3.3 | 135 | 5.154
37 | 111 | 55 | 13.5568 | 3.8 | 3.4 | 135 | 5.272
37 | 112 | 55 | 13.5989 | 3.8 | 3.5 | 135 | 5.39
37 | 113 | 55 | 13.6411 | 3.8 | 3.6 | 135 | 5.508
37 | 114 | 55 | 13.6832 | 3.8 | 3.7 | 135 | 5.626
37 | 115 | 55 | 13.7253 | 3.8 | 3.8 | 135 | 5.744
37 | 116 | 55 | 13.7675 | 3.8 | 3.9 | 135 | 5.862
37 | 117 | 55 | 13.8096 | 3.8 | 4 | 135 | 5.98
37 | 118 | 55 | 13.8517 | 3.8 | 4.1 | 135 | 6.098
37 | 119 | 55 | 13.8939 | 3.8 | 4.2 | 135 | 6.216
37 | 120 | 55 | 13.936 | 3.8 | 4.3 | 135 | 6.334
37 | 121 | 55 | 13.9781 | 3.8 | 4.4 | 135 | 6.452
37 | 122 | 55 | 14.0203 | 3.8 | 4.5 | 135 | 6.57
37 | 123 | 55 | 14.0624 | 3.8 | 4.6 | 135 | 6.688
37 | 124 | 55 | 14.1045 | 3.8 | 4.7 | 135 | 6.806
37 | 125 | 55 | 14.1467 | 3.8 | 4.8 | 135 | 6.924
37 | 126 | 55 | 14.1907 | 3.8 | 4.9 | 135 | 7.042
37 | 127 | 55 | 14.2347 | 3.8 | 5 | 135 | 7.16
37 | 128 | 55 | 14.2787 | 3.8 | 5.1 | 135 | 7.19
37 | 129 | 55 | 14.3227 | 3.8 | 5.2 | 135 | 7.22
37 | 130 | 55 | 14.3667 | 3.8 | 5.3 | 135 | 7.25
37 | 131 | 55 | 14.4107 | 3.8 | 5.4 | 135 | 7.28
37 | 132 | 55 | 14.4547 | 3.8 | 5.5 | 135 | 7.31
37 | 133 | 55 | 14.4987 | 3.8 | 5.6 | 135 | 7.34
37 | 134 | 55 | 14.5427 | 3.8 | 5.7 | 135 | 7.37
37 | 135 | 55 | 14.5867 | 3.8 | 5.8 | 135 | 7.4
37 | 136 | 55 | 14.6307 | 3.8 | 5.9 | 135 | 7.43
37 | 137 | 55 | 14.6747 | 3.8 | 6 | 135 | 7.46
37 | 138 | 55 | 14.7187 | 3.8 | 6.1 | 135 | 7.49
37 | 139 | 55 | 14.7627 | 3.8 | 6.2 | 135 | 7.52
37 | 140 | 55 | 14.8067 | 3.8 | 6.3 | 135 | 7.55
37 | 141 | 55 | 14.8507 | 3.8 | 6.4 | 135 | 7.58
37 | 142 | 55 | 14.8947 | 3.8 | 6.5 | 135 | 7.61
37 | 143 | 55 | 14.9387 | 3.8 | 6.6 | 135 | 7.64
37 | 144 | 55 | 14.9827 | 3.8 | 6.7 | 135 | 7.67
37 | 145 | 55 | 15.0267 | 3.8 | 6.8 | 135 | 7.7
37 | 146 | 55 | 15.0707 | 3.8 | 6.9 | 135 | 7.73
37 | 147 | 55 | 15.1147 | 3.8 | 7 | 135 | 7.76
37 | 148 | 55 | 15.1587 | 3.8 | 7.1 | 135 | 7.801
37 | 149 | 55 | 15.2027 | 3.8 | 7.2 | 135 | 7.842
37 | 150 | 55 | 15.2467 | 3.8 | 7.3 | 135 | 7.883
38 | 45 | 55 | 10 | 3.8 | 7.4 | 135 | 7.924
38 | 46 | 55 | 10.0636 | 3.8 | 7.5 | 135 | 7.965
38 | 47 | 55 | 10.1271 | 3.8 | 7.6 | 135 | 8.006
38 | 48 | 55 | 10.1907 | 3.8 | 7.7 | 135 | 8.047
38 | 49 | 55 | 10.2542 | 3.8 | 7.8 | 135 | 8.088
38 | 50 | 55 | 10.3178 | 3.8 | 7.9 | 135 | 8.129
38 | 51 | 55 | 10.3813 | 3.8 | 8 | 135 | 8.17
38 | 52 | 55 | 10.4449 | 3.8 | 8.1 | 135 | 8.211
38 | 53 | 55 | 10.5084 | 3.8 | 8.2 | 135 | 8.252
38 | 54 | 55 | 10.572 | 3.8 | 8.3 | 135 | 8.293
38 | 55 | 55 | 10.6356 | 3.8 | 8.4 | 135 | 8.334
38 | 56 | 55 | 10.6991 | 3.8 | 8.5 | 135 | 8.375
38 | 57 | 55 | 10.7627 | 3.8 | 8.6 | 135 | 8.416
38 | 58 | 55 | 10.8262 | 3.8 | 8.7 | 135 | 8.457
38 | 59 | 55 | 10.8898 | 3.8 | 8.8 | 135 | 8.498
38 | 60 | 55 | 10.9533 | 3.8 | 8.9 | 135 | 8.539
38 | 61 | 55 | 11.0169 | 3.8 | 9 | 135 | 8.58
38 | 62 | 55 | 11.0804 | 3.8 | 9.1 | 135 | 8.7
38 | 63 | 55 | 11.144 | 3.8 | 9.2 | 135 | 8.82
38 | 64 | 55 | 11.2076 | 3.8 | 9.3 | 135 | 8.94
38 | 65 | 55 | 11.2711 | 3.8 | 9.4 | 135 | 9.06
38 | 66 | 55 | 11.3347 | 3.8 | 9.5 | 135 | 9.18
38 | 67 | 55 | 11.3982 | 3.8 | 9.6 | 135 | 9.3
38 | 68 | 55 | 11.4618 | 3.8 | 9.7 | 135 | 9.42
38 | 69 | 55 | 11.5253 | 3.8 | 9.8 | 135 | 9.54
38 | 70 | 55 | 11.5889 | 3.8 | 9.9 | 135 | 9.66
38 | 71 | 55 | 11.6524 | 3.8 | 10 | 135 | 9.78
38 | 72 | 55 | 11.716 | 3.9 | 3 | 135 | 4.8
38 | 73 | 55 | 11.7796 | 3.9 | 3.1 | 135 | 4.919
38 | 74 | 55 | 11.8431 | 3.9 | 3.2 | 135 | 5.038
38 | 75 | 55 | 11.9067 | 3.9 | 3.3 | 135 | 5.157
38 | 76 | 55 | 11.9547 | 3.9 | 3.4 | 135 | 5.276
38 | 77 | 55 | 12.0027 | 3.9 | 3.5 | 135 | 5.395
38 | 78 | 55 | 12.0507 | 3.9 | 3.6 | 135 | 5.514
38 | 79 | 55 | 12.0987 | 3.9 | 3.7 | 135 | 5.633
38 | 80 | 55 | 12.1467 | 3.9 | 3.8 | 135 | 5.752
38 | 81 | 55 | 12.1947 | 3.9 | 3.9 | 135 | 5.871
38 | 82 | 55 | 12.2427 | 3.9 | 4 | 135 | 5.99
38 | 83 | 55 | 12.2907 | 3.9 | 4.1 | 135 | 6.109
38 | 84 | 55 | 12.3387 | 3.9 | 4.2 | 135 | 6.228
38 | 85 | 55 | 12.3867 | 3.9 | 4.3 | 135 | 6.347
38 | 86 | 55 | 12.4347 | 3.9 | 4.4 | 135 | 6.466
38 | 87 | 55 | 12.4827 | 3.9 | 4.5 | 135 | 6.585
38 | 88 | 55 | 12.5307 | 3.9 | 4.6 | 135 | 6.704
38 | 89 | 55 | 12.5787 | 3.9 | 4.7 | 135 | 6.823
38 | 90 | 55 | 12.6267 | 3.9 | 4.8 | 135 | 6.942
38 | 91 | 55 | 12.6747 | 3.9 | 4.9 | 135 | 7.061
38 | 92 | 55 | 12.7227 | 3.9 | 5 | 135 | 7.18
38 | 93 | 55 | 12.7707 | 3.9 | 5.1 | 135 | 7.21
38 | 94 | 55 | 12.8187 | 3.9 | 5.2 | 135 | 7.24
38 | 95 | 55 | 12.8667 | 3.9 | 5.3 | 135 | 7.27
38 | 96 | 55 | 12.9147 | 3.9 | 5.4 | 135 | 7.3
38 | 97 | 55 | 12.9627 | 3.9 | 5.5 | 135 | 7.33
38 | 98 | 55 | 13.0107 | 3.9 | 5.6 | 135 | 7.36
38 | 99 | 55 | 13.0587 | 3.9 | 5.7 | 135 | 7.39
38 | 100 | 55 | 13.1067 | 3.9 | 5.8 | 135 | 7.42
38 | 101 | 55 | 13.1485 | 3.9 | 5.9 | 135 | 7.45
38 | 102 | 55 | 13.1904 | 3.9 | 6 | 135 | 7.48
38 | 103 | 55 | 13.2323 | 3.9 | 6.1 | 135 | 7.51
38 | 104 | 55 | 13.2741 | 3.9 | 6.2 | 135 | 7.54
38 | 105 | 55 | 13.316 | 3.9 | 6.3 | 135 | 7.57
38 | 106 | 55 | 13.3579 | 3.9 | 6.4 | 135 | 7.6
38 | 107 | 55 | 13.3997 | 3.9 | 6.5 | 135 | 7.63
38 | 108 | 55 | 13.4416 | 3.9 | 6.6 | 135 | 7.66
38 | 109 | 55 | 13.4835 | 3.9 | 6.7 | 135 | 7.69
38 | 110 | 55 | 13.5253 | 3.9 | 6.8 | 135 | 7.72
38 | 111 | 55 | 13.5672 | 3.9 | 6.9 | 135 | 7.75
38 | 112 | 55 | 13.6091 | 3.9 | 7 | 135 | 7.78
38 | 113 | 55 | 13.6509 | 3.9 | 7.1 | 135 | 7.8205
38 | 114 | 55 | 13.6928 | 3.9 | 7.2 | 135 | 7.861
38 | 115 | 55 | 13.7347 | 3.9 | 7.3 | 135 | 7.9015
38 | 116 | 55 | 13.7765 | 3.9 | 7.4 | 135 | 7.942
38 | 117 | 55 | 13.8184 | 3.9 | 7.5 | 135 | 7.9825
38 | 118 | 55 | 13.8603 | 3.9 | 7.6 | 135 | 8.023
38 | 119 | 55 | 13.9021 | 3.9 | 7.7 | 135 | 8.0635
38 | 120 | 55 | 13.944 | 3.9 | 7.8 | 135 | 8.104
38 | 121 | 55 | 13.9859 | 3.9 | 7.9 | 135 | 8.1445
38 | 122 | 55 | 14.0277 | 3.9 | 8 | 135 | 8.185
38 | 123 | 55 | 14.0696 | 3.9 | 8.1 | 135 | 8.2255
38 | 124 | 55 | 14.1115 | 3.9 | 8.2 | 135 | 8.266
38 | 125 | 55 | 14.1533 | 3.9 | 8.3 | 135 | 8.3065
38 | 126 | 55 | 14.1973 | 3.9 | 8.4 | 135 | 8.347
38 | 127 | 55 | 14.2413 | 3.9 | 8.5 | 135 | 8.3875
38 | 128 | 55 | 14.2853 | 3.9 | 8.6 | 135 | 8.428
38 | 129 | 55 | 14.3293 | 3.9 | 8.7 | 135 | 8.4685
38 | 130 | 55 | 14.3733 | 3.9 | 8.8 | 135 | 8.509
38 | 131 | 55 | 14.4173 | 3.9 | 8.9 | 135 | 8.5495
38 | 132 | 55 | 14.4613 | 3.9 | 9 | 135 | 8.59
38 | 133 | 55 | 14.5053 | 3.9 | 9.1 | 135 | 8.71
38 | 134 | 55 | 14.5493 | 3.9 | 9.2 | 135 | 8.83
38 | 135 | 55 | 14.5933 | 3.9 | 9.3 | 135 | 8.95
38 | 136 | 55 | 14.6373 | 3.9 | 9.4 | 135 | 9.07
38 | 137 | 55 | 14.6813 | 3.9 | 9.5 | 135 | 9.19
38 | 138 | 55 | 14.7253 | 3.9 | 9.6 | 135 | 9.31
38 | 139 | 55 | 14.7693 | 3.9 | 9.7 | 135 | 9.43
38 | 140 | 55 | 14.8133 | 3.9 | 9.8 | 135 | 9.55
38 | 141 | 55 | 14.8573 | 3.9 | 9.9 | 135 | 9.67
38 | 142 | 55 | 14.9013 | 3.9 | 10 | 135 | 9.79
38 | 143 | 55 | 14.9453 | 4 | 3 | 135 | 4.8
38 | 144 | 55 | 14.9893 | 4 | 3.1 | 135 | 4.92
38 | 145 | 55 | 15.0333 | 4 | 3.2 | 135 | 5.04
38 | 146 | 55 | 15.0773 | 4 | 3.3 | 135 | 5.16
38 | 147 | 55 | 15.1213 | 4 | 3.4 | 135 | 5.28
38 | 148 | 55 | 15.1653 | 4 | 3.5 | 135 | 5.4
38 | 149 | 55 | 15.2093 | 4 | 3.6 | 135 | 5.52
38 | 150 | 55 | 15.2533 | 4 | 3.7 | 135 | 5.64
39 | 45 | 55 | 10 | 4 | 3.8 | 135 | 5.76
39 | 46 | 55 | 10.064 | 4 | 3.9 | 135 | 5.88
39 | 47 | 55 | 10.128 | 4 | 4 | 135 | 6
39 | 48 | 55 | 10.192 | 4 | 4.1 | 135 | 6.12
39 | 49 | 55 | 10.256 | 4 | 4.2 | 135 | 6.24
39 | 50 | 55 | 10.32 | 4 | 4.3 | 135 | 6.36
39 | 51 | 55 | 10.384 | 4 | 4.4 | 135 | 6.48
39 | 52 | 55 | 10.448 | 4 | 4.5 | 135 | 6.6
39 | 53 | 55 | 10.512 | 4 | 4.6 | 135 | 6.72
39 | 54 | 55 | 10.576 | 4 | 4.7 | 135 | 6.84
39 | 55 | 55 | 10.64 | 4 | 4.8 | 135 | 6.96
39 | 56 | 55 | 10.704 | 4 | 4.9 | 135 | 7.08
39 | 57 | 55 | 10.768 | 4 | 5 | 135 | 7.2
39 | 58 | 55 | 10.832 | 4 | 5.1 | 135 | 7.23
39 | 59 | 55 | 10.896 | 4 | 5.2 | 135 | 7.26
39 | 60 | 55 | 10.96 | 4 | 5.3 | 135 | 7.29
39 | 61 | 55 | 11.024 | 4 | 5.4 | 135 | 7.32
39 | 62 | 55 | 11.088 | 4 | 5.5 | 135 | 7.35
39 | 63 | 55 | 11.152 | 4 | 5.6 | 135 | 7.38
39 | 64 | 55 | 11.216 | 4 | 5.7 | 135 | 7.41
39 | 65 | 55 | 11.28 | 4 | 5.8 | 135 | 7.44
39 | 66 | 55 | 11.344 | 4 | 5.9 | 135 | 7.47
39 | 67 | 55 | 11.408 | 4 | 6 | 135 | 7.5
39 | 68 | 55 | 11.472 | 4 | 6.1 | 135 | 7.53
39 | 69 | 55 | 11.536 | 4 | 6.2 | 135 | 7.56
39 | 70 | 55 | 11.6 | 4 | 6.3 | 135 | 7.59
39 | 71 | 55 | 11.664 | 4 | 6.4 | 135 | 7.62
39 | 72 | 55 | 11.728 | 4 | 6.5 | 135 | 7.65
39 | 73 | 55 | 11.792 | 4 | 6.6 | 135 | 7.68
39 | 74 | 55 | 11.856 | 4 | 6.7 | 135 | 7.71
39 | 75 | 55 | 11.92 | 4 | 6.8 | 135 | 7.74
39 | 76 | 55 | 11.968 | 4 | 6.9 | 135 | 7.77
39 | 77 | 55 | 12.016 | 4 | 7 | 135 | 7.8
39 | 78 | 55 | 12.064 | 4 | 7.1 | 135 | 7.84
39 | 79 | 55 | 12.112 | 4 | 7.2 | 135 | 7.88
39 | 80 | 55 | 12.16 | 4 | 7.3 | 135 | 7.92
39 | 81 | 55 | 12.208 | 4 | 7.4 | 135 | 7.96
39 | 82 | 55 | 12.256 | 4 | 7.5 | 135 | 8
39 | 83 | 55 | 12.304 | 4 | 7.6 | 135 | 8.04
39 | 84 | 55 | 12.352 | 4 | 7.7 | 135 | 8.08
39 | 85 | 55 | 12.4 | 4 | 7.8 | 135 | 8.12
39 | 86 | 55 | 12.448 | 4 | 7.9 | 135 | 8.16
39 | 87 | 55 | 12.496 | 4 | 8 | 135 | 8.2
39 | 88 | 55 | 12.544 | 4 | 8.1 | 135 | 8.24
39 | 89 | 55 | 12.592 | 4 | 8.2 | 135 | 8.28
39 | 90 | 55 | 12.64 | 4 | 8.3 | 135 | 8.32
39 | 91 | 55 | 12.688 | 4 | 8.4 | 135 | 8.36
39 | 92 | 55 | 12.736 | 4 | 8.5 | 135 | 8.4
39 | 93 | 55 | 12.784 | 4 | 8.6 | 135 | 8.44
39 | 94 | 55 | 12.832 | 4 | 8.7 | 135 | 8.48
39 | 95 | 55 | 12.88 | 4 | 8.8 | 135 | 8.52
39 | 96 | 55 | 12.928 | 4 | 8.9 | 135 | 8.56
39 | 97 | 55 | 12.976 | 4 | 9 | 135 | 8.6
39 | 98 | 55 | 13.024 | 4 | 9.1 | 135 | 8.72
39 | 99 | 55 | 13.072 | 4 | 9.2 | 135 | 8.84
39 | 100 | 55 | 13.12 | 4 | 9.3 | 135 | 8.96
39 | 101 | 55 | 13.1616 | 4 | 9.4 | 135 | 9.08
39 | 102 | 55 | 13.2032 | 4 | 9.5 | 135 | 9.2
39 | 103 | 55 | 13.2448 | 4 | 9.6 | 135 | 9.32
39 | 104 | 55 | 13.2864 | 4 | 9.7 | 135 | 9.44
39 | 105 | 55 | 13.328 | 4 | 9.8 | 135 | 9.56
39 | 106 | 55 | 13.3696 | 4 | 9.9 | 135 | 9.68
39 | 107 | 55 | 13.4112 | 4 | 10 | 135 | 9.8
39 | 108 | 55 | 13.4528 | 4.1 | 3 | 135 | 4.81
39 | 109 | 55 | 13.4944 | 4.1 | 3.1 | 135 | 4.93
39 | 110 | 55 | 13.536 | 4.1 | 3.2 | 135 | 5.05
39 | 111 | 55 | 13.5776 | 4.1 | 3.3 | 135 | 5.17
39 | 112 | 55 | 13.6192 | 4.1 | 3.4 | 135 | 5.29
39 | 113 | 55 | 13.6608 | 4.1 | 3.5 | 135 | 5.41
39 | 114 | 55 | 13.7024 | 4.1 | 3.6 | 135 | 5.53
39 | 115 | 55 | 13.744 | 4.1 | 3.7 | 135 | 5.65
39 | 116 | 55 | 13.7856 | 4.1 | 3.8 | 135 | 5.77
39 | 117 | 55 | 13.8272 | 4.1 | 3.9 | 135 | 5.89
39 | 118 | 55 | 13.8688 | 4.1 | 4 | 135 | 6.01
39 | 119 | 55 | 13.9104 | 4.1 | 4.1 | 135 | 6.13
39 | 120 | 55 | 13.952 | 4.1 | 4.2 | 135 | 6.25
39 | 121 | 55 | 13.9936 | 4.1 | 4.3 | 135 | 6.37
39 | 122 | 55 | 14.0352 | 4.1 | 4.4 | 135 | 6.49
39 | 123 | 55 | 14.0768 | 4.1 | 4.5 | 135 | 6.61
39 | 124 | 55 | 14.1184 | 4.1 | 4.6 | 135 | 6.73
39 | 125 | 55 | 14.16 | 4.1 | 4.7 | 135 | 6.85
39 | 126 | 55 | 14.204 | 4.1 | 4.8 | 135 | 6.97
39 | 127 | 55 | 14.248 | 4.1 | 4.9 | 135 | 7.09
39 | 128 | 55 | 14.292 | 4.1 | 5 | 135 | 7.21
39 | 129 | 55 | 14.336 | 4.1 | 5.1 | 135 | 7.2405
39 | 130 | 55 | 14.38 | 4.1 | 5.2 | 135 | 7.271
39 | 131 | 55 | 14.424 | 4.1 | 5.3 | 135 | 7.3015
39 | 132 | 55 | 14.468 | 4.1 | 5.4 | 135 | 7.332
39 | 133 | 55 | 14.512 | 4.1 | 5.5 | 135 | 7.3625
39 | 134 | 55 | 14.556 | 4.1 | 5.6 | 135 | 7.393
39 | 135 | 55 | 14.6 | 4.1 | 5.7 | 135 | 7.4235
39 | 136 | 55 | 14.644 | 4.1 | 5.8 | 135 | 7.454
39 | 137 | 55 | 14.688 | 4.1 | 5.9 | 135 | 7.4845
39 | 138 | 55 | 14.732 | 4.1 | 6 | 135 | 7.515
39 | 139 | 55 | 14.776 | 4.1 | 6.1 | 135 | 7.5455
39 | 140 | 55 | 14.82 | 4.1 | 6.2 | 135 | 7.576
39 | 141 | 55 | 14.864 | 4.1 | 6.3 | 135 | 7.6065
39 | 142 | 55 | 14.908 | 4.1 | 6.4 | 135 | 7.637
39 | 143 | 55 | 14.952 | 4.1 | 6.5 | 135 | 7.6675
39 | 144 | 55 | 14.996 | 4.1 | 6.6 | 135 | 7.698
39 | 145 | 55 | 15.04 | 4.1 | 6.7 | 135 | 7.7285
39 | 146 | 55 | 15.084 | 4.1 | 6.8 | 135 | 7.759
39 | 147 | 55 | 15.128 | 4.1 | 6.9 | 135 | 7.7895
39 | 148 | 55 | 15.172 | 4.1 | 7 | 135 | 7.82
39 | 149 | 55 | 15.216 | 4.1 | 7.1 | 135 | 7.8605
39 | 150 | 55 | 15.26 | 4.1 | 7.2 | 135 | 7.901
40 | 45 | 55 | 10 | 4.1 | 7.3 | 135 | 7.9415
40 | 46 | 55 | 10.0644 | 4.1 | 7.4 | 135 | 7.982
40 | 47 | 55 | 10.1289 | 4.1 | 7.5 | 135 | 8.0225
40 | 48 | 55 | 10.1933 | 4.1 | 7.6 | 135 | 8.063
40 | 49 | 55 | 10.2578 | 4.1 | 7.7 | 135 | 8.1035
40 | 50 | 55 | 10.3222 | 4.1 | 7.8 | 135 | 8.144
40 | 51 | 55 | 10.3867 | 4.1 | 7.9 | 135 | 8.1845
40 | 52 | 55 | 10.4511 | 4.1 | 8 | 135 | 8.225
40 | 53 | 55 | 10.5156 | 4.1 | 8.1 | 135 | 8.2655
40 | 54 | 55 | 10.58 | 4.1 | 8.2 | 135 | 8.306
40 | 55 | 55 | 10.6444 | 4.1 | 8.3 | 135 | 8.3465
40 | 56 | 55 | 10.7089 | 4.1 | 8.4 | 135 | 8.387
40 | 57 | 55 | 10.7733 | 4.1 | 8.5 | 135 | 8.4275
40 | 58 | 55 | 10.8378 | 4.1 | 8.6 | 135 | 8.468
40 | 59 | 55 | 10.9022 | 4.1 | 8.7 | 135 | 8.5085
40 | 60 | 55 | 10.9667 | 4.1 | 8.8 | 135 | 8.549
40 | 61 | 55 | 11.0311 | 4.1 | 8.9 | 135 | 8.5895
40 | 62 | 55 | 11.0956 | 4.1 | 9 | 135 | 8.63
40 | 63 | 55 | 11.16 | 4.1 | 9.1 | 135 | 8.75
40 | 64 | 55 | 11.2244 | 4.1 | 9.2 | 135 | 8.87
40 | 65 | 55 | 11.2889 | 4.1 | 9.3 | 135 | 8.99
40 | 66 | 55 | 11.3533 | 4.1 | 9.4 | 135 | 9.11
40 | 67 | 55 | 11.4178 | 4.1 | 9.5 | 135 | 9.23
40 | 68 | 55 | 11.4822 | 4.1 | 9.6 | 135 | 9.35
40 | 69 | 55 | 11.5467 | 4.1 | 9.7 | 135 | 9.47
40 | 70 | 55 | 11.6111 | 4.1 | 9.8 | 135 | 9.59
40 | 71 | 55 | 11.6756 | 4.1 | 9.9 | 135 | 9.71
40 | 72 | 55 | 11.74 | 4.1 | 10 | 135 | 9.83
40 | 73 | 55 | 11.8044 | 4.2 | 3 | 135 | 4.82
40 | 74 | 55 | 11.8689 | 4.2 | 3.1 | 135 | 4.94
40 | 75 | 55 | 11.9333 | 4.2 | 3.2 | 135 | 5.06
40 | 76 | 55 | 11.9813 | 4.2 | 3.3 | 135 | 5.18
40 | 77 | 55 | 12.0293 | 4.2 | 3.4 | 135 | 5.3
40 | 78 | 55 | 12.0773 | 4.2 | 3.5 | 135 | 5.42
40 | 79 | 55 | 12.1253 | 4.2 | 3.6 | 135 | 5.54
40 | 80 | 55 | 12.1733 | 4.2 | 3.7 | 135 | 5.66
40 | 81 | 55 | 12.2213 | 4.2 | 3.8 | 135 | 5.78
40 | 82 | 55 | 12.2693 | 4.2 | 3.9 | 135 | 5.9
40 | 83 | 55 | 12.3173 | 4.2 | 4 | 135 | 6.02
40 | 84 | 55 | 12.3653 | 4.2 | 4.1 | 135 | 6.14
40 | 85 | 55 | 12.4133 | 4.2 | 4.2 | 135 | 6.26
40 | 86 | 55 | 12.4613 | 4.2 | 4.3 | 135 | 6.38
40 | 87 | 55 | 12.5093 | 4.2 | 4.4 | 135 | 6.5
40 | 88 | 55 | 12.5573 | 4.2 | 4.5 | 135 | 6.62
40 | 89 | 55 | 12.6053 | 4.2 | 4.6 | 135 | 6.74
40 | 90 | 55 | 12.6533 | 4.2 | 4.7 | 135 | 6.86
40 | 91 | 55 | 12.7013 | 4.2 | 4.8 | 135 | 6.98
40 | 92 | 55 | 12.7493 | 4.2 | 4.9 | 135 | 7.1
40 | 93 | 55 | 12.7973 | 4.2 | 5 | 135 | 7.22
40 | 94 | 55 | 12.8453 | 4.2 | 5.1 | 135 | 7.251
40 | 95 | 55 | 12.8933 | 4.2 | 5.2 | 135 | 7.282
40 | 96 | 55 | 12.9413 | 4.2 | 5.3 | 135 | 7.313
40 | 97 | 55 | 12.9893 | 4.2 | 5.4 | 135 | 7.344
40 | 98 | 55 | 13.0373 | 4.2 | 5.5 | 135 | 7.375
40 | 99 | 55 | 13.0853 | 4.2 | 5.6 | 135 | 7.406
40 | 100 | 55 | 13.1333 | 4.2 | 5.7 | 135 | 7.437
40 | 101 | 55 | 13.1747 | 4.2 | 5.8 | 135 | 7.468
40 | 102 | 55 | 13.216 | 4.2 | 5.9 | 135 | 7.499
40 | 103 | 55 | 13.2573 | 4.2 | 6 | 135 | 7.53
40 | 104 | 55 | 13.2987 | 4.2 | 6.1 | 135 | 7.561
40 | 105 | 55 | 13.34 | 4.2 | 6.2 | 135 | 7.592
40 | 106 | 55 | 13.3813 | 4.2 | 6.3 | 135 | 7.623
40 | 107 | 55 | 13.4227 | 4.2 | 6.4 | 135 | 7.654
40 | 108 | 55 | 13.464 | 4.2 | 6.5 | 135 | 7.685
40 | 109 | 55 | 13.5053 | 4.2 | 6.6 | 135 | 7.716
40 | 110 | 55 | 13.5467 | 4.2 | 6.7 | 135 | 7.747
40 | 111 | 55 | 13.588 | 4.2 | 6.8 | 135 | 7.778
40 | 112 | 55 | 13.6293 | 4.2 | 6.9 | 135 | 7.809
40 | 113 | 55 | 13.6707 | 4.2 | 7 | 135 | 7.84
40 | 114 | 55 | 13.712 | 4.2 | 7.1 | 135 | 7.881
40 | 115 | 55 | 13.7533 | 4.2 | 7.2 | 135 | 7.922
40 | 116 | 55 | 13.7947 | 4.2 | 7.3 | 135 | 7.963
40 | 117 | 55 | 13.836 | 4.2 | 7.4 | 135 | 8.004
40 | 118 | 55 | 13.8773 | 4.2 | 7.5 | 135 | 8.045
40 | 119 | 55 | 13.9187 | 4.2 | 7.6 | 135 | 8.086
40 | 120 | 55 | 13.96 | 4.2 | 7.7 | 135 | 8.127
40 | 121 | 55 | 14.0013 | 4.2 | 7.8 | 135 | 8.168
40 | 122 | 55 | 14.0427 | 4.2 | 7.9 | 135 | 8.209
40 | 123 | 55 | 14.084 | 4.2 | 8 | 135 | 8.25
40 | 124 | 55 | 14.1253 | 4.2 | 8.1 | 135 | 8.291
40 | 125 | 55 | 14.1667 | 4.2 | 8.2 | 135 | 8.332
40 | 126 | 55 | 14.2107 | 4.2 | 8.3 | 135 | 8.373
40 | 127 | 55 | 14.2547 | 4.2 | 8.4 | 135 | 8.414
40 | 128 | 55 | 14.2987 | 4.2 | 8.5 | 135 | 8.455
40 | 129 | 55 | 14.3427 | 4.2 | 8.6 | 135 | 8.496
40 | 130 | 55 | 14.3867 | 4.2 | 8.7 | 135 | 8.537
40 | 131 | 55 | 14.4307 | 4.2 | 8.8 | 135 | 8.578
40 | 132 | 55 | 14.4747 | 4.2 | 8.9 | 135 | 8.619
40 | 133 | 55 | 14.5187 | 4.2 | 9 | 135 | 8.66
40 | 134 | 55 | 14.5627 | 4.2 | 9.1 | 135 | 8.78
40 | 135 | 55 | 14.6067 | 4.2 | 9.2 | 135 | 8.9
40 | 136 | 55 | 14.6507 | 4.2 | 9.3 | 135 | 9.02
40 | 137 | 55 | 14.6947 | 4.2 | 9.4 | 135 | 9.14
40 | 138 | 55 | 14.7387 | 4.2 | 9.5 | 135 | 9.26
40 | 139 | 55 | 14.7827 | 4.2 | 9.6 | 135 | 9.38
40 | 140 | 55 | 14.8267 | 4.2 | 9.7 | 135 | 9.5
40 | 141 | 55 | 14.8707 | 4.2 | 9.8 | 135 | 9.62
40 | 142 | 55 | 14.9147 | 4.2 | 9.9 | 135 | 9.74
40 | 143 | 55 | 14.9587 | 4.2 | 10 | 135 | 9.86
40 | 144 | 55 | 15.0027 | 4.3 | 3 | 135 | 4.83
40 | 145 | 55 | 15.0467 | 4.3 | 3.1 | 135 | 4.95
40 | 146 | 55 | 15.0907 | 4.3 | 3.2 | 135 | 5.07
40 | 147 | 55 | 15.1347 | 4.3 | 3.3 | 135 | 5.19
40 | 148 | 55 | 15.1787 | 4.3 | 3.4 | 135 | 5.31
40 | 149 | 55 | 15.2227 | 4.3 | 3.5 | 135 | 5.43
40 | 150 | 55 | 15.2667 | 4.3 | 3.6 | 135 | 5.55
41 | 45 | 55 | 10 | 4.3 | 3.7 | 135 | 5.67
41 | 46 | 55 | 10.0649 | 4.3 | 3.8 | 135 | 5.79
41 | 47 | 55 | 10.1298 | 4.3 | 3.9 | 135 | 5.91
41 | 48 | 55 | 10.1947 | 4.3 | 4 | 135 | 6.03
41 | 49 | 55 | 10.2596 | 4.3 | 4.1 | 135 | 6.15
41 | 50 | 55 | 10.3244 | 4.3 | 4.2 | 135 | 6.27
41 | 51 | 55 | 10.3893 | 4.3 | 4.3 | 135 | 6.39
41 | 52 | 55 | 10.4542 | 4.3 | 4.4 | 135 | 6.51
41 | 53 | 55 | 10.5191 | 4.3 | 4.5 | 135 | 6.63
41 | 54 | 55 | 10.584 | 4.3 | 4.6 | 135 | 6.75
41 | 55 | 55 | 10.6489 | 4.3 | 4.7 | 135 | 6.87
41 | 56 | 55 | 10.7138 | 4.3 | 4.8 | 135 | 6.99
41 | 57 | 55 | 10.7787 | 4.3 | 4.9 | 135 | 7.11
41 | 58 | 55 | 10.8436 | 4.3 | 5 | 135 | 7.23
41 | 59 | 55 | 10.9084 | 4.3 | 5.1 | 135 | 7.2615
41 | 60 | 55 | 10.9733 | 4.3 | 5.2 | 135 | 7.293
41 | 61 | 55 | 11.0382 | 4.3 | 5.3 | 135 | 7.3245
41 | 62 | 55 | 11.1031 | 4.3 | 5.4 | 135 | 7.356
41 | 63 | 55 | 11.168 | 4.3 | 5.5 | 135 | 7.3875
41 | 64 | 55 | 11.2329 | 4.3 | 5.6 | 135 | 7.419
41 | 65 | 55 | 11.2978 | 4.3 | 5.7 | 135 | 7.4505
41 | 66 | 55 | 11.3627 | 4.3 | 5.8 | 135 | 7.482
41 | 67 | 55 | 11.4276 | 4.3 | 5.9 | 135 | 7.5135
41 | 68 | 55 | 11.4924 | 4.3 | 6 | 135 | 7.545
41 | 69 | 55 | 11.5573 | 4.3 | 6.1 | 135 | 7.5765
41 | 70 | 55 | 11.6222 | 4.3 | 6.2 | 135 | 7.608
41 | 71 | 55 | 11.6871 | 4.3 | 6.3 | 135 | 7.6395
41 | 72 | 55 | 11.752 | 4.3 | 6.4 | 135 | 7.671
41 | 73 | 55 | 11.8169 | 4.3 | 6.5 | 135 | 7.7025
41 | 74 | 55 | 11.8818 | 4.3 | 6.6 | 135 | 7.734
41 | 75 | 55 | 11.9467 | 4.3 | 6.7 | 135 | 7.7655
41 | 76 | 55 | 11.9947 | 4.3 | 6.8 | 135 | 7.797
41 | 77 | 55 | 12.0427 | 4.3 | 6.9 | 135 | 7.8285
41 | 78 | 55 | 12.0907 | 4.3 | 7 | 135 | 7.86
41 | 79 | 55 | 12.1387 | 4.3 | 7.1 | 135 | 7.9015
41 | 80 | 55 | 12.1867 | 4.3 | 7.2 | 135 | 7.943
41 | 81 | 55 | 12.2347 | 4.3 | 7.3 | 135 | 7.9845
41 | 82 | 55 | 12.2827 | 4.3 | 7.4 | 135 | 8.026
41 | 83 | 55 | 12.3307 | 4.3 | 7.5 | 135 | 8.0675
41 | 84 | 55 | 12.3787 | 4.3 | 7.6 | 135 | 8.109
41 | 85 | 55 | 12.4267 | 4.3 | 7.7 | 135 | 8.1505
41 | 86 | 55 | 12.4747 | 4.3 | 7.8 | 135 | 8.192
41 | 87 | 55 | 12.5227 | 4.3 | 7.9 | 135 | 8.2335
41 | 88 | 55 | 12.5707 | 4.3 | 8 | 135 | 8.275
41 | 89 | 55 | 12.6187 | 4.3 | 8.1 | 135 | 8.3165
41 | 90 | 55 | 12.6667 | 4.3 | 8.2 | 135 | 8.358
41 | 91 | 55 | 12.7147 | 4.3 | 8.3 | 135 | 8.3995
41 | 92 | 55 | 12.7627 | 4.3 | 8.4 | 135 | 8.441
41 | 93 | 55 | 12.8107 | 4.3 | 8.5 | 135 | 8.4825
41 | 94 | 55 | 12.8587 | 4.3 | 8.6 | 135 | 8.524
41 | 95 | 55 | 12.9067 | 4.3 | 8.7 | 135 | 8.5655
41 | 96 | 55 | 12.9547 | 4.3 | 8.8 | 135 | 8.607
41 | 97 | 55 | 13.0027 | 4.3 | 8.9 | 135 | 8.6485
41 | 98 | 55 | 13.0507 | 4.3 | 9 | 135 | 8.69
41 | 99 | 55 | 13.0987 | 4.3 | 9.1 | 135 | 8.81
41 | 100 | 55 | 13.1467 | 4.3 | 9.2 | 135 | 8.93
41 | 101 | 55 | 13.1877 | 4.3 | 9.3 | 135 | 9.05
41 | 102 | 55 | 13.2288 | 4.3 | 9.4 | 135 | 9.17
41 | 103 | 55 | 13.2699 | 4.3 | 9.5 | 135 | 9.29
41 | 104 | 55 | 13.3109 | 4.3 | 9.6 | 135 | 9.41
41 | 105 | 55 | 13.352 | 4.3 | 9.7 | 135 | 9.53
41 | 106 | 55 | 13.3931 | 4.3 | 9.8 | 135 | 9.65
41 | 107 | 55 | 13.4341 | 4.3 | 9.9 | 135 | 9.77
41 | 108 | 55 | 13.4752 | 4.3 | 10 | 135 | 9.89
41 | 109 | 55 | 13.5163 | 4.4 | 3 | 135 | 4.84
41 | 110 | 55 | 13.5573 | 4.4 | 3.1 | 135 | 4.96
41 | 111 | 55 | 13.5984 | 4.4 | 3.2 | 135 | 5.08
41 | 112 | 55 | 13.6395 | 4.4 | 3.3 | 135 | 5.2
41 | 113 | 55 | 13.6805 | 4.4 | 3.4 | 135 | 5.32
41 | 114 | 55 | 13.7216 | 4.4 | 3.5 | 135 | 5.44
41 | 115 | 55 | 13.7627 | 4.4 | 3.6 | 135 | 5.56
41 | 116 | 55 | 13.8037 | 4.4 | 3.7 | 135 | 5.68
41 | 117 | 55 | 13.8448 | 4.4 | 3.8 | 135 | 5.8
41 | 118 | 55 | 13.8859 | 4.4 | 3.9 | 135 | 5.92
41 | 119 | 55 | 13.9269 | 4.4 | 4 | 135 | 6.04
41 | 120 | 55 | 13.968 | 4.4 | 4.1 | 135 | 6.16
41 | 121 | 55 | 14.0091 | 4.4 | 4.2 | 135 | 6.28
41 | 122 | 55 | 14.0501 | 4.4 | 4.3 | 135 | 6.4
41 | 123 | 55 | 14.0912 | 4.4 | 4.4 | 135 | 6.52
41 | 124 | 55 | 14.1323 | 4.4 | 4.5 | 135 | 6.64
41 | 125 | 55 | 14.1733 | 4.4 | 4.6 | 135 | 6.76
41 | 126 | 55 | 14.2173 | 4.4 | 4.7 | 135 | 6.88
41 | 127 | 55 | 14.2613 | 4.4 | 4.8 | 135 | 7
41 | 128 | 55 | 14.3053 | 4.4 | 4.9 | 135 | 7.12
41 | 129 | 55 | 14.3493 | 4.4 | 5 | 135 | 7.24
41 | 130 | 55 | 14.3933 | 4.4 | 5.1 | 135 | 7.272
41 | 131 | 55 | 14.4373 | 4.4 | 5.2 | 135 | 7.304
41 | 132 | 55 | 14.4813 | 4.4 | 5.3 | 135 | 7.336
41 | 133 | 55 | 14.5253 | 4.4 | 5.4 | 135 | 7.368
41 | 134 | 55 | 14.5693 | 4.4 | 5.5 | 135 | 7.4
41 | 135 | 55 | 14.6133 | 4.4 | 5.6 | 135 | 7.432
41 | 136 | 55 | 14.6573 | 4.4 | 5.7 | 135 | 7.464
41 | 137 | 55 | 14.7013 | 4.4 | 5.8 | 135 | 7.496
41 | 138 | 55 | 14.7453 | 4.4 | 5.9 | 135 | 7.528
41 | 139 | 55 | 14.7893 | 4.4 | 6 | 135 | 7.56
41 | 140 | 55 | 14.8333 | 4.4 | 6.1 | 135 | 7.592
41 | 141 | 55 | 14.8773 | 4.4 | 6.2 | 135 | 7.624
41 | 142 | 55 | 14.9213 | 4.4 | 6.3 | 135 | 7.656
41 | 143 | 55 | 14.9653 | 4.4 | 6.4 | 135 | 7.688
41 | 144 | 55 | 15.0093 | 4.4 | 6.5 | 135 | 7.72
41 | 145 | 55 | 15.0533 | 4.4 | 6.6 | 135 | 7.752
41 | 146 | 55 | 15.0973 | 4.4 | 6.7 | 135 | 7.784
41 | 147 | 55 | 15.1413 | 4.4 | 6.8 | 135 | 7.816
41 | 148 | 55 | 15.1853 | 4.4 | 6.9 | 135 | 7.848
41 | 149 | 55 | 15.2293 | 4.4 | 7 | 135 | 7.88
41 | 150 | 55 | 15.2733 | 4.4 | 7.1 | 135 | 7.922
42 | 45 | 55 | 10 | 4.4 | 7.2 | 135 | 7.964
42 | 46 | 55 | 10.0653 | 4.4 | 7.3 | 135 | 8.006
42 | 47 | 55 | 10.1307 | 4.4 | 7.4 | 135 | 8.048
42 | 48 | 55 | 10.196 | 4.4 | 7.5 | 135 | 8.09
42 | 49 | 55 | 10.2613 | 4.4 | 7.6 | 135 | 8.132
42 | 50 | 55 | 10.3267 | 4.4 | 7.7 | 135 | 8.174
42 | 51 | 55 | 10.392 | 4.4 | 7.8 | 135 | 8.216
42 | 52 | 55 | 10.4573 | 4.4 | 7.9 | 135 | 8.258
42 | 53 | 55 | 10.5227 | 4.4 | 8 | 135 | 8.3
42 | 54 | 55 | 10.588 | 4.4 | 8.1 | 135 | 8.342
42 | 55 | 55 | 10.6533 | 4.4 | 8.2 | 135 | 8.384
42 | 56 | 55 | 10.7187 | 4.4 | 8.3 | 135 | 8.426
42 | 57 | 55 | 10.784 | 4.4 | 8.4 | 135 | 8.468
42 | 58 | 55 | 10.8493 | 4.4 | 8.5 | 135 | 8.51
42 | 59 | 55 | 10.9147 | 4.4 | 8.6 | 135 | 8.552
42 | 60 | 55 | 10.98 | 4.4 | 8.7 | 135 | 8.594
42 | 61 | 55 | 11.0453 | 4.4 | 8.8 | 135 | 8.636
42 | 62 | 55 | 11.1107 | 4.4 | 8.9 | 135 | 8.678
42 | 63 | 55 | 11.176 | 4.4 | 9 | 135 | 8.72
42 | 64 | 55 | 11.2413 | 4.4 | 9.1 | 135 | 8.84
42 | 65 | 55 | 11.3067 | 4.4 | 9.2 | 135 | 8.96
42 | 66 | 55 | 11.372 | 4.4 | 9.3 | 135 | 9.08
42 | 67 | 55 | 11.4373 | 4.4 | 9.4 | 135 | 9.2
42 | 68 | 55 | 11.5027 | 4.4 | 9.5 | 135 | 9.32
42 | 69 | 55 | 11.568 | 4.4 | 9.6 | 135 | 9.44
42 | 70 | 55 | 11.6333 | 4.4 | 9.7 | 135 | 9.56
42 | 71 | 55 | 11.6987 | 4.4 | 9.8 | 135 | 9.68
42 | 72 | 55 | 11.764 | 4.4 | 9.9 | 135 | 9.8
42 | 73 | 55 | 11.8293 | 4.4 | 10 | 135 | 9.92
42 | 74 | 55 | 11.8947 | 4.5 | 3 | 135 | 4.85
42 | 75 | 55 | 11.96 | 4.5 | 3.1 | 135 | 4.97
42 | 76 | 55 | 12.008 | 4.5 | 3.2 | 135 | 5.09
42 | 77 | 55 | 12.056 | 4.5 | 3.3 | 135 | 5.21
42 | 78 | 55 | 12.104 | 4.5 | 3.4 | 135 | 5.33
42 | 79 | 55 | 12.152 | 4.5 | 3.5 | 135 | 5.45
42 | 80 | 55 | 12.2 | 4.5 | 3.6 | 135 | 5.57
42 | 81 | 55 | 12.248 | 4.5 | 3.7 | 135 | 5.69
42 | 82 | 55 | 12.296 | 4.5 | 3.8 | 135 | 5.81
42 | 83 | 55 | 12.344 | 4.5 | 3.9 | 135 | 5.93
42 | 84 | 55 | 12.392 | 4.5 | 4 | 135 | 6.05
42 | 85 | 55 | 12.44 | 4.5 | 4.1 | 135 | 6.17
42 | 86 | 55 | 12.488 | 4.5 | 4.2 | 135 | 6.29
42 | 87 | 55 | 12.536 | 4.5 | 4.3 | 135 | 6.41
42 | 88 | 55 | 12.584 | 4.5 | 4.4 | 135 | 6.53
42 | 89 | 55 | 12.632 | 4.5 | 4.5 | 135 | 6.65
42 | 90 | 55 | 12.68 | 4.5 | 4.6 | 135 | 6.77
42 | 91 | 55 | 12.728 | 4.5 | 4.7 | 135 | 6.89
42 | 92 | 55 | 12.776 | 4.5 | 4.8 | 135 | 7.01
42 | 93 | 55 | 12.824 | 4.5 | 4.9 | 135 | 7.13
42 | 94 | 55 | 12.872 | 4.5 | 5 | 135 | 7.25
42 | 95 | 55 | 12.92 | 4.5 | 5.1 | 135 | 7.2825
42 | 96 | 55 | 12.968 | 4.5 | 5.2 | 135 | 7.315
42 | 97 | 55 | 13.016 | 4.5 | 5.3 | 135 | 7.3475
42 | 98 | 55 | 13.064 | 4.5 | 5.4 | 135 | 7.38
42 | 99 | 55 | 13.112 | 4.5 | 5.5 | 135 | 7.4125
42 | 100 | 55 | 13.16 | 4.5 | 5.6 | 135 | 7.445
42 | 101 | 55 | 13.2008 | 4.5 | 5.7 | 135 | 7.4775
42 | 102 | 55 | 13.2416 | 4.5 | 5.8 | 135 | 7.51
42 | 103 | 55 | 13.2824 | 4.5 | 5.9 | 135 | 7.5425
42 | 104 | 55 | 13.3232 | 4.5 | 6 | 135 | 7.575
42 | 105 | 55 | 13.364 | 4.5 | 6.1 | 135 | 7.6075
42 | 106 | 55 | 13.4048 | 4.5 | 6.2 | 135 | 7.64
42 | 107 | 55 | 13.4456 | 4.5 | 6.3 | 135 | 7.6725
42 | 108 | 55 | 13.4864 | 4.5 | 6.4 | 135 | 7.705
42 | 109 | 55 | 13.5272 | 4.5 | 6.5 | 135 | 7.7375
42 | 110 | 55 | 13.568 | 4.5 | 6.6 | 135 | 7.77
42 | 111 | 55 | 13.6088 | 4.5 | 6.7 | 135 | 7.8025
42 | 112 | 55 | 13.6496 | 4.5 | 6.8 | 135 | 7.835
42 | 113 | 55 | 13.6904 | 4.5 | 6.9 | 135 | 7.8675
42 | 114 | 55 | 13.7312 | 4.5 | 7 | 135 | 7.9
42 | 115 | 55 | 13.772 | 4.5 | 7.1 | 135 | 7.9425
42 | 116 | 55 | 13.8128 | 4.5 | 7.2 | 135 | 7.985
42 | 117 | 55 | 13.8536 | 4.5 | 7.3 | 135 | 8.0275
42 | 118 | 55 | 13.8944 | 4.5 | 7.4 | 135 | 8.07
42 | 119 | 55 | 13.9352 | 4.5 | 7.5 | 135 | 8.1125
42 | 120 | 55 | 13.976 | 4.5 | 7.6 | 135 | 8.155
42 | 121 | 55 | 14.0168 | 4.5 | 7.7 | 135 | 8.1975
42 | 122 | 55 | 14.0576 | 4.5 | 7.8 | 135 | 8.24
42 | 123 | 55 | 14.0984 | 4.5 | 7.9 | 135 | 8.2825
42 | 124 | 55 | 14.1392 | 4.5 | 8 | 135 | 8.325
42 | 125 | 55 | 14.18 | 4.5 | 8.1 | 135 | 8.3675
42 | 126 | 55 | 14.224 | 4.5 | 8.2 | 135 | 8.41
42 | 127 | 55 | 14.268 | 4.5 | 8.3 | 135 | 8.4525
42 | 128 | 55 | 14.312 | 4.5 | 8.4 | 135 | 8.495
42 | 129 | 55 | 14.356 | 4.5 | 8.5 | 135 | 8.5375
42 | 130 | 55 | 14.4 | 4.5 | 8.6 | 135 | 8.58
42 | 131 | 55 | 14.444 | 4.5 | 8.7 | 135 | 8.6225
42 | 132 | 55 | 14.488 | 4.5 | 8.8 | 135 | 8.665
42 | 133 | 55 | 14.532 | 4.5 | 8.9 | 135 | 8.7075
42 | 134 | 55 | 14.576 | 4.5 | 9 | 135 | 8.75
42 | 135 | 55 | 14.62 | 4.5 | 9.1 | 135 | 8.87
42 | 136 | 55 | 14.664 | 4.5 | 9.2 | 135 | 8.99
42 | 137 | 55 | 14.708 | 4.5 | 9.3 | 135 | 9.11
42 | 138 | 55 | 14.752 | 4.5 | 9.4 | 135 | 9.23
42 | 139 | 55 | 14.796 | 4.5 | 9.5 | 135 | 9.35
42 | 140 | 55 | 14.84 | 4.5 | 9.6 | 135 | 9.47
42 | 141 | 55 | 14.884 | 4.5 | 9.7 | 135 | 9.59
42 | 142 | 55 | 14.928 | 4.5 | 9.8 | 135 | 9.71
42 | 143 | 55 | 14.972 | 4.5 | 9.9 | 135 | 9.83
42 | 144 | 55 | 15.016 | 4.5 | 10 | 135 | 9.95
42 | 145 | 55 | 15.06 | 4.6 | 3 | 135 | 4.86
42 | 146 | 55 | 15.104 | 4.6 | 3.1 | 135 | 4.98
42 | 147 | 55 | 15.148 | 4.6 | 3.2 | 135 | 5.1
42 | 148 | 55 | 15.192 | 4.6 | 3.3 | 135 | 5.22
42 | 149 | 55 | 15.236 | 4.6 | 3.4 | 135 | 5.34
42 | 150 | 55 | 15.28 | 4.6 | 3.5 | 135 | 5.46
43 | 45 | 55 | 10 | 4.6 | 3.6 | 135 | 5.58
43 | 46 | 55 | 10.0658 | 4.6 | 3.7 | 135 | 5.7
43 | 47 | 55 | 10.1316 | 4.6 | 3.8 | 135 | 5.82
43 | 48 | 55 | 10.1973 | 4.6 | 3.9 | 135 | 5.94
43 | 49 | 55 | 10.2631 | 4.6 | 4 | 135 | 6.06
43 | 50 | 55 | 10.3289 | 4.6 | 4.1 | 135 | 6.18
43 | 51 | 55 | 10.3947 | 4.6 | 4.2 | 135 | 6.3
43 | 52 | 55 | 10.4604 | 4.6 | 4.3 | 135 | 6.42
43 | 53 | 55 | 10.5262 | 4.6 | 4.4 | 135 | 6.54
43 | 54 | 55 | 10.592 | 4.6 | 4.5 | 135 | 6.66
43 | 55 | 55 | 10.6578 | 4.6 | 4.6 | 135 | 6.78
43 | 56 | 55 | 10.7236 | 4.6 | 4.7 | 135 | 6.9
43 | 57 | 55 | 10.7893 | 4.6 | 4.8 | 135 | 7.02
43 | 58 | 55 | 10.8551 | 4.6 | 4.9 | 135 | 7.14
43 | 59 | 55 | 10.9209 | 4.6 | 5 | 135 | 7.26
43 | 60 | 55 | 10.9867 | 4.6 | 5.1 | 135 | 7.293
43 | 61 | 55 | 11.0524 | 4.6 | 5.2 | 135 | 7.326
43 | 62 | 55 | 11.1182 | 4.6 | 5.3 | 135 | 7.359
43 | 63 | 55 | 11.184 | 4.6 | 5.4 | 135 | 7.392
43 | 64 | 55 | 11.2498 | 4.6 | 5.5 | 135 | 7.425
43 | 65 | 55 | 11.3156 | 4.6 | 5.6 | 135 | 7.458
43 | 66 | 55 | 11.3813 | 4.6 | 5.7 | 135 | 7.491
43 | 67 | 55 | 11.4471 | 4.6 | 5.8 | 135 | 7.524
43 | 68 | 55 | 11.5129 | 4.6 | 5.9 | 135 | 7.557
43 | 69 | 55 | 11.5787 | 4.6 | 6 | 135 | 7.59
43 | 70 | 55 | 11.6444 | 4.6 | 6.1 | 135 | 7.623
43 | 71 | 55 | 11.7102 | 4.6 | 6.2 | 135 | 7.656
43 | 72 | 55 | 11.776 | 4.6 | 6.3 | 135 | 7.689
43 | 73 | 55 | 11.8418 | 4.6 | 6.4 | 135 | 7.722
43 | 74 | 55 | 11.9076 | 4.6 | 6.5 | 135 | 7.755
43 | 75 | 55 | 11.9733 | 4.6 | 6.6 | 135 | 7.788
43 | 76 | 55 | 12.0213 | 4.6 | 6.7 | 135 | 7.821
43 | 77 | 55 | 12.0693 | 4.6 | 6.8 | 135 | 7.854
43 | 78 | 55 | 12.1173 | 4.6 | 6.9 | 135 | 7.887
43 | 79 | 55 | 12.1653 | 4.6 | 7 | 135 | 7.92
43 | 80 | 55 | 12.2133 | 4.6 | 7.1 | 135 | 7.963
43 | 81 | 55 | 12.2613 | 4.6 | 7.2 | 135 | 8.006
43 | 82 | 55 | 12.3093 | 4.6 | 7.3 | 135 | 8.049
43 | 83 | 55 | 12.3573 | 4.6 | 7.4 | 135 | 8.092
43 | 84 | 55 | 12.4053 | 4.6 | 7.5 | 135 | 8.135
43 | 85 | 55 | 12.4533 | 4.6 | 7.6 | 135 | 8.178
43 | 86 | 55 | 12.5013 | 4.6 | 7.7 | 135 | 8.221
43 | 87 | 55 | 12.5493 | 4.6 | 7.8 | 135 | 8.264
43 | 88 | 55 | 12.5973 | 4.6 | 7.9 | 135 | 8.307
43 | 89 | 55 | 12.6453 | 4.6 | 8 | 135 | 8.35
43 | 90 | 55 | 12.6933 | 4.6 | 8.1 | 135 | 8.393
43 | 91 | 55 | 12.7413 | 4.6 | 8.2 | 135 | 8.436
43 | 92 | 55 | 12.7893 | 4.6 | 8.3 | 135 | 8.479
43 | 93 | 55 | 12.8373 | 4.6 | 8.4 | 135 | 8.522
43 | 94 | 55 | 12.8853 | 4.6 | 8.5 | 135 | 8.565
43 | 95 | 55 | 12.9333 | 4.6 | 8.6 | 135 | 8.608
43 | 96 | 55 | 12.9813 | 4.6 | 8.7 | 135 | 8.651
43 | 97 | 55 | 13.0293 | 4.6 | 8.8 | 135 | 8.694
43 | 98 | 55 | 13.0773 | 4.6 | 8.9 | 135 | 8.737
43 | 99 | 55 | 13.1253 | 4.6 | 9 | 135 | 8.78
43 | 100 | 55 | 13.1733 | 4.6 | 9.1 | 135 | 8.9
43 | 101 | 55 | 13.2139 | 4.6 | 9.2 | 135 | 9.02
43 | 102 | 55 | 13.2544 | 4.6 | 9.3 | 135 | 9.14
43 | 103 | 55 | 13.2949 | 4.6 | 9.4 | 135 | 9.26
43 | 104 | 55 | 13.3355 | 4.6 | 9.5 | 135 | 9.38
43 | 105 | 55 | 13.376 | 4.6 | 9.6 | 135 | 9.5
43 | 106 | 55 | 13.4165 | 4.6 | 9.7 | 135 | 9.62
43 | 107 | 55 | 13.4571 | 4.6 | 9.8 | 135 | 9.74
43 | 108 | 55 | 13.4976 | 4.6 | 9.9 | 135 | 9.86
43 | 109 | 55 | 13.5381 | 4.6 | 10 | 135 | 9.98
43 | 110 | 55 | 13.5787 | 4.7 | 3 | 135 | 4.87
43 | 111 | 55 | 13.6192 | 4.7 | 3.1 | 135 | 4.99
43 | 112 | 55 | 13.6597 | 4.7 | 3.2 | 135 | 5.11
43 | 113 | 55 | 13.7003 | 4.7 | 3.3 | 135 | 5.23
43 | 114 | 55 | 13.7408 | 4.7 | 3.4 | 135 | 5.35
43 | 115 | 55 | 13.7813 | 4.7 | 3.5 | 135 | 5.47
43 | 116 | 55 | 13.8219 | 4.7 | 3.6 | 135 | 5.59
43 | 117 | 55 | 13.8624 | 4.7 | 3.7 | 135 | 5.71
43 | 118 | 55 | 13.9029 | 4.7 | 3.8 | 135 | 5.83
43 | 119 | 55 | 13.9435 | 4.7 | 3.9 | 135 | 5.95
43 | 120 | 55 | 13.984 | 4.7 | 4 | 135 | 6.07
43 | 121 | 55 | 14.0245 | 4.7 | 4.1 | 135 | 6.19
43 | 122 | 55 | 14.0651 | 4.7 | 4.2 | 135 | 6.31
43 | 123 | 55 | 14.1056 | 4.7 | 4.3 | 135 | 6.43
43 | 124 | 55 | 14.1461 | 4.7 | 4.4 | 135 | 6.55
43 | 125 | 55 | 14.1867 | 4.7 | 4.5 | 135 | 6.67
43 | 126 | 55 | 14.2307 | 4.7 | 4.6 | 135 | 6.79
43 | 127 | 55 | 14.2747 | 4.7 | 4.7 | 135 | 6.91
43 | 128 | 55 | 14.3187 | 4.7 | 4.8 | 135 | 7.03
43 | 129 | 55 | 14.3627 | 4.7 | 4.9 | 135 | 7.15
43 | 130 | 55 | 14.4067 | 4.7 | 5 | 135 | 7.27
43 | 131 | 55 | 14.4507 | 4.7 | 5.1 | 135 | 7.3035
43 | 132 | 55 | 14.4947 | 4.7 | 5.2 | 135 | 7.337
43 | 133 | 55 | 14.5387 | 4.7 | 5.3 | 135 | 7.3705
43 | 134 | 55 | 14.5827 | 4.7 | 5.4 | 135 | 7.404
43 | 135 | 55 | 14.6267 | 4.7 | 5.5 | 135 | 7.4375
43 | 136 | 55 | 14.6707 | 4.7 | 5.6 | 135 | 7.471
43 | 137 | 55 | 14.7147 | 4.7 | 5.7 | 135 | 7.5045
43 | 138 | 55 | 14.7587 | 4.7 | 5.8 | 135 | 7.538
43 | 139 | 55 | 14.8027 | 4.7 | 5.9 | 135 | 7.5715
43 | 140 | 55 | 14.8467 | 4.7 | 6 | 135 | 7.605
43 | 141 | 55 | 14.8907 | 4.7 | 6.1 | 135 | 7.6385
43 | 142 | 55 | 14.9347 | 4.7 | 6.2 | 135 | 7.672
43 | 143 | 55 | 14.9787 | 4.7 | 6.3 | 135 | 7.7055
43 | 144 | 55 | 15.0227 | 4.7 | 6.4 | 135 | 7.739
43 | 145 | 55 | 15.0667 | 4.7 | 6.5 | 135 | 7.7725
43 | 146 | 55 | 15.1107 | 4.7 | 6.6 | 135 | 7.806
43 | 147 | 55 | 15.1547 | 4.7 | 6.7 | 135 | 7.8395
43 | 148 | 55 | 15.1987 | 4.7 | 6.8 | 135 | 7.873
43 | 149 | 55 | 15.2427 | 4.7 | 6.9 | 135 | 7.9065
43 | 150 | 55 | 15.2867 | 4.7 | 7 | 135 | 7.94
44 | 45 | 55 | 10 | 4.7 | 7.1 | 135 | 7.9835
44 | 46 | 55 | 10.0662 | 4.7 | 7.2 | 135 | 8.027
44 | 47 | 55 | 10.1324 | 4.7 | 7.3 | 135 | 8.0705
44 | 48 | 55 | 10.1987 | 4.7 | 7.4 | 135 | 8.114
44 | 49 | 55 | 10.2649 | 4.7 | 7.5 | 135 | 8.1575
44 | 50 | 55 | 10.3311 | 4.7 | 7.6 | 135 | 8.201
44 | 51 | 55 | 10.3973 | 4.7 | 7.7 | 135 | 8.2445
44 | 52 | 55 | 10.4636 | 4.7 | 7.8 | 135 | 8.288
44 | 53 | 55 | 10.5298 | 4.7 | 7.9 | 135 | 8.3315
44 | 54 | 55 | 10.596 | 4.7 | 8 | 135 | 8.375
44 | 55 | 55 | 10.6622 | 4.7 | 8.1 | 135 | 8.4185
44 | 56 | 55 | 10.7284 | 4.7 | 8.2 | 135 | 8.462
44 | 57 | 55 | 10.7947 | 4.7 | 8.3 | 135 | 8.5055
44 | 58 | 55 | 10.8609 | 4.7 | 8.4 | 135 | 8.549
44 | 59 | 55 | 10.9271 | 4.7 | 8.5 | 135 | 8.5925
44 | 60 | 55 | 10.9933 | 4.7 | 8.6 | 135 | 8.636
44 | 61 | 55 | 11.0596 | 4.7 | 8.7 | 135 | 8.6795
44 | 62 | 55 | 11.1258 | 4.7 | 8.8 | 135 | 8.723
44 | 63 | 55 | 11.192 | 4.7 | 8.9 | 135 | 8.7665
44 | 64 | 55 | 11.2582 | 4.7 | 9 | 135 | 8.81
44 | 65 | 55 | 11.3244 | 4.7 | 9.1 | 135 | 8.93
44 | 66 | 55 | 11.3907 | 4.7 | 9.2 | 135 | 9.05
44 | 67 | 55 | 11.4569 | 4.7 | 9.3 | 135 | 9.17
44 | 68 | 55 | 11.5231 | 4.7 | 9.4 | 135 | 9.29
44 | 69 | 55 | 11.5893 | 4.7 | 9.5 | 135 | 9.41
44 | 70 | 55 | 11.6556 | 4.7 | 9.6 | 135 | 9.53
44 | 71 | 55 | 11.7218 | 4.7 | 9.7 | 135 | 9.65
44 | 72 | 55 | 11.788 | 4.7 | 9.8 | 135 | 9.77
44 | 73 | 55 | 11.8542 | 4.7 | 9.9 | 135 | 9.89
44 | 74 | 55 | 11.9204 | 4.7 | 10 | 135 | 10.01
44 | 75 | 55 | 11.9867 | 4.8 | 3 | 135 | 4.88
44 | 76 | 55 | 12.0347 | 4.8 | 3.1 | 135 | 5
44 | 77 | 55 | 12.0827 | 4.8 | 3.2 | 135 | 5.12
44 | 78 | 55 | 12.1307 | 4.8 | 3.3 | 135 | 5.24
44 | 79 | 55 | 12.1787 | 4.8 | 3.4 | 135 | 5.36
44 | 80 | 55 | 12.2267 | 4.8 | 3.5 | 135 | 5.48
44 | 81 | 55 | 12.2747 | 4.8 | 3.6 | 135 | 5.6
44 | 82 | 55 | 12.3227 | 4.8 | 3.7 | 135 | 5.72
44 | 83 | 55 | 12.3707 | 4.8 | 3.8 | 135 | 5.84
44 | 84 | 55 | 12.4187 | 4.8 | 3.9 | 135 | 5.96
44 | 85 | 55 | 12.4667 | 4.8 | 4 | 135 | 6.08
44 | 86 | 55 | 12.5147 | 4.8 | 4.1 | 135 | 6.2
44 | 87 | 55 | 12.5627 | 4.8 | 4.2 | 135 | 6.32
44 | 88 | 55 | 12.6107 | 4.8 | 4.3 | 135 | 6.44
44 | 89 | 55 | 12.6587 | 4.8 | 4.4 | 135 | 6.56
44 | 90 | 55 | 12.7067 | 4.8 | 4.5 | 135 | 6.68
44 | 91 | 55 | 12.7547 | 4.8 | 4.6 | 135 | 6.8
44 | 92 | 55 | 12.8027 | 4.8 | 4.7 | 135 | 6.92
44 | 93 | 55 | 12.8507 | 4.8 | 4.8 | 135 | 7.04
44 | 94 | 55 | 12.8987 | 4.8 | 4.9 | 135 | 7.16
44 | 95 | 55 | 12.9467 | 4.8 | 5 | 135 | 7.28
44 | 96 | 55 | 12.9947 | 4.8 | 5.1 | 135 | 7.314
44 | 97 | 55 | 13.0427 | 4.8 | 5.2 | 135 | 7.348
44 | 98 | 55 | 13.0907 | 4.8 | 5.3 | 135 | 7.382
44 | 99 | 55 | 13.1387 | 4.8 | 5.4 | 135 | 7.416
44 | 100 | 55 | 13.1867 | 4.8 | 5.5 | 135 | 7.45
44 | 101 | 55 | 13.2269 | 4.8 | 5.6 | 135 | 7.484
44 | 102 | 55 | 13.2672 | 4.8 | 5.7 | 135 | 7.518
44 | 103 | 55 | 13.3075 | 4.8 | 5.8 | 135 | 7.552
44 | 104 | 55 | 13.3477 | 4.8 | 5.9 | 135 | 7.586
44 | 105 | 55 | 13.388 | 4.8 | 6 | 135 | 7.62
44 | 106 | 55 | 13.4283 | 4.8 | 6.1 | 135 | 7.654
44 | 107 | 55 | 13.4685 | 4.8 | 6.2 | 135 | 7.688
44 | 108 | 55 | 13.5088 | 4.8 | 6.3 | 135 | 7.722
44 | 109 | 55 | 13.5491 | 4.8 | 6.4 | 135 | 7.756
44 | 110 | 55 | 13.5893 | 4.8 | 6.5 | 135 | 7.79
44 | 111 | 55 | 13.6296 | 4.8 | 6.6 | 135 | 7.824
44 | 112 | 55 | 13.6699 | 4.8 | 6.7 | 135 | 7.858
44 | 113 | 55 | 13.7101 | 4.8 | 6.8 | 135 | 7.892
44 | 114 | 55 | 13.7504 | 4.8 | 6.9 | 135 | 7.926
44 | 115 | 55 | 13.7907 | 4.8 | 7 | 135 | 7.96
44 | 116 | 55 | 13.8309 | 4.8 | 7.1 | 135 | 8.004
44 | 117 | 55 | 13.8712 | 4.8 | 7.2 | 135 | 8.048
44 | 118 | 55 | 13.9115 | 4.8 | 7.3 | 135 | 8.092
44 | 119 | 55 | 13.9517 | 4.8 | 7.4 | 135 | 8.136
44 | 120 | 55 | 13.992 | 4.8 | 7.5 | 135 | 8.18
44 | 121 | 55 | 14.0323 | 4.8 | 7.6 | 135 | 8.224
44 | 122 | 55 | 14.0725 | 4.8 | 7.7 | 135 | 8.268
44 | 123 | 55 | 14.1128 | 4.8 | 7.8 | 135 | 8.312
44 | 124 | 55 | 14.1531 | 4.8 | 7.9 | 135 | 8.356
44 | 125 | 55 | 14.1933 | 4.8 | 8 | 135 | 8.4
44 | 126 | 55 | 14.2373 | 4.8 | 8.1 | 135 | 8.444
44 | 127 | 55 | 14.2813 | 4.8 | 8.2 | 135 | 8.488
44 | 128 | 55 | 14.3253 | 4.8 | 8.3 | 135 | 8.532
44 | 129 | 55 | 14.3693 | 4.8 | 8.4 | 135 | 8.576
44 | 130 | 55 | 14.4133 | 4.8 | 8.5 | 135 | 8.62
44 | 131 | 55 | 14.4573 | 4.8 | 8.6 | 135 | 8.664
44 | 132 | 55 | 14.5013 | 4.8 | 8.7 | 135 | 8.708
44 | 133 | 55 | 14.5453 | 4.8 | 8.8 | 135 | 8.752
44 | 134 | 55 | 14.5893 | 4.8 | 8.9 | 135 | 8.796
44 | 135 | 55 | 14.6333 | 4.8 | 9 | 135 | 8.84
44 | 136 | 55 | 14.6773 | 4.8 | 9.1 | 135 | 8.96
44 | 137 | 55 | 14.7213 | 4.8 | 9.2 | 135 | 9.08
44 | 138 | 55 | 14.7653 | 4.8 | 9.3 | 135 | 9.2
44 | 139 | 55 | 14.8093 | 4.8 | 9.4 | 135 | 9.32
44 | 140 | 55 | 14.8533 | 4.8 | 9.5 | 135 | 9.44
44 | 141 | 55 | 14.8973 | 4.8 | 9.6 | 135 | 9.56
44 | 142 | 55 | 14.9413 | 4.8 | 9.7 | 135 | 9.68
44 | 143 | 55 | 14.9853 | 4.8 | 9.8 | 135 | 9.8
44 | 144 | 55 | 15.0293 | 4.8 | 9.9 | 135 | 9.92
44 | 145 | 55 | 15.0733 | 4.8 | 10 | 135 | 10.04
44 | 146 | 55 | 15.1173 | 4.9 | 3 | 135 | 4.89
44 | 147 | 55 | 15.1613 | 4.9 | 3.1 | 135 | 5.01
44 | 148 | 55 | 15.2053 | 4.9 | 3.2 | 135 | 5.13
44 | 149 | 55 | 15.2493 | 4.9 | 3.3 | 135 | 5.25
44 | 150 | 55 | 15.2933 | 4.9 | 3.4 | 135 | 5.37
45 | 45 | 55 | 10 | 4.9 | 3.5 | 135 | 5.49
45 | 46 | 55 | 10.0667 | 4.9 | 3.6 | 135 | 5.61
45 | 47 | 55 | 10.1333 | 4.9 | 3.7 | 135 | 5.73
45 | 48 | 55 | 10.2 | 4.9 | 3.8 | 135 | 5.85
45 | 49 | 55 | 10.2667 | 4.9 | 3.9 | 135 | 5.97
45 | 50 | 55 | 10.3333 | 4.9 | 4 | 135 | 6.09
45 | 51 | 55 | 10.4 | 4.9 | 4.1 | 135 | 6.21
45 | 52 | 55 | 10.4667 | 4.9 | 4.2 | 135 | 6.33
45 | 53 | 55 | 10.5333 | 4.9 | 4.3 | 135 | 6.45
45 | 54 | 55 | 10.6 | 4.9 | 4.4 | 135 | 6.57
45 | 55 | 55 | 10.6667 | 4.9 | 4.5 | 135 | 6.69
45 | 56 | 55 | 10.7333 | 4.9 | 4.6 | 135 | 6.81
45 | 57 | 55 | 10.8 | 4.9 | 4.7 | 135 | 6.93
45 | 58 | 55 | 10.8667 | 4.9 | 4.8 | 135 | 7.05
45 | 59 | 55 | 10.9333 | 4.9 | 4.9 | 135 | 7.17
45 | 60 | 55 | 11 | 4.9 | 5 | 135 | 7.29
45 | 61 | 55 | 11.0667 | 4.9 | 5.1 | 135 | 7.3245
45 | 62 | 55 | 11.1333 | 4.9 | 5.2 | 135 | 7.359
45 | 63 | 55 | 11.2 | 4.9 | 5.3 | 135 | 7.3935
45 | 64 | 55 | 11.2667 | 4.9 | 5.4 | 135 | 7.428
45 | 65 | 55 | 11.3333 | 4.9 | 5.5 | 135 | 7.4625
45 | 66 | 55 | 11.4 | 4.9 | 5.6 | 135 | 7.497
45 | 67 | 55 | 11.4667 | 4.9 | 5.7 | 135 | 7.5315
45 | 68 | 55 | 11.5333 | 4.9 | 5.8 | 135 | 7.566
45 | 69 | 55 | 11.6 | 4.9 | 5.9 | 135 | 7.6005
45 | 70 | 55 | 11.6667 | 4.9 | 6 | 135 | 7.635
45 | 71 | 55 | 11.7333 | 4.9 | 6.1 | 135 | 7.6695
45 | 72 | 55 | 11.8 | 4.9 | 6.2 | 135 | 7.704
45 | 73 | 55 | 11.8667 | 4.9 | 6.3 | 135 | 7.7385
45 | 74 | 55 | 11.9333 | 4.9 | 6.4 | 135 | 7.773
45 | 75 | 55 | 12 | 4.9 | 6.5 | 135 | 7.8075
45 | 76 | 55 | 12.048 | 4.9 | 6.6 | 135 | 7.842
45 | 77 | 55 | 12.096 | 4.9 | 6.7 | 135 | 7.8765
45 | 78 | 55 | 12.144 | 4.9 | 6.8 | 135 | 7.911
45 | 79 | 55 | 12.192 | 4.9 | 6.9 | 135 | 7.9455
45 | 80 | 55 | 12.24 | 4.9 | 7 | 135 | 7.98
45 | 81 | 55 | 12.288 | 4.9 | 7.1 | 135 | 8.0245
45 | 82 | 55 | 12.336 | 4.9 | 7.2 | 135 | 8.069
45 | 83 | 55 | 12.384 | 4.9 | 7.3 | 135 | 8.1135
45 | 84 | 55 | 12.432 | 4.9 | 7.4 | 135 | 8.158
45 | 85 | 55 | 12.48 | 4.9 | 7.5 | 135 | 8.2025
45 | 86 | 55 | 12.528 | 4.9 | 7.6 | 135 | 8.247
45 | 87 | 55 | 12.576 | 4.9 | 7.7 | 135 | 8.2915
45 | 88 | 55 | 12.624 | 4.9 | 7.8 | 135 | 8.336
45 | 89 | 55 | 12.672 | 4.9 | 7.9 | 135 | 8.3805
45 | 90 | 55 | 12.72 | 4.9 | 8 | 135 | 8.425
45 | 91 | 55 | 12.768 | 4.9 | 8.1 | 135 | 8.4695
45 | 92 | 55 | 12.816 | 4.9 | 8.2 | 135 | 8.514
45 | 93 | 55 | 12.864 | 4.9 | 8.3 | 135 | 8.5585
45 | 94 | 55 | 12.912 | 4.9 | 8.4 | 135 | 8.603
45 | 95 | 55 | 12.96 | 4.9 | 8.5 | 135 | 8.6475
45 | 96 | 55 | 13.008 | 4.9 | 8.6 | 135 | 8.692
45 | 97 | 55 | 13.056 | 4.9 | 8.7 | 135 | 8.7365
45 | 98 | 55 | 13.104 | 4.9 | 8.8 | 135 | 8.781
45 | 99 | 55 | 13.152 | 4.9 | 8.9 | 135 | 8.8255
45 | 100 | 55 | 13.2 | 4.9 | 9 | 135 | 8.87
45 | 101 | 55 | 13.24 | 4.9 | 9.1 | 135 | 8.99
45 | 102 | 55 | 13.28 | 4.9 | 9.2 | 135 | 9.11
45 | 103 | 55 | 13.32 | 4.9 | 9.3 | 135 | 9.23
45 | 104 | 55 | 13.36 | 4.9 | 9.4 | 135 | 9.35
45 | 105 | 55 | 13.4 | 4.9 | 9.5 | 135 | 9.47
45 | 106 | 55 | 13.44 | 4.9 | 9.6 | 135 | 9.59
45 | 107 | 55 | 13.48 | 4.9 | 9.7 | 135 | 9.71
45 | 108 | 55 | 13.52 | 4.9 | 9.8 | 135 | 9.83
45 | 109 | 55 | 13.56 | 4.9 | 9.9 | 135 | 9.95
45 | 110 | 55 | 13.6 | 4.9 | 10 | 135 | 10.07
45 | 111 | 55 | 13.64 | 5 | 3 | 135 | 4.9
45 | 112 | 55 | 13.68 | 5 | 3.1 | 135 | 5.02
45 | 113 | 55 | 13.72 | 5 | 3.2 | 135 | 5.14
45 | 114 | 55 | 13.76 | 5 | 3.3 | 135 | 5.26
45 | 115 | 55 | 13.8 | 5 | 3.4 | 135 | 5.38
45 | 116 | 55 | 13.84 | 5 | 3.5 | 135 | 5.5
45 | 117 | 55 | 13.88 | 5 | 3.6 | 135 | 5.62
45 | 118 | 55 | 13.92 | 5 | 3.7 | 135 | 5.74
45 | 119 | 55 | 13.96 | 5 | 3.8 | 135 | 5.86
45 | 120 | 55 | 14 | 5 | 3.9 | 135 | 5.98
45 | 121 | 55 | 14.04 | 5 | 4 | 135 | 6.1
45 | 122 | 55 | 14.08 | 5 | 4.1 | 135 | 6.22
45 | 123 | 55 | 14.12 | 5 | 4.2 | 135 | 6.34
45 | 124 | 55 | 14.16 | 5 | 4.3 | 135 | 6.46
45 | 125 | 55 | 14.2 | 5 | 4.4 | 135 | 6.58
45 | 126 | 55 | 14.244 | 5 | 4.5 | 135 | 6.7
45 | 127 | 55 | 14.288 | 5 | 4.6 | 135 | 6.82
45 | 128 | 55 | 14.332 | 5 | 4.7 | 135 | 6.94
45 | 129 | 55 | 14.376 | 5 | 4.8 | 135 | 7.06
45 | 130 | 55 | 14.42 | 5 | 4.9 | 135 | 7.18
45 | 131 | 55 | 14.464 | 5 | 5 | 135 | 7.3
45 | 132 | 55 | 14.508 | 5 | 5.1 | 135 | 7.335
45 | 133 | 55 | 14.552 | 5 | 5.2 | 135 | 7.37
45 | 134 | 55 | 14.596 | 5 | 5.3 | 135 | 7.405
45 | 135 | 55 | 14.64 | 5 | 5.4 | 135 | 7.44
45 | 136 | 55 | 14.684 | 5 | 5.5 | 135 | 7.475
45 | 137 | 55 | 14.728 | 5 | 5.6 | 135 | 7.51
45 | 138 | 55 | 14.772 | 5 | 5.7 | 135 | 7.545
45 | 139 | 55 | 14.816 | 5 | 5.8 | 135 | 7.58
45 | 140 | 55 | 14.86 | 5 | 5.9 | 135 | 7.615
45 | 141 | 55 | 14.904 | 5 | 6 | 135 | 7.65
45 | 142 | 55 | 14.948 | 5 | 6.1 | 135 | 7.685
45 | 143 | 55 | 14.992 | 5 | 6.2 | 135 | 7.72
45 | 144 | 55 | 15.036 | 5 | 6.3 | 135 | 7.755
45 | 145 | 55 | 15.08 | 5 | 6.4 | 135 | 7.79
45 | 146 | 55 | 15.124 | 5 | 6.5 | 135 | 7.825
45 | 147 | 55 | 15.168 | 5 | 6.6 | 135 | 7.86
45 | 148 | 55 | 15.212 | 5 | 6.7 | 135 | 7.895
45 | 149 | 55 | 15.256 | 5 | 6.8 | 135 | 7.93
45 | 150 | 55 | 15.3 | 5 | 6.9 | 135 | 7.965
46 | 45 | 55 | 10.0133 | 5 | 7 | 135 | 8
46 | 46 | 55 | 10.0798 | 5 | 7.1 | 135 | 8.045
46 | 47 | 55 | 10.1462 | 5 | 7.2 | 135 | 8.09
46 | 48 | 55 | 10.2127 | 5 | 7.3 | 135 | 8.135
46 | 49 | 55 | 10.2791 | 5 | 7.4 | 135 | 8.18
46 | 50 | 55 | 10.3456 | 5 | 7.5 | 135 | 8.225
46 | 51 | 55 | 10.412 | 5 | 7.6 | 135 | 8.27
46 | 52 | 55 | 10.4784 | 5 | 7.7 | 135 | 8.315
46 | 53 | 55 | 10.5449 | 5 | 7.8 | 135 | 8.36
46 | 54 | 55 | 10.6113 | 5 | 7.9 | 135 | 8.405
46 | 55 | 55 | 10.6778 | 5 | 8 | 135 | 8.45
46 | 56 | 55 | 10.7442 | 5 | 8.1 | 135 | 8.495
46 | 57 | 55 | 10.8107 | 5 | 8.2 | 135 | 8.54
46 | 58 | 55 | 10.8771 | 5 | 8.3 | 135 | 8.585
46 | 59 | 55 | 10.9436 | 5 | 8.4 | 135 | 8.63
46 | 60 | 55 | 11.01 | 5 | 8.5 | 135 | 8.675
46 | 61 | 55 | 11.0764 | 5 | 8.6 | 135 | 8.72
46 | 62 | 55 | 11.1429 | 5 | 8.7 | 135 | 8.765
46 | 63 | 55 | 11.2093 | 5 | 8.8 | 135 | 8.81
46 | 64 | 55 | 11.2758 | 5 | 8.9 | 135 | 8.855
46 | 65 | 55 | 11.3422 | 5 | 9 | 135 | 8.9
46 | 66 | 55 | 11.4087 | 5 | 9.1 | 135 | 9.02
46 | 67 | 55 | 11.4751 | 5 | 9.2 | 135 | 9.14
46 | 68 | 55 | 11.5416 | 5 | 9.3 | 135 | 9.26
46 | 69 | 55 | 11.608 | 5 | 9.4 | 135 | 9.38
46 | 70 | 55 | 11.6744 | 5 | 9.5 | 135 | 9.5
46 | 71 | 55 | 11.7409 | 5 | 9.6 | 135 | 9.62
46 | 72 | 55 | 11.8073 | 5 | 9.7 | 135 | 9.74
46 | 73 | 55 | 11.8738 | 5 | 9.8 | 135 | 9.86
46 | 74 | 55 | 11.9402 | 5 | 9.9 | 135 | 9.98
46 | 75 | 55 | 12.0067 | 5 | 10 | 135 | 10.1
46 | 76 | 55 | 12.0565 | 2 | 3 | 0 | 13.1
46 | 77 | 55 | 12.1064 | 2 | 3.1 | 0 | 13.1
46 | 78 | 55 | 12.1563 | 2 | 3.2 | 0 | 13.1
46 | 79 | 55 | 12.2061 | 2 | 3.3 | 0 | 13.1
46 | 80 | 55 | 12.256 | 2 | 3.4 | 0 | 13.1
46 | 81 | 55 | 12.3059 | 2 | 3.5 | 0 | 13.1
46 | 82 | 55 | 12.3557 | 2 | 3.6 | 0 | 13.1
46 | 83 | 55 | 12.4056 | 2 | 3.7 | 0 | 13.1
46 | 84 | 55 | 12.4555 | 2 | 3.8 | 0 | 13.1
46 | 85 | 55 | 12.5053 | 2 | 3.9 | 0 | 13.1
46 | 86 | 55 | 12.5552 | 2 | 4 | 0 | 13.1
46 | 87 | 55 | 12.6051 | 2 | 4.1 | 0 | 13.1
46 | 88 | 55 | 12.6549 | 2 | 4.2 | 0 | 13.1
46 | 89 | 55 | 12.7048 | 2 | 4.3 | 0 | 13.1
46 | 90 | 55 | 12.7547 | 2 | 4.4 | 0 | 13.1
46 | 91 | 55 | 12.8045 | 2 | 4.5 | 0 | 13.1
46 | 92 | 55 | 12.8544 | 2 | 4.6 | 0 | 13.1
46 | 93 | 55 | 12.9043 | 2 | 4.7 | 0 | 13.1
46 | 94 | 55 | 12.9541 | 2 | 4.8 | 0 | 13.1
46 | 95 | 55 | 13.004 | 2 | 4.9 | 0 | 13.1
46 | 96 | 55 | 13.0539 | 2 | 5 | 0 | 13.1
46 | 97 | 55 | 13.1037 | 2 | 5.1 | 0 | 13.1
46 | 98 | 55 | 13.1536 | 2 | 5.2 | 0 | 13.1
46 | 99 | 55 | 13.2035 | 2 | 5.3 | 0 | 13.1
46 | 100 | 55 | 13.2533 | 2 | 5.4 | 0 | 13.1
46 | 101 | 55 | 13.2915 | 2 | 5.5 | 0 | 13.1
46 | 102 | 55 | 13.3296 | 2 | 5.6 | 0 | 13.1
46 | 103 | 55 | 13.3677 | 2 | 5.7 | 0 | 13.1
46 | 104 | 55 | 13.4059 | 2 | 5.8 | 0 | 13.1
46 | 105 | 55 | 13.444 | 2 | 5.9 | 0 | 13.1
46 | 106 | 55 | 13.4821 | 2 | 6 | 0 | 13.1
46 | 107 | 55 | 13.5203 | 2 | 6.1 | 0 | 13.1
46 | 108 | 55 | 13.5584 | 2 | 6.2 | 0 | 13.1
46 | 109 | 55 | 13.5965 | 2 | 6.3 | 0 | 13.1
46 | 110 | 55 | 13.6347 | 2 | 6.4 | 0 | 13.1
46 | 111 | 55 | 13.6728 | 2 | 6.5 | 0 | 13.1
46 | 112 | 55 | 13.7109 | 2 | 6.6 | 0 | 13.1
46 | 113 | 55 | 13.7491 | 2 | 6.7 | 0 | 13.1
46 | 114 | 55 | 13.7872 | 2 | 6.8 | 0 | 13.1
46 | 115 | 55 | 13.8253 | 2 | 6.9 | 0 | 13.1
46 | 116 | 55 | 13.8635 | 2 | 7 | 0 | 13.1
46 | 117 | 55 | 13.9016 | 2 | 7.1 | 0 | 13.1
46 | 118 | 55 | 13.9397 | 2 | 7.2 | 0 | 13.1
46 | 119 | 55 | 13.9779 | 2 | 7.3 | 0 | 13.1
46 | 120 | 55 | 14.016 | 2 | 7.4 | 0 | 13.1
46 | 121 | 55 | 14.0541 | 2 | 7.5 | 0 | 13.1
46 | 122 | 55 | 14.0923 | 2 | 7.6 | 0 | 13.1
46 | 123 | 55 | 14.1304 | 2 | 7.7 | 0 | 13.1
46 | 124 | 55 | 14.1685 | 2 | 7.8 | 0 | 13.1
46 | 125 | 55 | 14.2067 | 2 | 7.9 | 0 | 13.1
46 | 126 | 55 | 14.2512 | 2 | 8 | 0 | 13.1
46 | 127 | 55 | 14.2957 | 2 | 8.1 | 0 | 13.1
46 | 128 | 55 | 14.3403 | 2 | 8.2 | 0 | 13.1
46 | 129 | 55 | 14.3848 | 2 | 8.3 | 0 | 13.1
46 | 130 | 55 | 14.4293 | 2 | 8.4 | 0 | 13.1
46 | 131 | 55 | 14.4739 | 2 | 8.5 | 0 | 13.1
46 | 132 | 55 | 14.5184 | 2 | 8.6 | 0 | 13.1
46 | 133 | 55 | 14.5629 | 2 | 8.7 | 0 | 13.1
46 | 134 | 55 | 14.6075 | 2 | 8.8 | 0 | 13.1
46 | 135 | 55 | 14.652 | 2 | 8.9 | 0 | 13.1
46 | 136 | 55 | 14.6965 | 2 | 9 | 0 | 13.1
46 | 137 | 55 | 14.7411 | 2 | 9.1 | 0 | 13.1
46 | 138 | 55 | 14.7856 | 2 | 9.2 | 0 | 13.1
46 | 139 | 55 | 14.8301 | 2 | 9.3 | 0 | 13.1
46 | 140 | 55 | 14.8747 | 2 | 9.4 | 0 | 13.1
46 | 141 | 55 | 14.9192 | 2 | 9.5 | 0 | 13.1
46 | 142 | 55 | 14.9637 | 2 | 9.6 | 0 | 13.1
46 | 143 | 55 | 15.0083 | 2 | 9.7 | 0 | 13.1
46 | 144 | 55 | 15.0528 | 2 | 9.8 | 0 | 13.1
46 | 145 | 55 | 15.0973 | 2 | 9.9 | 0 | 13.1
46 | 146 | 55 | 15.1419 | 2 | 10 | 0 | 13.1
46 | 147 | 55 | 15.1864 | 2.1 | 3 | 0 | 13.12
46 | 148 | 55 | 15.2309 | 2.1 | 3.1 | 0 | 13.12
46 | 149 | 55 | 15.2755 | 2.1 | 3.2 | 0 | 13.12
46 | 150 | 55 | 15.32 | 2.1 | 3.3 | 0 | 13.12
47 | 45 | 55 | 10.0267 | 2.1 | 3.4 | 0 | 13.12
47 | 46 | 55 | 10.0929 | 2.1 | 3.5 | 0 | 13.12
47 | 47 | 55 | 10.1591 | 2.1 | 3.6 | 0 | 13.12
47 | 48 | 55 | 10.2253 | 2.1 | 3.7 | 0 | 13.12
47 | 49 | 55 | 10.2916 | 2.1 | 3.8 | 0 | 13.12
47 | 50 | 55 | 10.3578 | 2.1 | 3.9 | 0 | 13.12
47 | 51 | 55 | 10.424 | 2.1 | 4 | 0 | 13.12
47 | 52 | 55 | 10.4902 | 2.1 | 4.1 | 0 | 13.12
47 | 53 | 55 | 10.5564 | 2.1 | 4.2 | 0 | 13.12
47 | 54 | 55 | 10.6227 | 2.1 | 4.3 | 0 | 13.12
47 | 55 | 55 | 10.6889 | 2.1 | 4.4 | 0 | 13.12
47 | 56 | 55 | 10.7551 | 2.1 | 4.5 | 0 | 13.12
47 | 57 | 55 | 10.8213 | 2.1 | 4.6 | 0 | 13.12
47 | 58 | 55 | 10.8876 | 2.1 | 4.7 | 0 | 13.12
47 | 59 | 55 | 10.9538 | 2.1 | 4.8 | 0 | 13.12
47 | 60 | 55 | 11.02 | 2.1 | 4.9 | 0 | 13.12
47 | 61 | 55 | 11.0862 | 2.1 | 5 | 0 | 13.12
47 | 62 | 55 | 11.1524 | 2.1 | 5.1 | 0 | 13.12
47 | 63 | 55 | 11.2187 | 2.1 | 5.2 | 0 | 13.12
47 | 64 | 55 | 11.2849 | 2.1 | 5.3 | 0 | 13.12
47 | 65 | 55 | 11.3511 | 2.1 | 5.4 | 0 | 13.12
47 | 66 | 55 | 11.4173 | 2.1 | 5.5 | 0 | 13.12
47 | 67 | 55 | 11.4836 | 2.1 | 5.6 | 0 | 13.12
47 | 68 | 55 | 11.5498 | 2.1 | 5.7 | 0 | 13.12
47 | 69 | 55 | 11.616 | 2.1 | 5.8 | 0 | 13.12
47 | 70 | 55 | 11.6822 | 2.1 | 5.9 | 0 | 13.12
47 | 71 | 55 | 11.7484 | 2.1 | 6 | 0 | 13.12
47 | 72 | 55 | 11.8147 | 2.1 | 6.1 | 0 | 13.12
47 | 73 | 55 | 11.8809 | 2.1 | 6.2 | 0 | 13.12
47 | 74 | 55 | 11.9471 | 2.1 | 6.3 | 0 | 13.12
47 | 75 | 55 | 12.0133 | 2.1 | 6.4 | 0 | 13.12
47 | 76 | 55 | 12.0651 | 2.1 | 6.5 | 0 | 13.12
47 | 77 | 55 | 12.1168 | 2.1 | 6.6 | 0 | 13.12
47 | 78 | 55 | 12.1685 | 2.1 | 6.7 | 0 | 13.12
47 | 79 | 55 | 12.2203 | 2.1 | 6.8 | 0 | 13.12
47 | 80 | 55 | 12.272 | 2.1 | 6.9 | 0 | 13.12
47 | 81 | 55 | 12.3237 | 2.1 | 7 | 0 | 13.12
47 | 82 | 55 | 12.3755 | 2.1 | 7.1 | 0 | 13.12
47 | 83 | 55 | 12.4272 | 2.1 | 7.2 | 0 | 13.12
47 | 84 | 55 | 12.4789 | 2.1 | 7.3 | 0 | 13.12
47 | 85 | 55 | 12.5307 | 2.1 | 7.4 | 0 | 13.12
47 | 86 | 55 | 12.5824 | 2.1 | 7.5 | 0 | 13.12
47 | 87 | 55 | 12.6341 | 2.1 | 7.6 | 0 | 13.12
47 | 88 | 55 | 12.6859 | 2.1 | 7.7 | 0 | 13.12
47 | 89 | 55 | 12.7376 | 2.1 | 7.8 | 0 | 13.12
47 | 90 | 55 | 12.7893 | 2.1 | 7.9 | 0 | 13.12
47 | 91 | 55 | 12.8411 | 2.1 | 8 | 0 | 13.12
47 | 92 | 55 | 12.8928 | 2.1 | 8.1 | 0 | 13.12
47 | 93 | 55 | 12.9445 | 2.1 | 8.2 | 0 | 13.12
47 | 94 | 55 | 12.9963 | 2.1 | 8.3 | 0 | 13.12
47 | 95 | 55 | 13.048 | 2.1 | 8.4 | 0 | 13.12
47 | 96 | 55 | 13.0997 | 2.1 | 8.5 | 0 | 13.12
47 | 97 | 55 | 13.1515 | 2.1 | 8.6 | 0 | 13.12
47 | 98 | 55 | 13.2032 | 2.1 | 8.7 | 0 | 13.12
47 | 99 | 55 | 13.2549 | 2.1 | 8.8 | 0 | 13.12
47 | 100 | 55 | 13.3067 | 2.1 | 8.9 | 0 | 13.12
47 | 101 | 55 | 13.3429 | 2.1 | 9 | 0 | 13.12
47 | 102 | 55 | 13.3792 | 2.1 | 9.1 | 0 | 13.12
47 | 103 | 55 | 13.4155 | 2.1 | 9.2 | 0 | 13.12
47 | 104 | 55 | 13.4517 | 2.1 | 9.3 | 0 | 13.12
47 | 105 | 55 | 13.488 | 2.1 | 9.4 | 0 | 13.12
47 | 106 | 55 | 13.5243 | 2.1 | 9.5 | 0 | 13.12
47 | 107 | 55 | 13.5605 | 2.1 | 9.6 | 0 | 13.12
47 | 108 | 55 | 13.5968 | 2.1 | 9.7 | 0 | 13.12
47 | 109 | 55 | 13.6331 | 2.1 | 9.8 | 0 | 13.12
47 | 110 | 55 | 13.6693 | 2.1 | 9.9 | 0 | 13.12
47 | 111 | 55 | 13.7056 | 2.1 | 10 | 0 | 13.12
47 | 112 | 55 | 13.7419 | 2.2 | 3 | 0 | 13.14
47 | 113 | 55 | 13.7781 | 2.2 | 3.1 | 0 | 13.14
47 | 114 | 55 | 13.8144 | 2.2 | 3.2 | 0 | 13.14
47 | 115 | 55 | 13.8507 | 2.2 | 3.3 | 0 | 13.14
47 | 116 | 55 | 13.8869 | 2.2 | 3.4 | 0 | 13.14
47 | 117 | 55 | 13.9232 | 2.2 | 3.5 | 0 | 13.14
47 | 118 | 55 | 13.9595 | 2.2 | 3.6 | 0 | 13.14
47 | 119 | 55 | 13.9957 | 2.2 | 3.7 | 0 | 13.14
47 | 120 | 55 | 14.032 | 2.2 | 3.8 | 0 | 13.14
47 | 121 | 55 | 14.0683 | 2.2 | 3.9 | 0 | 13.14
47 | 122 | 55 | 14.1045 | 2.2 | 4 | 0 | 13.14
47 | 123 | 55 | 14.1408 | 2.2 | 4.1 | 0 | 13.14
47 | 124 | 55 | 14.1771 | 2.2 | 4.2 | 0 | 13.14
47 | 125 | 55 | 14.2133 | 2.2 | 4.3 | 0 | 13.14
47 | 126 | 55 | 14.2584 | 2.2 | 4.4 | 0 | 13.14
47 | 127 | 55 | 14.3035 | 2.2 | 4.5 | 0 | 13.14
47 | 128 | 55 | 14.3485 | 2.2 | 4.6 | 0 | 13.14
47 | 129 | 55 | 14.3936 | 2.2 | 4.7 | 0 | 13.14
47 | 130 | 55 | 14.4387 | 2.2 | 4.8 | 0 | 13.14
47 | 131 | 55 | 14.4837 | 2.2 | 4.9 | 0 | 13.14
47 | 132 | 55 | 14.5288 | 2.2 | 5 | 0 | 13.14
47 | 133 | 55 | 14.5739 | 2.2 | 5.1 | 0 | 13.14
47 | 134 | 55 | 14.6189 | 2.2 | 5.2 | 0 | 13.14
47 | 135 | 55 | 14.664 | 2.2 | 5.3 | 0 | 13.14
47 | 136 | 55 | 14.7091 | 2.2 | 5.4 | 0 | 13.14
47 | 137 | 55 | 14.7541 | 2.2 | 5.5 | 0 | 13.14
47 | 138 | 55 | 14.7992 | 2.2 | 5.6 | 0 | 13.14
47 | 139 | 55 | 14.8443 | 2.2 | 5.7 | 0 | 13.14
47 | 140 | 55 | 14.8893 | 2.2 | 5.8 | 0 | 13.14
47 | 141 | 55 | 14.9344 | 2.2 | 5.9 | 0 | 13.14
47 | 142 | 55 | 14.9795 | 2.2 | 6 | 0 | 13.14
47 | 143 | 55 | 15.0245 | 2.2 | 6.1 | 0 | 13.14
47 | 144 | 55 | 15.0696 | 2.2 | 6.2 | 0 | 13.14
47 | 145 | 55 | 15.1147 | 2.2 | 6.3 | 0 | 13.14
47 | 146 | 55 | 15.1597 | 2.2 | 6.4 | 0 | 13.14
47 | 147 | 55 | 15.2048 | 2.2 | 6.5 | 0 | 13.14
47 | 148 | 55 | 15.2499 | 2.2 | 6.6 | 0 | 13.14
47 | 149 | 55 | 15.2949 | 2.2 | 6.7 | 0 | 13.14
47 | 150 | 55 | 15.34 | 2.2 | 6.8 | 0 | 13.14
48 | 45 | 55 | 10.04 | 2.2 | 6.9 | 0 | 13.14
48 | 46 | 55 | 10.106 | 2.2 | 7 | 0 | 13.14
48 | 47 | 55 | 10.172 | 2.2 | 7.1 | 0 | 13.14
48 | 48 | 55 | 10.238 | 2.2 | 7.2 | 0 | 13.14
48 | 49 | 55 | 10.304 | 2.2 | 7.3 | 0 | 13.14
48 | 50 | 55 | 10.37 | 2.2 | 7.4 | 0 | 13.14
48 | 51 | 55 | 10.436 | 2.2 | 7.5 | 0 | 13.14
48 | 52 | 55 | 10.502 | 2.2 | 7.6 | 0 | 13.14
48 | 53 | 55 | 10.568 | 2.2 | 7.7 | 0 | 13.14
48 | 54 | 55 | 10.634 | 2.2 | 7.8 | 0 | 13.14
48 | 55 | 55 | 10.7 | 2.2 | 7.9 | 0 | 13.14
48 | 56 | 55 | 10.766 | 2.2 | 8 | 0 | 13.14
48 | 57 | 55 | 10.832 | 2.2 | 8.1 | 0 | 13.14
48 | 58 | 55 | 10.898 | 2.2 | 8.2 | 0 | 13.14
48 | 59 | 55 | 10.964 | 2.2 | 8.3 | 0 | 13.14
48 | 60 | 55 | 11.03 | 2.2 | 8.4 | 0 | 13.14
48 | 61 | 55 | 11.096 | 2.2 | 8.5 | 0 | 13.14
48 | 62 | 55 | 11.162 | 2.2 | 8.6 | 0 | 13.14
48 | 63 | 55 | 11.228 | 2.2 | 8.7 | 0 | 13.14
48 | 64 | 55 | 11.294 | 2.2 | 8.8 | 0 | 13.14
48 | 65 | 55 | 11.36 | 2.2 | 8.9 | 0 | 13.14
48 | 66 | 55 | 11.426 | 2.2 | 9 | 0 | 13.14
48 | 67 | 55 | 11.492 | 2.2 | 9.1 | 0 | 13.14
48 | 68 | 55 | 11.558 | 2.2 | 9.2 | 0 | 13.14
48 | 69 | 55 | 11.624 | 2.2 | 9.3 | 0 | 13.14
48 | 70 | 55 | 11.69 | 2.2 | 9.4 | 0 | 13.14
48 | 71 | 55 | 11.756 | 2.2 | 9.5 | 0 | 13.14
48 | 72 | 55 | 11.822 | 2.2 | 9.6 | 0 | 13.14
48 | 73 | 55 | 11.888 | 2.2 | 9.7 | 0 | 13.14
48 | 74 | 55 | 11.954 | 2.2 | 9.8 | 0 | 13.14
48 | 75 | 55 | 12.02 | 2.2 | 9.9 | 0 | 13.14
48 | 76 | 55 | 12.0736 | 2.2 | 10 | 0 | 13.14
48 | 77 | 55 | 12.1272 | 2.3 | 3 | 0 | 13.16
48 | 78 | 55 | 12.1808 | 2.3 | 3.1 | 0 | 13.16
48 | 79 | 55 | 12.2344 | 2.3 | 3.2 | 0 | 13.16
48 | 80 | 55 | 12.288 | 2.3 | 3.3 | 0 | 13.16
48 | 81 | 55 | 12.3416 | 2.3 | 3.4 | 0 | 13.16
48 | 82 | 55 | 12.3952 | 2.3 | 3.5 | 0 | 13.16
48 | 83 | 55 | 12.4488 | 2.3 | 3.6 | 0 | 13.16
48 | 84 | 55 | 12.5024 | 2.3 | 3.7 | 0 | 13.16
48 | 85 | 55 | 12.556 | 2.3 | 3.8 | 0 | 13.16
48 | 86 | 55 | 12.6096 | 2.3 | 3.9 | 0 | 13.16
48 | 87 | 55 | 12.6632 | 2.3 | 4 | 0 | 13.16
48 | 88 | 55 | 12.7168 | 2.3 | 4.1 | 0 | 13.16
48 | 89 | 55 | 12.7704 | 2.3 | 4.2 | 0 | 13.16
48 | 90 | 55 | 12.824 | 2.3 | 4.3 | 0 | 13.16
48 | 91 | 55 | 12.8776 | 2.3 | 4.4 | 0 | 13.16
48 | 92 | 55 | 12.9312 | 2.3 | 4.5 | 0 | 13.16
48 | 93 | 55 | 12.9848 | 2.3 | 4.6 | 0 | 13.16
48 | 94 | 55 | 13.0384 | 2.3 | 4.7 | 0 | 13.16
48 | 95 | 55 | 13.092 | 2.3 | 4.8 | 0 | 13.16
48 | 96 | 55 | 13.1456 | 2.3 | 4.9 | 0 | 13.16
48 | 97 | 55 | 13.1992 | 2.3 | 5 | 0 | 13.16
48 | 98 | 55 | 13.2528 | 2.3 | 5.1 | 0 | 13.16
48 | 99 | 55 | 13.3064 | 2.3 | 5.2 | 0 | 13.16
48 | 100 | 55 | 13.36 | 2.3 | 5.3 | 0 | 13.16
48 | 101 | 55 | 13.3944 | 2.3 | 5.4 | 0 | 13.16
48 | 102 | 55 | 13.4288 | 2.3 | 5.5 | 0 | 13.16
48 | 103 | 55 | 13.4632 | 2.3 | 5.6 | 0 | 13.16
48 | 104 | 55 | 13.4976 | 2.3 | 5.7 | 0 | 13.16
48 | 105 | 55 | 13.532 | 2.3 | 5.8 | 0 | 13.16
48 | 106 | 55 | 13.5664 | 2.3 | 5.9 | 0 | 13.16
48 | 107 | 55 | 13.6008 | 2.3 | 6 | 0 | 13.16
48 | 108 | 55 | 13.6352 | 2.3 | 6.1 | 0 | 13.16
48 | 109 | 55 | 13.6696 | 2.3 | 6.2 | 0 | 13.16
48 | 110 | 55 | 13.704 | 2.3 | 6.3 | 0 | 13.16
48 | 111 | 55 | 13.7384 | 2.3 | 6.4 | 0 | 13.16
48 | 112 | 55 | 13.7728 | 2.3 | 6.5 | 0 | 13.16
48 | 113 | 55 | 13.8072 | 2.3 | 6.6 | 0 | 13.16
48 | 114 | 55 | 13.8416 | 2.3 | 6.7 | 0 | 13.16
48 | 115 | 55 | 13.876 | 2.3 | 6.8 | 0 | 13.16
48 | 116 | 55 | 13.9104 | 2.3 | 6.9 | 0 | 13.16
48 | 117 | 55 | 13.9448 | 2.3 | 7 | 0 | 13.16
48 | 118 | 55 | 13.9792 | 2.3 | 7.1 | 0 | 13.16
48 | 119 | 55 | 14.0136 | 2.3 | 7.2 | 0 | 13.16
48 | 120 | 55 | 14.048 | 2.3 | 7.3 | 0 | 13.16
48 | 121 | 55 | 14.0824 | 2.3 | 7.4 | 0 | 13.16
48 | 122 | 55 | 14.1168 | 2.3 | 7.5 | 0 | 13.16
48 | 123 | 55 | 14.1512 | 2.3 | 7.6 | 0 | 13.16
48 | 124 | 55 | 14.1856 | 2.3 | 7.7 | 0 | 13.16
48 | 125 | 55 | 14.22 | 2.3 | 7.8 | 0 | 13.16
48 | 126 | 55 | 14.2656 | 2.3 | 7.9 | 0 | 13.16
48 | 127 | 55 | 14.3112 | 2.3 | 8 | 0 | 13.16
48 | 128 | 55 | 14.3568 | 2.3 | 8.1 | 0 | 13.16
48 | 129 | 55 | 14.4024 | 2.3 | 8.2 | 0 | 13.16
48 | 130 | 55 | 14.448 | 2.3 | 8.3 | 0 | 13.16
48 | 131 | 55 | 14.4936 | 2.3 | 8.4 | 0 | 13.16
48 | 132 | 55 | 14.5392 | 2.3 | 8.5 | 0 | 13.16
48 | 133 | 55 | 14.5848 | 2.3 | 8.6 | 0 | 13.16
48 | 134 | 55 | 14.6304 | 2.3 | 8.7 | 0 | 13.16
48 | 135 | 55 | 14.676 | 2.3 | 8.8 | 0 | 13.16
48 | 136 | 55 | 14.7216 | 2.3 | 8.9 | 0 | 13.16
48 | 137 | 55 | 14.7672 | 2.3 | 9 | 0 | 13.16
48 | 138 | 55 | 14.8128 | 2.3 | 9.1 | 0 | 13.16
48 | 139 | 55 | 14.8584 | 2.3 | 9.2 | 0 | 13.16
48 | 140 | 55 | 14.904 | 2.3 | 9.3 | 0 | 13.16
48 | 141 | 55 | 14.9496 | 2.3 | 9.4 | 0 | 13.16
48 | 142 | 55 | 14.9952 | 2.3 | 9.5 | 0 | 13.16
48 | 143 | 55 | 15.0408 | 2.3 | 9.6 | 0 | 13.16
48 | 144 | 55 | 15.0864 | 2.3 | 9.7 | 0 | 13.16
48 | 145 | 55 | 15.132 | 2.3 | 9.8 | 0 | 13.16
48 | 146 | 55 | 15.1776 | 2.3 | 9.9 | 0 | 13.16
48 | 147 | 55 | 15.2232 | 2.3 | 10 | 0 | 13.16
48 | 148 | 55 | 15.2688 | 2.4 | 3 | 0 | 13.18
48 | 149 | 55 | 15.3144 | 2.4 | 3.1 | 0 | 13.18
48 | 150 | 55 | 15.36 | 2.4 | 3.2 | 0 | 13.18
49 | 45 | 55 | 10.0533 | 2.4 | 3.3 | 0 | 13.18
49 | 46 | 55 | 10.1191 | 2.4 | 3.4 | 0 | 13.18
49 | 47 | 55 | 10.1849 | 2.4 | 3.5 | 0 | 13.18
49 | 48 | 55 | 10.2507 | 2.4 | 3.6 | 0 | 13.18
49 | 49 | 55 | 10.3164 | 2.4 | 3.7 | 0 | 13.18
49 | 50 | 55 | 10.3822 | 2.4 | 3.8 | 0 | 13.18
49 | 51 | 55 | 10.448 | 2.4 | 3.9 | 0 | 13.18
49 | 52 | 55 | 10.5138 | 2.4 | 4 | 0 | 13.18
49 | 53 | 55 | 10.5796 | 2.4 | 4.1 | 0 | 13.18
49 | 54 | 55 | 10.6453 | 2.4 | 4.2 | 0 | 13.18
49 | 55 | 55 | 10.7111 | 2.4 | 4.3 | 0 | 13.18
49 | 56 | 55 | 10.7769 | 2.4 | 4.4 | 0 | 13.18
49 | 57 | 55 | 10.8427 | 2.4 | 4.5 | 0 | 13.18
49 | 58 | 55 | 10.9084 | 2.4 | 4.6 | 0 | 13.18
49 | 59 | 55 | 10.9742 | 2.4 | 4.7 | 0 | 13.18
49 | 60 | 55 | 11.04 | 2.4 | 4.8 | 0 | 13.18
49 | 61 | 55 | 11.1058 | 2.4 | 4.9 | 0 | 13.18
49 | 62 | 55 | 11.1716 | 2.4 | 5 | 0 | 13.18
49 | 63 | 55 | 11.2373 | 2.4 | 5.1 | 0 | 13.18
49 | 64 | 55 | 11.3031 | 2.4 | 5.2 | 0 | 13.18
49 | 65 | 55 | 11.3689 | 2.4 | 5.3 | 0 | 13.18
49 | 66 | 55 | 11.4347 | 2.4 | 5.4 | 0 | 13.18
49 | 67 | 55 | 11.5004 | 2.4 | 5.5 | 0 | 13.18
49 | 68 | 55 | 11.5662 | 2.4 | 5.6 | 0 | 13.18
49 | 69 | 55 | 11.632 | 2.4 | 5.7 | 0 | 13.18
49 | 70 | 55 | 11.6978 | 2.4 | 5.8 | 0 | 13.18
49 | 71 | 55 | 11.7636 | 2.4 | 5.9 | 0 | 13.18
49 | 72 | 55 | 11.8293 | 2.4 | 6 | 0 | 13.18
49 | 73 | 55 | 11.8951 | 2.4 | 6.1 | 0 | 13.18
49 | 74 | 55 | 11.9609 | 2.4 | 6.2 | 0 | 13.18
49 | 75 | 55 | 12.0267 | 2.4 | 6.3 | 0 | 13.18
49 | 76 | 55 | 12.0821 | 2.4 | 6.4 | 0 | 13.18
49 | 77 | 55 | 12.1376 | 2.4 | 6.5 | 0 | 13.18
49 | 78 | 55 | 12.1931 | 2.4 | 6.6 | 0 | 13.18
49 | 79 | 55 | 12.2485 | 2.4 | 6.7 | 0 | 13.18
49 | 80 | 55 | 12.304 | 2.4 | 6.8 | 0 | 13.18
49 | 81 | 55 | 12.3595 | 2.4 | 6.9 | 0 | 13.18
49 | 82 | 55 | 12.4149 | 2.4 | 7 | 0 | 13.18
49 | 83 | 55 | 12.4704 | 2.4 | 7.1 | 0 | 13.18
49 | 84 | 55 | 12.5259 | 2.4 | 7.2 | 0 | 13.18
49 | 85 | 55 | 12.5813 | 2.4 | 7.3 | 0 | 13.18
49 | 86 | 55 | 12.6368 | 2.4 | 7.4 | 0 | 13.18
49 | 87 | 55 | 12.6923 | 2.4 | 7.5 | 0 | 13.18
49 | 88 | 55 | 12.7477 | 2.4 | 7.6 | 0 | 13.18
49 | 89 | 55 | 12.8032 | 2.4 | 7.7 | 0 | 13.18
49 | 90 | 55 | 12.8587 | 2.4 | 7.8 | 0 | 13.18
49 | 91 | 55 | 12.9141 | 2.4 | 7.9 | 0 | 13.18
49 | 92 | 55 | 12.9696 | 2.4 | 8 | 0 | 13.18
49 | 93 | 55 | 13.0251 | 2.4 | 8.1 | 0 | 13.18
49 | 94 | 55 | 13.0805 | 2.4 | 8.2 | 0 | 13.18
49 | 95 | 55 | 13.136 | 2.4 | 8.3 | 0 | 13.18
49 | 96 | 55 | 13.1915 | 2.4 | 8.4 | 0 | 13.18
49 | 97 | 55 | 13.2469 | 2.4 | 8.5 | 0 | 13.18
49 | 98 | 55 | 13.3024 | 2.4 | 8.6 | 0 | 13.18
49 | 99 | 55 | 13.3579 | 2.4 | 8.7 | 0 | 13.18
49 | 100 | 55 | 13.4133 | 2.4 | 8.8 | 0 | 13.18
49 | 101 | 55 | 13.4459 | 2.4 | 8.9 | 0 | 13.18
49 | 102 | 55 | 13.4784 | 2.4 | 9 | 0 | 13.18
49 | 103 | 55 | 13.5109 | 2.4 | 9.1 | 0 | 13.18
49 | 104 | 55 | 13.5435 | 2.4 | 9.2 | 0 | 13.18
49 | 105 | 55 | 13.576 | 2.4 | 9.3 | 0 | 13.18
49 | 106 | 55 | 13.6085 | 2.4 | 9.4 | 0 | 13.18
49 | 107 | 55 | 13.6411 | 2.4 | 9.5 | 0 | 13.18
49 | 108 | 55 | 13.6736 | 2.4 | 9.6 | 0 | 13.18
49 | 109 | 55 | 13.7061 | 2.4 | 9.7 | 0 | 13.18
49 | 110 | 55 | 13.7387 | 2.4 | 9.8 | 0 | 13.18
49 | 111 | 55 | 13.7712 | 2.4 | 9.9 | 0 | 13.18
49 | 112 | 55 | 13.8037 | 2.4 | 10 | 0 | 13.18
49 | 113 | 55 | 13.8363 | 2.5 | 3 | 0 | 13.2
49 | 114 | 55 | 13.8688 | 2.5 | 3.1 | 0 | 13.2
49 | 115 | 55 | 13.9013 | 2.5 | 3.2 | 0 | 13.2
49 | 116 | 55 | 13.9339 | 2.5 | 3.3 | 0 | 13.2
49 | 117 | 55 | 13.9664 | 2.5 | 3.4 | 0 | 13.2
49 | 118 | 55 | 13.9989 | 2.5 | 3.5 | 0 | 13.2
49 | 119 | 55 | 14.0315 | 2.5 | 3.6 | 0 | 13.2
49 | 120 | 55 | 14.064 | 2.5 | 3.7 | 0 | 13.2
49 | 121 | 55 | 14.0965 | 2.5 | 3.8 | 0 | 13.2
49 | 122 | 55 | 14.1291 | 2.5 | 3.9 | 0 | 13.2
49 | 123 | 55 | 14.1616 | 2.5 | 4 | 0 | 13.2
49 | 124 | 55 | 14.1941 | 2.5 | 4.1 | 0 | 13.2
49 | 125 | 55 | 14.2267 | 2.5 | 4.2 | 0 | 13.2
49 | 126 | 55 | 14.2728 | 2.5 | 4.3 | 0 | 13.2
49 | 127 | 55 | 14.3189 | 2.5 | 4.4 | 0 | 13.2
49 | 128 | 55 | 14.3651 | 2.5 | 4.5 | 0 | 13.2
49 | 129 | 55 | 14.4112 | 2.5 | 4.6 | 0 | 13.2
49 | 130 | 55 | 14.4573 | 2.5 | 4.7 | 0 | 13.2
49 | 131 | 55 | 14.5035 | 2.5 | 4.8 | 0 | 13.2
49 | 132 | 55 | 14.5496 | 2.5 | 4.9 | 0 | 13.2
49 | 133 | 55 | 14.5957 | 2.5 | 5 | 0 | 13.2
49 | 134 | 55 | 14.6419 | 2.5 | 5.1 | 0 | 13.2
49 | 135 | 55 | 14.688 | 2.5 | 5.2 | 0 | 13.2
49 | 136 | 55 | 14.7341 | 2.5 | 5.3 | 0 | 13.2
49 | 137 | 55 | 14.7803 | 2.5 | 5.4 | 0 | 13.2
49 | 138 | 55 | 14.8264 | 2.5 | 5.5 | 0 | 13.2
49 | 139 | 55 | 14.8725 | 2.5 | 5.6 | 0 | 13.2
49 | 140 | 55 | 14.9187 | 2.5 | 5.7 | 0 | 13.2
49 | 141 | 55 | 14.9648 | 2.5 | 5.8 | 0 | 13.2
49 | 142 | 55 | 15.0109 | 2.5 | 5.9 | 0 | 13.2
49 | 143 | 55 | 15.0571 | 2.5 | 6 | 0 | 13.2
49 | 144 | 55 | 15.1032 | 2.5 | 6.1 | 0 | 13.2
49 | 145 | 55 | 15.1493 | 2.5 | 6.2 | 0 | 13.2
49 | 146 | 55 | 15.1955 | 2.5 | 6.3 | 0 | 13.2
49 | 147 | 55 | 15.2416 | 2.5 | 6.4 | 0 | 13.2
49 | 148 | 55 | 15.2877 | 2.5 | 6.5 | 0 | 13.2
49 | 149 | 55 | 15.3339 | 2.5 | 6.6 | 0 | 13.2
49 | 150 | 55 | 15.38 | 2.5 | 6.7 | 0 | 13.2
50 | 45 | 55 | 10.0667 | 2.5 | 6.8 | 0 | 13.2
50 | 46 | 55 | 10.1322 | 2.5 | 6.9 | 0 | 13.2
50 | 47 | 55 | 10.1978 | 2.5 | 7 | 0 | 13.2
50 | 48 | 55 | 10.2633 | 2.5 | 7.1 | 0 | 13.2
50 | 49 | 55 | 10.3289 | 2.5 | 7.2 | 0 | 13.2
50 | 50 | 55 | 10.3944 | 2.5 | 7.3 | 0 | 13.2
50 | 51 | 55 | 10.46 | 2.5 | 7.4 | 0 | 13.2
50 | 52 | 55 | 10.5256 | 2.5 | 7.5 | 0 | 13.2
50 | 53 | 55 | 10.5911 | 2.5 | 7.6 | 0 | 13.2
50 | 54 | 55 | 10.6567 | 2.5 | 7.7 | 0 | 13.2
50 | 55 | 55 | 10.7222 | 2.5 | 7.8 | 0 | 13.2
50 | 56 | 55 | 10.7878 | 2.5 | 7.9 | 0 | 13.2
50 | 57 | 55 | 10.8533 | 2.5 | 8 | 0 | 13.2
50 | 58 | 55 | 10.9189 | 2.5 | 8.1 | 0 | 13.2
50 | 59 | 55 | 10.9844 | 2.5 | 8.2 | 0 | 13.2
50 | 60 | 55 | 11.05 | 2.5 | 8.3 | 0 | 13.2
50 | 61 | 55 | 11.1156 | 2.5 | 8.4 | 0 | 13.2
50 | 62 | 55 | 11.1811 | 2.5 | 8.5 | 0 | 13.2
50 | 63 | 55 | 11.2467 | 2.5 | 8.6 | 0 | 13.2
50 | 64 | 55 | 11.3122 | 2.5 | 8.7 | 0 | 13.2
50 | 65 | 55 | 11.3778 | 2.5 | 8.8 | 0 | 13.2
50 | 66 | 55 | 11.4433 | 2.5 | 8.9 | 0 | 13.2
50 | 67 | 55 | 11.5089 | 2.5 | 9 | 0 | 13.2
50 | 68 | 55 | 11.5744 | 2.5 | 9.1 | 0 | 13.2
50 | 69 | 55 | 11.64 | 2.5 | 9.2 | 0 | 13.2
50 | 70 | 55 | 11.7056 | 2.5 | 9.3 | 0 | 13.2
50 | 71 | 55 | 11.7711 | 2.5 | 9.4 | 0 | 13.2
50 | 72 | 55 | 11.8367 | 2.5 | 9.5 | 0 | 13.2
50 | 73 | 55 | 11.9022 | 2.5 | 9.6 | 0 | 13.2
50 | 74 | 55 | 11.9678 | 2.5 | 9.7 | 0 | 13.2
50 | 75 | 55 | 12.0333 | 2.5 | 9.8 | 0 | 13.2
50 | 76 | 55 | 12.0907 | 2.5 | 9.9 | 0 | 13.2
50 | 77 | 55 | 12.148 | 2.5 | 10 | 0 | 13.2
50 | 78 | 55 | 12.2053 | 2.6 | 3 | 0 | 13.22
50 | 79 | 55 | 12.2627 | 2.6 | 3.1 | 0 | 13.22
50 | 80 | 55 | 12.32 | 2.6 | 3.2 | 0 | 13.22
50 | 81 | 55 | 12.3773 | 2.6 | 3.3 | 0 | 13.22
50 | 82 | 55 | 12.4347 | 2.6 | 3.4 | 0 | 13.22
50 | 83 | 55 | 12.492 | 2.6 | 3.5 | 0 | 13.22
50 | 84 | 55 | 12.5493 | 2.6 | 3.6 | 0 | 13.22
50 | 85 | 55 | 12.6067 | 2.6 | 3.7 | 0 | 13.22
50 | 86 | 55 | 12.664 | 2.6 | 3.8 | 0 | 13.22
50 | 87 | 55 | 12.7213 | 2.6 | 3.9 | 0 | 13.22
50 | 88 | 55 | 12.7787 | 2.6 | 4 | 0 | 13.22
50 | 89 | 55 | 12.836 | 2.6 | 4.1 | 0 | 13.22
50 | 90 | 55 | 12.8933 | 2.6 | 4.2 | 0 | 13.22
50 | 91 | 55 | 12.9507 | 2.6 | 4.3 | 0 | 13.22
50 | 92 | 55 | 13.008 | 2.6 | 4.4 | 0 | 13.22
50 | 93 | 55 | 13.0653 | 2.6 | 4.5 | 0 | 13.22
50 | 94 | 55 | 13.1227 | 2.6 | 4.6 | 0 | 13.22
50 | 95 | 55 | 13.18 | 2.6 | 4.7 | 0 | 13.22
50 | 96 | 55 | 13.2373 | 2.6 | 4.8 | 0 | 13.22
50 | 97 | 55 | 13.2947 | 2.6 | 4.9 | 0 | 13.22
50 | 98 | 55 | 13.352 | 2.6 | 5 | 0 | 13.22
50 | 99 | 55 | 13.4093 | 2.6 | 5.1 | 0 | 13.22
50 | 100 | 55 | 13.4667 | 2.6 | 5.2 | 0 | 13.22
50 | 101 | 55 | 13.4973 | 2.6 | 5.3 | 0 | 13.22
50 | 102 | 55 | 13.528 | 2.6 | 5.4 | 0 | 13.22
50 | 103 | 55 | 13.5587 | 2.6 | 5.5 | 0 | 13.22
50 | 104 | 55 | 13.5893 | 2.6 | 5.6 | 0 | 13.22
50 | 105 | 55 | 13.62 | 2.6 | 5.7 | 0 | 13.22
50 | 106 | 55 | 13.6507 | 2.6 | 5.8 | 0 | 13.22
50 | 107 | 55 | 13.6813 | 2.6 | 5.9 | 0 | 13.22
50 | 108 | 55 | 13.712 | 2.6 | 6 | 0 | 13.22
50 | 109 | 55 | 13.7427 | 2.6 | 6.1 | 0 | 13.22
50 | 110 | 55 | 13.7733 | 2.6 | 6.2 | 0 | 13.22
50 | 111 | 55 | 13.804 | 2.6 | 6.3 | 0 | 13.22
50 | 112 | 55 | 13.8347 | 2.6 | 6.4 | 0 | 13.22
50 | 113 | 55 | 13.8653 | 2.6 | 6.5 | 0 | 13.22
50 | 114 | 55 | 13.896 | 2.6 | 6.6 | 0 | 13.22
50 | 115 | 55 | 13.9267 | 2.6 | 6.7 | 0 | 13.22
50 | 116 | 55 | 13.9573 | 2.6 | 6.8 | 0 | 13.22
50 | 117 | 55 | 13.988 | 2.6 | 6.9 | 0 | 13.22
50 | 118 | 55 | 14.0187 | 2.6 | 7 | 0 | 13.22
50 | 119 | 55 | 14.0493 | 2.6 | 7.1 | 0 | 13.22
50 | 120 | 55 | 14.08 | 2.6 | 7.2 | 0 | 13.22
50 | 121 | 55 | 14.1107 | 2.6 | 7.3 | 0 | 13.22
50 | 122 | 55 | 14.1413 | 2.6 | 7.4 | 0 | 13.22
50 | 123 | 55 | 14.172 | 2.6 | 7.5 | 0 | 13.22
50 | 124 | 55 | 14.2027 | 2.6 | 7.6 | 0 | 13.22
50 | 125 | 55 | 14.2333 | 2.6 | 7.7 | 0 | 13.22
50 | 126 | 55 | 14.28 | 2.6 | 7.8 | 0 | 13.22
50 | 127 | 55 | 14.3267 | 2.6 | 7.9 | 0 | 13.22
50 | 128 | 55 | 14.3733 | 2.6 | 8 | 0 | 13.22
50 | 129 | 55 | 14.42 | 2.6 | 8.1 | 0 | 13.22
50 | 130 | 55 | 14.4667 | 2.6 | 8.2 | 0 | 13.22
50 | 131 | 55 | 14.5133 | 2.6 | 8.3 | 0 | 13.22
50 | 132 | 55 | 14.56 | 2.6 | 8.4 | 0 | 13.22
50 | 133 | 55 | 14.6067 | 2.6 | 8.5 | 0 | 13.22
50 | 134 | 55 | 14.6533 | 2.6 | 8.6 | 0 | 13.22
50 | 135 | 55 | 14.7 | 2.6 | 8.7 | 0 | 13.22
50 | 136 | 55 | 14.7467 | 2.6 | 8.8 | 0 | 13.22
50 | 137 | 55 | 14.7933 | 2.6 | 8.9 | 0 | 13.22
50 | 138 | 55 | 14.84 | 2.6 | 9 | 0 | 13.22
50 | 139 | 55 | 14.8867 | 2.6 | 9.1 | 0 | 13.22
50 | 140 | 55 | 14.9333 | 2.6 | 9.2 | 0 | 13.22
50 | 141 | 55 | 14.98 | 2.6 | 9.3 | 0 | 13.22
50 | 142 | 55 | 15.0267 | 2.6 | 9.4 | 0 | 13.22
50 | 143 | 55 | 15.0733 | 2.6 | 9.5 | 0 | 13.22
50 | 144 | 55 | 15.12 | 2.6 | 9.6 | 0 | 13.22
50 | 145 | 55 | 15.1667 | 2.6 | 9.7 | 0 | 13.22
50 | 146 | 55 | 15.2133 | 2.6 | 9.8 | 0 | 13.22
50 | 147 | 55 | 15.26 | 2.6 | 9.9 | 0 | 13.22
50 | 148 | 55 | 15.3067 | 2.6 | 10 | 0 | 13.22
50 | 149 | 55 | 15.3533 | 2.7 | 3 | 0 | 13.24
50 | 150 | 55 | 15.4 | 2.7 | 3.1 | 0 | 13.24
51 | 45 | 55 | 10.08 | 2.7 | 3.2 | 0 | 13.24
51 | 46 | 55 | 10.1453 | 2.7 | 3.3 | 0 | 13.24
51 | 47 | 55 | 10.2107 | 2.7 | 3.4 | 0 | 13.24
51 | 48 | 55 | 10.276 | 2.7 | 3.5 | 0 | 13.24
51 | 49 | 55 | 10.3413 | 2.7 | 3.6 | 0 | 13.24
51 | 50 | 55 | 10.4067 | 2.7 | 3.7 | 0 | 13.24
51 | 51 | 55 | 10.472 | 2.7 | 3.8 | 0 | 13.24
51 | 52 | 55 | 10.5373 | 2.7 | 3.9 | 0 | 13.24
51 | 53 | 55 | 10.6027 | 2.7 | 4 | 0 | 13.24
51 | 54 | 55 | 10.668 | 2.7 | 4.1 | 0 | 13.24
51 | 55 | 55 | 10.7333 | 2.7 | 4.2 | 0 | 13.24
51 | 56 | 55 | 10.7987 | 2.7 | 4.3 | 0 | 13.24
51 | 57 | 55 | 10.864 | 2.7 | 4.4 | 0 | 13.24
51 | 58 | 55 | 10.9293 | 2.7 | 4.5 | 0 | 13.24
51 | 59 | 55 | 10.9947 | 2.7 | 4.6 | 0 | 13.24
51 | 60 | 55 | 11.06 | 2.7 | 4.7 | 0 | 13.24
51 | 61 | 55 | 11.1253 | 2.7 | 4.8 | 0 | 13.24
51 | 62 | 55 | 11.1907 | 2.7 | 4.9 | 0 | 13.24
51 | 63 | 55 | 11.256 | 2.7 | 5 | 0 | 13.24
51 | 64 | 55 | 11.3213 | 2.7 | 5.1 | 0 | 13.24
51 | 65 | 55 | 11.3867 | 2.7 | 5.2 | 0 | 13.24
51 | 66 | 55 | 11.452 | 2.7 | 5.3 | 0 | 13.24
51 | 67 | 55 | 11.5173 | 2.7 | 5.4 | 0 | 13.24
51 | 68 | 55 | 11.5827 | 2.7 | 5.5 | 0 | 13.24
51 | 69 | 55 | 11.648 | 2.7 | 5.6 | 0 | 13.24
51 | 70 | 55 | 11.7133 | 2.7 | 5.7 | 0 | 13.24
51 | 71 | 55 | 11.7787 | 2.7 | 5.8 | 0 | 13.24
51 | 72 | 55 | 11.844 | 2.7 | 5.9 | 0 | 13.24
51 | 73 | 55 | 11.9093 | 2.7 | 6 | 0 | 13.24
51 | 74 | 55 | 11.9747 | 2.7 | 6.1 | 0 | 13.24
51 | 75 | 55 | 12.04 | 2.7 | 6.2 | 0 | 13.24
51 | 76 | 55 | 12.0992 | 2.7 | 6.3 | 0 | 13.24
51 | 77 | 55 | 12.1584 | 2.7 | 6.4 | 0 | 13.24
51 | 78 | 55 | 12.2176 | 2.7 | 6.5 | 0 | 13.24
51 | 79 | 55 | 12.2768 | 2.7 | 6.6 | 0 | 13.24
51 | 80 | 55 | 12.336 | 2.7 | 6.7 | 0 | 13.24
51 | 81 | 55 | 12.3952 | 2.7 | 6.8 | 0 | 13.24
51 | 82 | 55 | 12.4544 | 2.7 | 6.9 | 0 | 13.24
51 | 83 | 55 | 12.5136 | 2.7 | 7 | 0 | 13.24
51 | 84 | 55 | 12.5728 | 2.7 | 7.1 | 0 | 13.24
51 | 85 | 55 | 12.632 | 2.7 | 7.2 | 0 | 13.24
51 | 86 | 55 | 12.6912 | 2.7 | 7.3 | 0 | 13.24
51 | 87 | 55 | 12.7504 | 2.7 | 7.4 | 0 | 13.24
51 | 88 | 55 | 12.8096 | 2.7 | 7.5 | 0 | 13.24
51 | 89 | 55 | 12.8688 | 2.7 | 7.6 | 0 | 13.24
51 | 90 | 55 | 12.928 | 2.7 | 7.7 | 0 | 13.24
51 | 91 | 55 | 12.9872 | 2.7 | 7.8 | 0 | 13.24
51 | 92 | 55 | 13.0464 | 2.7 | 7.9 | 0 | 13.24
51 | 93 | 55 | 13.1056 | 2.7 | 8 | 0 | 13.24
51 | 94 | 55 | 13.1648 | 2.7 | 8.1 | 0 | 13.24
51 | 95 | 55 | 13.224 | 2.7 | 8.2 | 0 | 13.24
51 | 96 | 55 | 13.2832 | 2.7 | 8.3 | 0 | 13.24
51 | 97 | 55 | 13.3424 | 2.7 | 8.4 | 0 | 13.24
51 | 98 | 55 | 13.4016 | 2.7 | 8.5 | 0 | 13.24
51 | 99 | 55 | 13.4608 | 2.7 | 8.6 | 0 | 13.24
51 | 100 | 55 | 13.52 | 2.7 | 8.7 | 0 | 13.24
51 | 101 | 55 | 13.5488 | 2.7 | 8.8 | 0 | 13.24
51 | 102 | 55 | 13.5776 | 2.7 | 8.9 | 0 | 13.24
51 | 103 | 55 | 13.6064 | 2.7 | 9 | 0 | 13.24
51 | 104 | 55 | 13.6352 | 2.7 | 9.1 | 0 | 13.24
51 | 105 | 55 | 13.664 | 2.7 | 9.2 | 0 | 13.24
51 | 106 | 55 | 13.6928 | 2.7 | 9.3 | 0 | 13.24
51 | 107 | 55 | 13.7216 | 2.7 | 9.4 | 0 | 13.24
51 | 108 | 55 | 13.7504 | 2.7 | 9.5 | 0 | 13.24
51 | 109 | 55 | 13.7792 | 2.7 | 9.6 | 0 | 13.24
51 | 110 | 55 | 13.808 | 2.7 | 9.7 | 0 | 13.24
51 | 111 | 55 | 13.8368 | 2.7 | 9.8 | 0 | 13.24
51 | 112 | 55 | 13.8656 | 2.7 | 9.9 | 0 | 13.24
51 | 113 | 55 | 13.8944 | 2.7 | 10 | 0 | 13.24
51 | 114 | 55 | 13.9232 | 2.8 | 3 | 0 | 13.26
51 | 115 | 55 | 13.952 | 2.8 | 3.1 | 0 | 13.26
51 | 116 | 55 | 13.9808 | 2.8 | 3.2 | 0 | 13.26
51 | 117 | 55 | 14.0096 | 2.8 | 3.3 | 0 | 13.26
51 | 118 | 55 | 14.0384 | 2.8 | 3.4 | 0 | 13.26
51 | 119 | 55 | 14.0672 | 2.8 | 3.5 | 0 | 13.26
51 | 120 | 55 | 14.096 | 2.8 | 3.6 | 0 | 13.26
51 | 121 | 55 | 14.1248 | 2.8 | 3.7 | 0 | 13.26
51 | 122 | 55 | 14.1536 | 2.8 | 3.8 | 0 | 13.26
51 | 123 | 55 | 14.1824 | 2.8 | 3.9 | 0 | 13.26
51 | 124 | 55 | 14.2112 | 2.8 | 4 | 0 | 13.26
51 | 125 | 55 | 14.24 | 2.8 | 4.1 | 0 | 13.26
51 | 126 | 55 | 14.2872 | 2.8 | 4.2 | 0 | 13.26
51 | 127 | 55 | 14.3344 | 2.8 | 4.3 | 0 | 13.26
51 | 128 | 55 | 14.3816 | 2.8 | 4.4 | 0 | 13.26
51 | 129 | 55 | 14.4288 | 2.8 | 4.5 | 0 | 13.26
51 | 130 | 55 | 14.476 | 2.8 | 4.6 | 0 | 13.26
51 | 131 | 55 | 14.5232 | 2.8 | 4.7 | 0 | 13.26
51 | 132 | 55 | 14.5704 | 2.8 | 4.8 | 0 | 13.26
51 | 133 | 55 | 14.6176 | 2.8 | 4.9 | 0 | 13.26
51 | 134 | 55 | 14.6648 | 2.8 | 5 | 0 | 13.26
51 | 135 | 55 | 14.712 | 2.8 | 5.1 | 0 | 13.26
51 | 136 | 55 | 14.7592 | 2.8 | 5.2 | 0 | 13.26
51 | 137 | 55 | 14.8064 | 2.8 | 5.3 | 0 | 13.26
51 | 138 | 55 | 14.8536 | 2.8 | 5.4 | 0 | 13.26
51 | 139 | 55 | 14.9008 | 2.8 | 5.5 | 0 | 13.26
51 | 140 | 55 | 14.948 | 2.8 | 5.6 | 0 | 13.26
51 | 141 | 55 | 14.9952 | 2.8 | 5.7 | 0 | 13.26
51 | 142 | 55 | 15.0424 | 2.8 | 5.8 | 0 | 13.26
51 | 143 | 55 | 15.0896 | 2.8 | 5.9 | 0 | 13.26
51 | 144 | 55 | 15.1368 | 2.8 | 6 | 0 | 13.26
51 | 145 | 55 | 15.184 | 2.8 | 6.1 | 0 | 13.26
51 | 146 | 55 | 15.2312 | 2.8 | 6.2 | 0 | 13.26
51 | 147 | 55 | 15.2784 | 2.8 | 6.3 | 0 | 13.26
51 | 148 | 55 | 15.3256 | 2.8 | 6.4 | 0 | 13.26
51 | 149 | 55 | 15.3728 | 2.8 | 6.5 | 0 | 13.26
51 | 150 | 55 | 15.42 | 2.8 | 6.6 | 0 | 13.26
52 | 45 | 55 | 10.0933 | 2.8 | 6.7 | 0 | 13.26
52 | 46 | 55 | 10.1584 | 2.8 | 6.8 | 0 | 13.26
52 | 47 | 55 | 10.2236 | 2.8 | 6.9 | 0 | 13.26
52 | 48 | 55 | 10.2887 | 2.8 | 7 | 0 | 13.26
52 | 49 | 55 | 10.3538 | 2.8 | 7.1 | 0 | 13.26
52 | 50 | 55 | 10.4189 | 2.8 | 7.2 | 0 | 13.26
52 | 51 | 55 | 10.484 | 2.8 | 7.3 | 0 | 13.26
52 | 52 | 55 | 10.5491 | 2.8 | 7.4 | 0 | 13.26
52 | 53 | 55 | 10.6142 | 2.8 | 7.5 | 0 | 13.26
52 | 54 | 55 | 10.6793 | 2.8 | 7.6 | 0 | 13.26
52 | 55 | 55 | 10.7444 | 2.8 | 7.7 | 0 | 13.26
52 | 56 | 55 | 10.8096 | 2.8 | 7.8 | 0 | 13.26
52 | 57 | 55 | 10.8747 | 2.8 | 7.9 | 0 | 13.26
52 | 58 | 55 | 10.9398 | 2.8 | 8 | 0 | 13.26
52 | 59 | 55 | 11.0049 | 2.8 | 8.1 | 0 | 13.26
52 | 60 | 55 | 11.07 | 2.8 | 8.2 | 0 | 13.26
52 | 61 | 55 | 11.1351 | 2.8 | 8.3 | 0 | 13.26
52 | 62 | 55 | 11.2002 | 2.8 | 8.4 | 0 | 13.26
52 | 63 | 55 | 11.2653 | 2.8 | 8.5 | 0 | 13.26
52 | 64 | 55 | 11.3304 | 2.8 | 8.6 | 0 | 13.26
52 | 65 | 55 | 11.3956 | 2.8 | 8.7 | 0 | 13.26
52 | 66 | 55 | 11.4607 | 2.8 | 8.8 | 0 | 13.26
52 | 67 | 55 | 11.5258 | 2.8 | 8.9 | 0 | 13.26
52 | 68 | 55 | 11.5909 | 2.8 | 9 | 0 | 13.26
52 | 69 | 55 | 11.656 | 2.8 | 9.1 | 0 | 13.26
52 | 70 | 55 | 11.7211 | 2.8 | 9.2 | 0 | 13.26
52 | 71 | 55 | 11.7862 | 2.8 | 9.3 | 0 | 13.26
52 | 72 | 55 | 11.8513 | 2.8 | 9.4 | 0 | 13.26
52 | 73 | 55 | 11.9164 | 2.8 | 9.5 | 0 | 13.26
52 | 74 | 55 | 11.9816 | 2.8 | 9.6 | 0 | 13.26
52 | 75 | 55 | 12.0467 | 2.8 | 9.7 | 0 | 13.26
52 | 76 | 55 | 12.1077 | 2.8 | 9.8 | 0 | 13.26
52 | 77 | 55 | 12.1688 | 2.8 | 9.9 | 0 | 13.26
52 | 78 | 55 | 12.2299 | 2.8 | 10 | 0 | 13.26
52 | 79 | 55 | 12.2909 | 2.9 | 3 | 0 | 13.28
52 | 80 | 55 | 12.352 | 2.9 | 3.1 | 0 | 13.28
52 | 81 | 55 | 12.4131 | 2.9 | 3.2 | 0 | 13.28
52 | 82 | 55 | 12.4741 | 2.9 | 3.3 | 0 | 13.28
52 | 83 | 55 | 12.5352 | 2.9 | 3.4 | 0 | 13.28
52 | 84 | 55 | 12.5963 | 2.9 | 3.5 | 0 | 13.28
52 | 85 | 55 | 12.6573 | 2.9 | 3.6 | 0 | 13.28
52 | 86 | 55 | 12.7184 | 2.9 | 3.7 | 0 | 13.28
52 | 87 | 55 | 12.7795 | 2.9 | 3.8 | 0 | 13.28
52 | 88 | 55 | 12.8405 | 2.9 | 3.9 | 0 | 13.28
52 | 89 | 55 | 12.9016 | 2.9 | 4 | 0 | 13.28
52 | 90 | 55 | 12.9627 | 2.9 | 4.1 | 0 | 13.28
52 | 91 | 55 | 13.0237 | 2.9 | 4.2 | 0 | 13.28
52 | 92 | 55 | 13.0848 | 2.9 | 4.3 | 0 | 13.28
52 | 93 | 55 | 13.1459 | 2.9 | 4.4 | 0 | 13.28
52 | 94 | 55 | 13.2069 | 2.9 | 4.5 | 0 | 13.28
52 | 95 | 55 | 13.268 | 2.9 | 4.6 | 0 | 13.28
52 | 96 | 55 | 13.3291 | 2.9 | 4.7 | 0 | 13.28
52 | 97 | 55 | 13.3901 | 2.9 | 4.8 | 0 | 13.28
52 | 98 | 55 | 13.4512 | 2.9 | 4.9 | 0 | 13.28
52 | 99 | 55 | 13.5123 | 2.9 | 5 | 0 | 13.28
52 | 100 | 55 | 13.5733 | 2.9 | 5.1 | 0 | 13.28
52 | 101 | 55 | 13.6003 | 2.9 | 5.2 | 0 | 13.28
52 | 102 | 55 | 13.6272 | 2.9 | 5.3 | 0 | 13.28
52 | 103 | 55 | 13.6541 | 2.9 | 5.4 | 0 | 13.28
52 | 104 | 55 | 13.6811 | 2.9 | 5.5 | 0 | 13.28
52 | 105 | 55 | 13.708 | 2.9 | 5.6 | 0 | 13.28
52 | 106 | 55 | 13.7349 | 2.9 | 5.7 | 0 | 13.28
52 | 107 | 55 | 13.7619 | 2.9 | 5.8 | 0 | 13.28
52 | 108 | 55 | 13.7888 | 2.9 | 5.9 | 0 | 13.28
52 | 109 | 55 | 13.8157 | 2.9 | 6 | 0 | 13.28
52 | 110 | 55 | 13.8427 | 2.9 | 6.1 | 0 | 13.28
52 | 111 | 55 | 13.8696 | 2.9 | 6.2 | 0 | 13.28
52 | 112 | 55 | 13.8965 | 2.9 | 6.3 | 0 | 13.28
52 | 113 | 55 | 13.9235 | 2.9 | 6.4 | 0 | 13.28
52 | 114 | 55 | 13.9504 | 2.9 | 6.5 | 0 | 13.28
52 | 115 | 55 | 13.9773 | 2.9 | 6.6 | 0 | 13.28
52 | 116 | 55 | 14.0043 | 2.9 | 6.7 | 0 | 13.28
52 | 117 | 55 | 14.0312 | 2.9 | 6.8 | 0 | 13.28
52 | 118 | 55 | 14.0581 | 2.9 | 6.9 | 0 | 13.28
52 | 119 | 55 | 14.0851 | 2.9 | 7 | 0 | 13.28
52 | 120 | 55 | 14.112 | 2.9 | 7.1 | 0 | 13.28
52 | 121 | 55 | 14.1389 | 2.9 | 7.2 | 0 | 13.28
52 | 122 | 55 | 14.1659 | 2.9 | 7.3 | 0 | 13.28
52 | 123 | 55 | 14.1928 | 2.9 | 7.4 | 0 | 13.28
52 | 124 | 55 | 14.2197 | 2.9 | 7.5 | 0 | 13.28
52 | 125 | 55 | 14.2467 | 2.9 | 7.6 | 0 | 13.28
52 | 126 | 55 | 14.2944 | 2.9 | 7.7 | 0 | 13.28
52 | 127 | 55 | 14.3421 | 2.9 | 7.8 | 0 | 13.28
52 | 128 | 55 | 14.3899 | 2.9 | 7.9 | 0 | 13.28
52 | 129 | 55 | 14.4376 | 2.9 | 8 | 0 | 13.28
52 | 130 | 55 | 14.4853 | 2.9 | 8.1 | 0 | 13.28
52 | 131 | 55 | 14.5331 | 2.9 | 8.2 | 0 | 13.28
52 | 132 | 55 | 14.5808 | 2.9 | 8.3 | 0 | 13.28
52 | 133 | 55 | 14.6285 | 2.9 | 8.4 | 0 | 13.28
52 | 134 | 55 | 14.6763 | 2.9 | 8.5 | 0 | 13.28
52 | 135 | 55 | 14.724 | 2.9 | 8.6 | 0 | 13.28
52 | 136 | 55 | 14.7717 | 2.9 | 8.7 | 0 | 13.28
52 | 137 | 55 | 14.8195 | 2.9 | 8.8 | 0 | 13.28
52 | 138 | 55 | 14.8672 | 2.9 | 8.9 | 0 | 13.28
52 | 139 | 55 | 14.9149 | 2.9 | 9 | 0 | 13.28
52 | 140 | 55 | 14.9627 | 2.9 | 9.1 | 0 | 13.28
52 | 141 | 55 | 15.0104 | 2.9 | 9.2 | 0 | 13.28
52 | 142 | 55 | 15.0581 | 2.9 | 9.3 | 0 | 13.28
52 | 143 | 55 | 15.1059 | 2.9 | 9.4 | 0 | 13.28
52 | 144 | 55 | 15.1536 | 2.9 | 9.5 | 0 | 13.28
52 | 145 | 55 | 15.2013 | 2.9 | 9.6 | 0 | 13.28
52 | 146 | 55 | 15.2491 | 2.9 | 9.7 | 0 | 13.28
52 | 147 | 55 | 15.2968 | 2.9 | 9.8 | 0 | 13.28
52 | 148 | 55 | 15.3445 | 2.9 | 9.9 | 0 | 13.28
52 | 149 | 55 | 15.3923 | 2.9 | 10 | 0 | 13.28
52 | 150 | 55 | 15.44 | 3 | 3 | 0 | 13.3
53 | 45 | 55 | 10.1067 | 3 | 3.1 | 0 | 13.3
53 | 46 | 55 | 10.1716 | 3 | 3.2 | 0 | 13.3
53 | 47 | 55 | 10.2364 | 3 | 3.3 | 0 | 13.3
53 | 48 | 55 | 10.3013 | 3 | 3.4 | 0 | 13.3
53 | 49 | 55 | 10.3662 | 3 | 3.5 | 0 | 13.3
53 | 50 | 55 | 10.4311 | 3 | 3.6 | 0 | 13.3
53 | 51 | 55 | 10.496 | 3 | 3.7 | 0 | 13.3
53 | 52 | 55 | 10.5609 | 3 | 3.8 | 0 | 13.3
53 | 53 | 55 | 10.6258 | 3 | 3.9 | 0 | 13.3
53 | 54 | 55 | 10.6907 | 3 | 4 | 0 | 13.3
53 | 55 | 55 | 10.7556 | 3 | 4.1 | 0 | 13.3
53 | 56 | 55 | 10.8204 | 3 | 4.2 | 0 | 13.3
53 | 57 | 55 | 10.8853 | 3 | 4.3 | 0 | 13.3
53 | 58 | 55 | 10.9502 | 3 | 4.4 | 0 | 13.3
53 | 59 | 55 | 11.0151 | 3 | 4.5 | 0 | 13.3
53 | 60 | 55 | 11.08 | 3 | 4.6 | 0 | 13.3
53 | 61 | 55 | 11.1449 | 3 | 4.7 | 0 | 13.3
53 | 62 | 55 | 11.2098 | 3 | 4.8 | 0 | 13.3
53 | 63 | 55 | 11.2747 | 3 | 4.9 | 0 | 13.3
53 | 64 | 55 | 11.3396 | 3 | 5 | 0 | 13.3
53 | 65 | 55 | 11.4044 | 3 | 5.1 | 0 | 13.3
53 | 66 | 55 | 11.4693 | 3 | 5.2 | 0 | 13.3
53 | 67 | 55 | 11.5342 | 3 | 5.3 | 0 | 13.3
53 | 68 | 55 | 11.5991 | 3 | 5.4 | 0 | 13.3
53 | 69 | 55 | 11.664 | 3 | 5.5 | 0 | 13.3
53 | 70 | 55 | 11.7289 | 3 | 5.6 | 0 | 13.3
53 | 71 | 55 | 11.7938 | 3 | 5.7 | 0 | 13.3
53 | 72 | 55 | 11.8587 | 3 | 5.8 | 0 | 13.3
53 | 73 | 55 | 11.9236 | 3 | 5.9 | 0 | 13.3
53 | 74 | 55 | 11.9884 | 3 | 6 | 0 | 13.3
53 | 75 | 55 | 12.0533 | 3 | 6.1 | 0 | 13.3
53 | 76 | 55 | 12.1163 | 3 | 6.2 | 0 | 13.3
53 | 77 | 55 | 12.1792 | 3 | 6.3 | 0 | 13.3
53 | 78 | 55 | 12.2421 | 3 | 6.4 | 0 | 13.3
53 | 79 | 55 | 12.3051 | 3 | 6.5 | 0 | 13.3
53 | 80 | 55 | 12.368 | 3 | 6.6 | 0 | 13.3
53 | 81 | 55 | 12.4309 | 3 | 6.7 | 0 | 13.3
53 | 82 | 55 | 12.4939 | 3 | 6.8 | 0 | 13.3
53 | 83 | 55 | 12.5568 | 3 | 6.9 | 0 | 13.3
53 | 84 | 55 | 12.6197 | 3 | 7 | 0 | 13.3
53 | 85 | 55 | 12.6827 | 3 | 7.1 | 0 | 13.3
53 | 86 | 55 | 12.7456 | 3 | 7.2 | 0 | 13.3
53 | 87 | 55 | 12.8085 | 3 | 7.3 | 0 | 13.3
53 | 88 | 55 | 12.8715 | 3 | 7.4 | 0 | 13.3
53 | 89 | 55 | 12.9344 | 3 | 7.5 | 0 | 13.3
53 | 90 | 55 | 12.9973 | 3 | 7.6 | 0 | 13.3
53 | 91 | 55 | 13.0603 | 3 | 7.7 | 0 | 13.3
53 | 92 | 55 | 13.1232 | 3 | 7.8 | 0 | 13.3
53 | 93 | 55 | 13.1861 | 3 | 7.9 | 0 | 13.3
53 | 94 | 55 | 13.2491 | 3 | 8 | 0 | 13.3
53 | 95 | 55 | 13.312 | 3 | 8.1 | 0 | 13.3
53 | 96 | 55 | 13.3749 | 3 | 8.2 | 0 | 13.3
53 | 97 | 55 | 13.4379 | 3 | 8.3 | 0 | 13.3
53 | 98 | 55 | 13.5008 | 3 | 8.4 | 0 | 13.3
53 | 99 | 55 | 13.5637 | 3 | 8.5 | 0 | 13.3
53 | 100 | 55 | 13.6267 | 3 | 8.6 | 0 | 13.3
53 | 101 | 55 | 13.6517 | 3 | 8.7 | 0 | 13.3
53 | 102 | 55 | 13.6768 | 3 | 8.8 | 0 | 13.3
53 | 103 | 55 | 13.7019 | 3 | 8.9 | 0 | 13.3
53 | 104 | 55 | 13.7269 | 3 | 9 | 0 | 13.3
53 | 105 | 55 | 13.752 | 3 | 9.1 | 0 | 13.3
53 | 106 | 55 | 13.7771 | 3 | 9.2 | 0 | 13.3
53 | 107 | 55 | 13.8021 | 3 | 9.3 | 0 | 13.3
53 | 108 | 55 | 13.8272 | 3 | 9.4 | 0 | 13.3
53 | 109 | 55 | 13.8523 | 3 | 9.5 | 0 | 13.3
53 | 110 | 55 | 13.8773 | 3 | 9.6 | 0 | 13.3
53 | 111 | 55 | 13.9024 | 3 | 9.7 | 0 | 13.3
53 | 112 | 55 | 13.9275 | 3 | 9.8 | 0 | 13.3
53 | 113 | 55 | 13.9525 | 3 | 9.9 | 0 | 13.3
53 | 114 | 55 | 13.9776 | 3 | 10 | 0 | 13.3
53 | 115 | 55 | 14.0027 | 3.1 | 3 | 0 | 13.33
53 | 116 | 55 | 14.0277 | 3.1 | 3.1 | 0 | 13.33
53 | 117 | 55 | 14.0528 | 3.1 | 3.2 | 0 | 13.33
53 | 118 | 55 | 14.0779 | 3.1 | 3.3 | 0 | 13.33
53 | 119 | 55 | 14.1029 | 3.1 | 3.4 | 0 | 13.33
53 | 120 | 55 | 14.128 | 3.1 | 3.5 | 0 | 13.33
53 | 121 | 55 | 14.1531 | 3.1 | 3.6 | 0 | 13.33
53 | 122 | 55 | 14.1781 | 3.1 | 3.7 | 0 | 13.33
53 | 123 | 55 | 14.2032 | 3.1 | 3.8 | 0 | 13.33
53 | 124 | 55 | 14.2283 | 3.1 | 3.9 | 0 | 13.33
53 | 125 | 55 | 14.2533 | 3.1 | 4 | 0 | 13.33
53 | 126 | 55 | 14.3016 | 3.1 | 4.1 | 0 | 13.33
53 | 127 | 55 | 14.3499 | 3.1 | 4.2 | 0 | 13.33
53 | 128 | 55 | 14.3981 | 3.1 | 4.3 | 0 | 13.33
53 | 129 | 55 | 14.4464 | 3.1 | 4.4 | 0 | 13.33
53 | 130 | 55 | 14.4947 | 3.1 | 4.5 | 0 | 13.33
53 | 131 | 55 | 14.5429 | 3.1 | 4.6 | 0 | 13.33
53 | 132 | 55 | 14.5912 | 3.1 | 4.7 | 0 | 13.33
53 | 133 | 55 | 14.6395 | 3.1 | 4.8 | 0 | 13.33
53 | 134 | 55 | 14.6877 | 3.1 | 4.9 | 0 | 13.33
53 | 135 | 55 | 14.736 | 3.1 | 5 | 0 | 13.33
53 | 136 | 55 | 14.7843 | 3.1 | 5.1 | 0 | 13.33
53 | 137 | 55 | 14.8325 | 3.1 | 5.2 | 0 | 13.33
53 | 138 | 55 | 14.8808 | 3.1 | 5.3 | 0 | 13.33
53 | 139 | 55 | 14.9291 | 3.1 | 5.4 | 0 | 13.33
53 | 140 | 55 | 14.9773 | 3.1 | 5.5 | 0 | 13.33
53 | 141 | 55 | 15.0256 | 3.1 | 5.6 | 0 | 13.33
53 | 142 | 55 | 15.0739 | 3.1 | 5.7 | 0 | 13.33
53 | 143 | 55 | 15.1221 | 3.1 | 5.8 | 0 | 13.33
53 | 144 | 55 | 15.1704 | 3.1 | 5.9 | 0 | 13.33
53 | 145 | 55 | 15.2187 | 3.1 | 6 | 0 | 13.33
53 | 146 | 55 | 15.2669 | 3.1 | 6.1 | 0 | 13.33
53 | 147 | 55 | 15.3152 | 3.1 | 6.2 | 0 | 13.33
53 | 148 | 55 | 15.3635 | 3.1 | 6.3 | 0 | 13.33
53 | 149 | 55 | 15.4117 | 3.1 | 6.4 | 0 | 13.33
53 | 150 | 55 | 15.46 | 3.1 | 6.5 | 0 | 13.33
54 | 45 | 55 | 10.12 | 3.1 | 6.6 | 0 | 13.33
54 | 46 | 55 | 10.1847 | 3.1 | 6.7 | 0 | 13.33
54 | 47 | 55 | 10.2493 | 3.1 | 6.8 | 0 | 13.33
54 | 48 | 55 | 10.314 | 3.1 | 6.9 | 0 | 13.33
54 | 49 | 55 | 10.3787 | 3.1 | 7 | 0 | 13.33
54 | 50 | 55 | 10.4433 | 3.1 | 7.1 | 0 | 13.33
54 | 51 | 55 | 10.508 | 3.1 | 7.2 | 0 | 13.33
54 | 52 | 55 | 10.5727 | 3.1 | 7.3 | 0 | 13.33
54 | 53 | 55 | 10.6373 | 3.1 | 7.4 | 0 | 13.33
54 | 54 | 55 | 10.702 | 3.1 | 7.5 | 0 | 13.33
54 | 55 | 55 | 10.7667 | 3.1 | 7.6 | 0 | 13.33
54 | 56 | 55 | 10.8313 | 3.1 | 7.7 | 0 | 13.33
54 | 57 | 55 | 10.896 | 3.1 | 7.8 | 0 | 13.33
54 | 58 | 55 | 10.9607 | 3.1 | 7.9 | 0 | 13.33
54 | 59 | 55 | 11.0253 | 3.1 | 8 | 0 | 13.33
54 | 60 | 55 | 11.09 | 3.1 | 8.1 | 0 | 13.33
54 | 61 | 55 | 11.1547 | 3.1 | 8.2 | 0 | 13.33
54 | 62 | 55 | 11.2193 | 3.1 | 8.3 | 0 | 13.33
54 | 63 | 55 | 11.284 | 3.1 | 8.4 | 0 | 13.33
54 | 64 | 55 | 11.3487 | 3.1 | 8.5 | 0 | 13.33
54 | 65 | 55 | 11.4133 | 3.1 | 8.6 | 0 | 13.33
54 | 66 | 55 | 11.478 | 3.1 | 8.7 | 0 | 13.33
54 | 67 | 55 | 11.5427 | 3.1 | 8.8 | 0 | 13.33
54 | 68 | 55 | 11.6073 | 3.1 | 8.9 | 0 | 13.33
54 | 69 | 55 | 11.672 | 3.1 | 9 | 0 | 13.33
54 | 70 | 55 | 11.7367 | 3.1 | 9.1 | 0 | 13.33
54 | 71 | 55 | 11.8013 | 3.1 | 9.2 | 0 | 13.33
54 | 72 | 55 | 11.866 | 3.1 | 9.3 | 0 | 13.33
54 | 73 | 55 | 11.9307 | 3.1 | 9.4 | 0 | 13.33
54 | 74 | 55 | 11.9953 | 3.1 | 9.5 | 0 | 13.33
54 | 75 | 55 | 12.06 | 3.1 | 9.6 | 0 | 13.33
54 | 76 | 55 | 12.1248 | 3.1 | 9.7 | 0 | 13.33
54 | 77 | 55 | 12.1896 | 3.1 | 9.8 | 0 | 13.33
54 | 78 | 55 | 12.2544 | 3.1 | 9.9 | 0 | 13.33
54 | 79 | 55 | 12.3192 | 3.1 | 10 | 0 | 13.33
54 | 80 | 55 | 12.384 | 3.2 | 3 | 0 | 13.36
54 | 81 | 55 | 12.4488 | 3.2 | 3.1 | 0 | 13.36
54 | 82 | 55 | 12.5136 | 3.2 | 3.2 | 0 | 13.36
54 | 83 | 55 | 12.5784 | 3.2 | 3.3 | 0 | 13.36
54 | 84 | 55 | 12.6432 | 3.2 | 3.4 | 0 | 13.36
54 | 85 | 55 | 12.708 | 3.2 | 3.5 | 0 | 13.36
54 | 86 | 55 | 12.7728 | 3.2 | 3.6 | 0 | 13.36
54 | 87 | 55 | 12.8376 | 3.2 | 3.7 | 0 | 13.36
54 | 88 | 55 | 12.9024 | 3.2 | 3.8 | 0 | 13.36
54 | 89 | 55 | 12.9672 | 3.2 | 3.9 | 0 | 13.36
54 | 90 | 55 | 13.032 | 3.2 | 4 | 0 | 13.36
54 | 91 | 55 | 13.0968 | 3.2 | 4.1 | 0 | 13.36
54 | 92 | 55 | 13.1616 | 3.2 | 4.2 | 0 | 13.36
54 | 93 | 55 | 13.2264 | 3.2 | 4.3 | 0 | 13.36
54 | 94 | 55 | 13.2912 | 3.2 | 4.4 | 0 | 13.36
54 | 95 | 55 | 13.356 | 3.2 | 4.5 | 0 | 13.36
54 | 96 | 55 | 13.4208 | 3.2 | 4.6 | 0 | 13.36
54 | 97 | 55 | 13.4856 | 3.2 | 4.7 | 0 | 13.36
54 | 98 | 55 | 13.5504 | 3.2 | 4.8 | 0 | 13.36
54 | 99 | 55 | 13.6152 | 3.2 | 4.9 | 0 | 13.36
54 | 100 | 55 | 13.68 | 3.2 | 5 | 0 | 13.36
54 | 101 | 55 | 13.7032 | 3.2 | 5.1 | 0 | 13.36
54 | 102 | 55 | 13.7264 | 3.2 | 5.2 | 0 | 13.36
54 | 103 | 55 | 13.7496 | 3.2 | 5.3 | 0 | 13.36
54 | 104 | 55 | 13.7728 | 3.2 | 5.4 | 0 | 13.36
54 | 105 | 55 | 13.796 | 3.2 | 5.5 | 0 | 13.36
54 | 106 | 55 | 13.8192 | 3.2 | 5.6 | 0 | 13.36
54 | 107 | 55 | 13.8424 | 3.2 | 5.7 | 0 | 13.36
54 | 108 | 55 | 13.8656 | 3.2 | 5.8 | 0 | 13.36
54 | 109 | 55 | 13.8888 | 3.2 | 5.9 | 0 | 13.36
54 | 110 | 55 | 13.912 | 3.2 | 6 | 0 | 13.36
54 | 111 | 55 | 13.9352 | 3.2 | 6.1 | 0 | 13.36
54 | 112 | 55 | 13.9584 | 3.2 | 6.2 | 0 | 13.36
54 | 113 | 55 | 13.9816 | 3.2 | 6.3 | 0 | 13.36
54 | 114 | 55 | 14.0048 | 3.2 | 6.4 | 0 | 13.36
54 | 115 | 55 | 14.028 | 3.2 | 6.5 | 0 | 13.36
54 | 116 | 55 | 14.0512 | 3.2 | 6.6 | 0 | 13.36
54 | 117 | 55 | 14.0744 | 3.2 | 6.7 | 0 | 13.36
54 | 118 | 55 | 14.0976 | 3.2 | 6.8 | 0 | 13.36
54 | 119 | 55 | 14.1208 | 3.2 | 6.9 | 0 | 13.36
54 | 120 | 55 | 14.144 | 3.2 | 7 | 0 | 13.36
54 | 121 | 55 | 14.1672 | 3.2 | 7.1 | 0 | 13.36
54 | 122 | 55 | 14.1904 | 3.2 | 7.2 | 0 | 13.36
54 | 123 | 55 | 14.2136 | 3.2 | 7.3 | 0 | 13.36
54 | 124 | 55 | 14.2368 | 3.2 | 7.4 | 0 | 13.36
54 | 125 | 55 | 14.26 | 3.2 | 7.5 | 0 | 13.36
54 | 126 | 55 | 14.3088 | 3.2 | 7.6 | 0 | 13.36
54 | 127 | 55 | 14.3576 | 3.2 | 7.7 | 0 | 13.36
54 | 128 | 55 | 14.4064 | 3.2 | 7.8 | 0 | 13.36
54 | 129 | 55 | 14.4552 | 3.2 | 7.9 | 0 | 13.36
54 | 130 | 55 | 14.504 | 3.2 | 8 | 0 | 13.36
54 | 131 | 55 | 14.5528 | 3.2 | 8.1 | 0 | 13.36
54 | 132 | 55 | 14.6016 | 3.2 | 8.2 | 0 | 13.36
54 | 133 | 55 | 14.6504 | 3.2 | 8.3 | 0 | 13.36
54 | 134 | 55 | 14.6992 | 3.2 | 8.4 | 0 | 13.36
54 | 135 | 55 | 14.748 | 3.2 | 8.5 | 0 | 13.36
54 | 136 | 55 | 14.7968 | 3.2 | 8.6 | 0 | 13.36
54 | 137 | 55 | 14.8456 | 3.2 | 8.7 | 0 | 13.36
54 | 138 | 55 | 14.8944 | 3.2 | 8.8 | 0 | 13.36
54 | 139 | 55 | 14.9432 | 3.2 | 8.9 | 0 | 13.36
54 | 140 | 55 | 14.992 | 3.2 | 9 | 0 | 13.36
54 | 141 | 55 | 15.0408 | 3.2 | 9.1 | 0 | 13.36
54 | 142 | 55 | 15.0896 | 3.2 | 9.2 | 0 | 13.36
54 | 143 | 55 | 15.1384 | 3.2 | 9.3 | 0 | 13.36
54 | 144 | 55 | 15.1872 | 3.2 | 9.4 | 0 | 13.36
54 | 145 | 55 | 15.236 | 3.2 | 9.5 | 0 | 13.36
54 | 146 | 55 | 15.2848 | 3.2 | 9.6 | 0 | 13.36
54 | 147 | 55 | 15.3336 | 3.2 | 9.7 | 0 | 13.36
54 | 148 | 55 | 15.3824 | 3.2 | 9.8 | 0 | 13.36
54 | 149 | 55 | 15.4312 | 3.2 | 9.9 | 0 | 13.36
54 | 150 | 55 | 15.48 | 3.2 | 10 | 0 | 13.36
55 | 45 | 55 | 10.1333 | 3.3 | 3 | 0 | 13.39
55 | 46 | 55 | 10.1978 | 3.3 | 3.1 | 0 | 13.39
55 | 47 | 55 | 10.2622 | 3.3 | 3.2 | 0 | 13.39
55 | 48 | 55 | 10.3267 | 3.3 | 3.3 | 0 | 13.39
55 | 49 | 55 | 10.3911 | 3.3 | 3.4 | 0 | 13.39
55 | 50 | 55 | 10.4556 | 3.3 | 3.5 | 0 | 13.39
55 | 51 | 55 | 10.52 | 3.3 | 3.6 | 0 | 13.39
55 | 52 | 55 | 10.5844 | 3.3 | 3.7 | 0 | 13.39
55 | 53 | 55 | 10.6489 | 3.3 | 3.8 | 0 | 13.39
55 | 54 | 55 | 10.7133 | 3.3 | 3.9 | 0 | 13.39
55 | 55 | 55 | 10.7778 | 3.3 | 4 | 0 | 13.39
55 | 56 | 55 | 10.8422 | 3.3 | 4.1 | 0 | 13.39
55 | 57 | 55 | 10.9067 | 3.3 | 4.2 | 0 | 13.39
55 | 58 | 55 | 10.9711 | 3.3 | 4.3 | 0 | 13.39
55 | 59 | 55 | 11.0356 | 3.3 | 4.4 | 0 | 13.39
55 | 60 | 55 | 11.1 | 3.3 | 4.5 | 0 | 13.39
55 | 61 | 55 | 11.1644 | 3.3 | 4.6 | 0 | 13.39
55 | 62 | 55 | 11.2289 | 3.3 | 4.7 | 0 | 13.39
55 | 63 | 55 | 11.2933 | 3.3 | 4.8 | 0 | 13.39
55 | 64 | 55 | 11.3578 | 3.3 | 4.9 | 0 | 13.39
55 | 65 | 55 | 11.4222 | 3.3 | 5 | 0 | 13.39
55 | 66 | 55 | 11.4867 | 3.3 | 5.1 | 0 | 13.39
55 | 67 | 55 | 11.5511 | 3.3 | 5.2 | 0 | 13.39
55 | 68 | 55 | 11.6156 | 3.3 | 5.3 | 0 | 13.39
55 | 69 | 55 | 11.68 | 3.3 | 5.4 | 0 | 13.39
55 | 70 | 55 | 11.7444 | 3.3 | 5.5 | 0 | 13.39
55 | 71 | 55 | 11.8089 | 3.3 | 5.6 | 0 | 13.39
55 | 72 | 55 | 11.8733 | 3.3 | 5.7 | 0 | 13.39
55 | 73 | 55 | 11.9378 | 3.3 | 5.8 | 0 | 13.39
55 | 74 | 55 | 12.0022 | 3.3 | 5.9 | 0 | 13.39
55 | 75 | 55 | 12.0667 | 3.3 | 6 | 0 | 13.39
55 | 76 | 55 | 12.1333 | 3.3 | 6.1 | 0 | 13.39
55 | 77 | 55 | 12.2 | 3.3 | 6.2 | 0 | 13.39
55 | 78 | 55 | 12.2667 | 3.3 | 6.3 | 0 | 13.39
55 | 79 | 55 | 12.3333 | 3.3 | 6.4 | 0 | 13.39
55 | 80 | 55 | 12.4 | 3.3 | 6.5 | 0 | 13.39
55 | 81 | 55 | 12.4667 | 3.3 | 6.6 | 0 | 13.39
55 | 82 | 55 | 12.5333 | 3.3 | 6.7 | 0 | 13.39
55 | 83 | 55 | 12.6 | 3.3 | 6.8 | 0 | 13.39
55 | 84 | 55 | 12.6667 | 3.3 | 6.9 | 0 | 13.39
55 | 85 | 55 | 12.7333 | 3.3 | 7 | 0 | 13.39
55 | 86 | 55 | 12.8 | 3.3 | 7.1 | 0 | 13.39
55 | 87 | 55 | 12.8667 | 3.3 | 7.2 | 0 | 13.39
55 | 88 | 55 | 12.9333 | 3.3 | 7.3 | 0 | 13.39
55 | 89 | 55 | 13 | 3.3 | 7.4 | 0 | 13.39
55 | 90 | 55 | 13.0667 | 3.3 | 7.5 | 0 | 13.39
55 | 91 | 55 | 13.1333 | 3.3 | 7.6 | 0 | 13.39
55 | 92 | 55 | 13.2 | 3.3 | 7.7 | 0 | 13.39
55 | 93 | 55 | 13.2667 | 3.3 | 7.8 | 0 | 13.39
55 | 94 | 55 | 13.3333 | 3.3 | 7.9 | 0 | 13.39
55 | 95 | 55 | 13.4 | 3.3 | 8 | 0 | 13.39
55 | 96 | 55 | 13.4667 | 3.3 | 8.1 | 0 | 13.39
55 | 97 | 55 | 13.5333 | 3.3 | 8.2 | 0 | 13.39
55 | 98 | 55 | 13.6 | 3.3 | 8.3 | 0 | 13.39
55 | 99 | 55 | 13.6667 | 3.3 | 8.4 | 0 | 13.39
55 | 100 | 55 | 13.7333 | 3.3 | 8.5 | 0 | 13.39
55 | 101 | 55 | 13.7547 | 3.3 | 8.6 | 0 | 13.39
55 | 102 | 55 | 13.776 | 3.3 | 8.7 | 0 | 13.39
55 | 103 | 55 | 13.7973 | 3.3 | 8.8 | 0 | 13.39
55 | 104 | 55 | 13.8187 | 3.3 | 8.9 | 0 | 13.39
55 | 105 | 55 | 13.84 | 3.3 | 9 | 0 | 13.39
55 | 106 | 55 | 13.8613 | 3.3 | 9.1 | 0 | 13.39
55 | 107 | 55 | 13.8827 | 3.3 | 9.2 | 0 | 13.39
55 | 108 | 55 | 13.904 | 3.3 | 9.3 | 0 | 13.39
55 | 109 | 55 | 13.9253 | 3.3 | 9.4 | 0 | 13.39
55 | 110 | 55 | 13.9467 | 3.3 | 9.5 | 0 | 13.39
55 | 111 | 55 | 13.968 | 3.3 | 9.6 | 0 | 13.39
55 | 112 | 55 | 13.9893 | 3.3 | 9.7 | 0 | 13.39
55 | 113 | 55 | 14.0107 | 3.3 | 9.8 | 0 | 13.39
55 | 114 | 55 | 14.032 | 3.3 | 9.9 | 0 | 13.39
55 | 115 | 55 | 14.0533 | 3.3 | 10 | 0 | 13.39
55 | 116 | 55 | 14.0747 | 3.4 | 3 | 0 | 13.42
55 | 117 | 55 | 14.096 | 3.4 | 3.1 | 0 | 13.42
55 | 118 | 55 | 14.1173 | 3.4 | 3.2 | 0 | 13.42
55 | 119 | 55 | 14.1387 | 3.4 | 3.3 | 0 | 13.42
55 | 120 | 55 | 14.16 | 3.4 | 3.4 | 0 | 13.42
55 | 121 | 55 | 14.1813 | 3.4 | 3.5 | 0 | 13.42
55 | 122 | 55 | 14.2027 | 3.4 | 3.6 | 0 | 13.42
55 | 123 | 55 | 14.224 | 3.4 | 3.7 | 0 | 13.42
55 | 124 | 55 | 14.2453 | 3.4 | 3.8 | 0 | 13.42
55 | 125 | 55 | 14.2667 | 3.4 | 3.9 | 0 | 13.42
55 | 126 | 55 | 14.316 | 3.4 | 4 | 0 | 13.42
55 | 127 | 55 | 14.3653 | 3.4 | 4.1 | 0 | 13.42
55 | 128 | 55 | 14.4147 | 3.4 | 4.2 | 0 | 13.42
55 | 129 | 55 | 14.464 | 3.4 | 4.3 | 0 | 13.42
55 | 130 | 55 | 14.5133 | 3.4 | 4.4 | 0 | 13.42
55 | 131 | 55 | 14.5627 | 3.4 | 4.5 | 0 | 13.42
55 | 132 | 55 | 14.612 | 3.4 | 4.6 | 0 | 13.42
55 | 133 | 55 | 14.6613 | 3.4 | 4.7 | 0 | 13.42
55 | 134 | 55 | 14.7107 | 3.4 | 4.8 | 0 | 13.42
55 | 135 | 55 | 14.76 | 3.4 | 4.9 | 0 | 13.42
55 | 136 | 55 | 14.8093 | 3.4 | 5 | 0 | 13.42
55 | 137 | 55 | 14.8587 | 3.4 | 5.1 | 0 | 13.42
55 | 138 | 55 | 14.908 | 3.4 | 5.2 | 0 | 13.42
55 | 139 | 55 | 14.9573 | 3.4 | 5.3 | 0 | 13.42
55 | 140 | 55 | 15.0067 | 3.4 | 5.4 | 0 | 13.42
55 | 141 | 55 | 15.056 | 3.4 | 5.5 | 0 | 13.42
55 | 142 | 55 | 15.1053 | 3.4 | 5.6 | 0 | 13.42
55 | 143 | 55 | 15.1547 | 3.4 | 5.7 | 0 | 13.42
55 | 144 | 55 | 15.204 | 3.4 | 5.8 | 0 | 13.42
55 | 145 | 55 | 15.2533 | 3.4 | 5.9 | 0 | 13.42
55 | 146 | 55 | 15.3027 | 3.4 | 6 | 0 | 13.42
55 | 147 | 55 | 15.352 | 3.4 | 6.1 | 0 | 13.42
55 | 148 | 55 | 15.4013 | 3.4 | 6.2 | 0 | 13.42
55 | 149 | 55 | 15.4507 | 3.4 | 6.3 | 0 | 13.42
55 | 150 | 55 | 15.5 | 3.4 | 6.4 | 0 | 13.42
56 | 45 | 55 | 10.1467 | 3.4 | 6.5 | 0 | 13.42
56 | 46 | 55 | 10.2109 | 3.4 | 6.6 | 0 | 13.42
56 | 47 | 55 | 10.2751 | 3.4 | 6.7 | 0 | 13.42
56 | 48 | 55 | 10.3393 | 3.4 | 6.8 | 0 | 13.42
56 | 49 | 55 | 10.4036 | 3.4 | 6.9 | 0 | 13.42
56 | 50 | 55 | 10.4678 | 3.4 | 7 | 0 | 13.42
56 | 51 | 55 | 10.532 | 3.4 | 7.1 | 0 | 13.42
56 | 52 | 55 | 10.5962 | 3.4 | 7.2 | 0 | 13.42
56 | 53 | 55 | 10.6604 | 3.4 | 7.3 | 0 | 13.42
56 | 54 | 55 | 10.7247 | 3.4 | 7.4 | 0 | 13.42
56 | 55 | 55 | 10.7889 | 3.4 | 7.5 | 0 | 13.42
56 | 56 | 55 | 10.8531 | 3.4 | 7.6 | 0 | 13.42
56 | 57 | 55 | 10.9173 | 3.4 | 7.7 | 0 | 13.42
56 | 58 | 55 | 10.9816 | 3.4 | 7.8 | 0 | 13.42
56 | 59 | 55 | 11.0458 | 3.4 | 7.9 | 0 | 13.42
56 | 60 | 55 | 11.11 | 3.4 | 8 | 0 | 13.42
56 | 61 | 55 | 11.1742 | 3.4 | 8.1 | 0 | 13.42
56 | 62 | 55 | 11.2384 | 3.4 | 8.2 | 0 | 13.42
56 | 63 | 55 | 11.3027 | 3.4 | 8.3 | 0 | 13.42
56 | 64 | 55 | 11.3669 | 3.4 | 8.4 | 0 | 13.42
56 | 65 | 55 | 11.4311 | 3.4 | 8.5 | 0 | 13.42
56 | 66 | 55 | 11.4953 | 3.4 | 8.6 | 0 | 13.42
56 | 67 | 55 | 11.5596 | 3.4 | 8.7 | 0 | 13.42
56 | 68 | 55 | 11.6238 | 3.4 | 8.8 | 0 | 13.42
56 | 69 | 55 | 11.688 | 3.4 | 8.9 | 0 | 13.42
56 | 70 | 55 | 11.7522 | 3.4 | 9 | 0 | 13.42
56 | 71 | 55 | 11.8164 | 3.4 | 9.1 | 0 | 13.42
56 | 72 | 55 | 11.8807 | 3.4 | 9.2 | 0 | 13.42
56 | 73 | 55 | 11.9449 | 3.4 | 9.3 | 0 | 13.42
56 | 74 | 55 | 12.0091 | 3.4 | 9.4 | 0 | 13.42
56 | 75 | 55 | 12.0733 | 3.4 | 9.5 | 0 | 13.42
56 | 76 | 55 | 12.1419 | 3.4 | 9.6 | 0 | 13.42
56 | 77 | 55 | 12.2104 | 3.4 | 9.7 | 0 | 13.42
56 | 78 | 55 | 12.2789 | 3.4 | 9.8 | 0 | 13.42
56 | 79 | 55 | 12.3475 | 3.4 | 9.9 | 0 | 13.42
56 | 80 | 55 | 12.416 | 3.4 | 10 | 0 | 13.42
56 | 81 | 55 | 12.4845 | 3.5 | 3 | 0 | 13.45
56 | 82 | 55 | 12.5531 | 3.5 | 3.1 | 0 | 13.45
56 | 83 | 55 | 12.6216 | 3.5 | 3.2 | 0 | 13.45
56 | 84 | 55 | 12.6901 | 3.5 | 3.3 | 0 | 13.45
56 | 85 | 55 | 12.7587 | 3.5 | 3.4 | 0 | 13.45
56 | 86 | 55 | 12.8272 | 3.5 | 3.5 | 0 | 13.45
56 | 87 | 55 | 12.8957 | 3.5 | 3.6 | 0 | 13.45
56 | 88 | 55 | 12.9643 | 3.5 | 3.7 | 0 | 13.45
56 | 89 | 55 | 13.0328 | 3.5 | 3.8 | 0 | 13.45
56 | 90 | 55 | 13.1013 | 3.5 | 3.9 | 0 | 13.45
56 | 91 | 55 | 13.1699 | 3.5 | 4 | 0 | 13.45
56 | 92 | 55 | 13.2384 | 3.5 | 4.1 | 0 | 13.45
56 | 93 | 55 | 13.3069 | 3.5 | 4.2 | 0 | 13.45
56 | 94 | 55 | 13.3755 | 3.5 | 4.3 | 0 | 13.45
56 | 95 | 55 | 13.444 | 3.5 | 4.4 | 0 | 13.45
56 | 96 | 55 | 13.5125 | 3.5 | 4.5 | 0 | 13.45
56 | 97 | 55 | 13.5811 | 3.5 | 4.6 | 0 | 13.45
56 | 98 | 55 | 13.6496 | 3.5 | 4.7 | 0 | 13.45
56 | 99 | 55 | 13.7181 | 3.5 | 4.8 | 0 | 13.45
56 | 100 | 55 | 13.7867 | 3.5 | 4.9 | 0 | 13.45
56 | 101 | 55 | 13.8061 | 3.5 | 5 | 0 | 13.45
56 | 102 | 55 | 13.8256 | 3.5 | 5.1 | 0 | 13.45
56 | 103 | 55 | 13.8451 | 3.5 | 5.2 | 0 | 13.45
56 | 104 | 55 | 13.8645 | 3.5 | 5.3 | 0 | 13.45
56 | 105 | 55 | 13.884 | 3.5 | 5.4 | 0 | 13.45
56 | 106 | 55 | 13.9035 | 3.5 | 5.5 | 0 | 13.45
56 | 107 | 55 | 13.9229 | 3.5 | 5.6 | 0 | 13.45
56 | 108 | 55 | 13.9424 | 3.5 | 5.7 | 0 | 13.45
56 | 109 | 55 | 13.9619 | 3.5 | 5.8 | 0 | 13.45
56 | 110 | 55 | 13.9813 | 3.5 | 5.9 | 0 | 13.45
56 | 111 | 55 | 14.0008 | 3.5 | 6 | 0 | 13.45
56 | 112 | 55 | 14.0203 | 3.5 | 6.1 | 0 | 13.45
56 | 113 | 55 | 14.0397 | 3.5 | 6.2 | 0 | 13.45
56 | 114 | 55 | 14.0592 | 3.5 | 6.3 | 0 | 13.45
56 | 115 | 55 | 14.0787 | 3.5 | 6.4 | 0 | 13.45
56 | 116 | 55 | 14.0981 | 3.5 | 6.5 | 0 | 13.45
56 | 117 | 55 | 14.1176 | 3.5 | 6.6 | 0 | 13.45
56 | 118 | 55 | 14.1371 | 3.5 | 6.7 | 0 | 13.45
56 | 119 | 55 | 14.1565 | 3.5 | 6.8 | 0 | 13.45
56 | 120 | 55 | 14.176 | 3.5 | 6.9 | 0 | 13.45
56 | 121 | 55 | 14.1955 | 3.5 | 7 | 0 | 13.45
56 | 122 | 55 | 14.2149 | 3.5 | 7.1 | 0 | 13.45
56 | 123 | 55 | 14.2344 | 3.5 | 7.2 | 0 | 13.45
56 | 124 | 55 | 14.2539 | 3.5 | 7.3 | 0 | 13.45
56 | 125 | 55 | 14.2733 | 3.5 | 7.4 | 0 | 13.45
56 | 126 | 55 | 14.3232 | 3.5 | 7.5 | 0 | 13.45
56 | 127 | 55 | 14.3731 | 3.5 | 7.6 | 0 | 13.45
56 | 128 | 55 | 14.4229 | 3.5 | 7.7 | 0 | 13.45
56 | 129 | 55 | 14.4728 | 3.5 | 7.8 | 0 | 13.45
56 | 130 | 55 | 14.5227 | 3.5 | 7.9 | 0 | 13.45
56 | 131 | 55 | 14.5725 | 3.5 | 8 | 0 | 13.45
56 | 132 | 55 | 14.6224 | 3.5 | 8.1 | 0 | 13.45
56 | 133 | 55 | 14.6723 | 3.5 | 8.2 | 0 | 13.45
56 | 134 | 55 | 14.7221 | 3.5 | 8.3 | 0 | 13.45
56 | 135 | 55 | 14.772 | 3.5 | 8.4 | 0 | 13.45
56 | 136 | 55 | 14.8219 | 3.5 | 8.5 | 0 | 13.45
56 | 137 | 55 | 14.8717 | 3.5 | 8.6 | 0 | 13.45
56 | 138 | 55 | 14.9216 | 3.5 | 8.7 | 0 | 13.45
56 | 139 | 55 | 14.9715 | 3.5 | 8.8 | 0 | 13.45
56 | 140 | 55 | 15.0213 | 3.5 | 8.9 | 0 | 13.45
56 | 141 | 55 | 15.0712 | 3.5 | 9 | 0 | 13.45
56 | 142 | 55 | 15.1211 | 3.5 | 9.1 | 0 | 13.45
56 | 143 | 55 | 15.1709 | 3.5 | 9.2 | 0 | 13.45
56 | 144 | 55 | 15.2208 | 3.5 | 9.3 | 0 | 13.45
56 | 145 | 55 | 15.2707 | 3.5 | 9.4 | 0 | 13.45
56 | 146 | 55 | 15.3205 | 3.5 | 9.5 | 0 | 13.45
56 | 147 | 55 | 15.3704 | 3.5 | 9.6 | 0 | 13.45
56 | 148 | 55 | 15.4203 | 3.5 | 9.7 | 0 | 13.45
56 | 149 | 55 | 15.4701 | 3.5 | 9.8 | 0 | 13.45
56 | 150 | 55 | 15.52 | 3.5 | 9.9 | 0 | 13.45
57 | 45 | 55 | 10.16 | 3.5 | 10 | 0 | 13.45
57 | 46 | 55 | 10.224 | 3.6 | 3 | 0 | 13.48
57 | 47 | 55 | 10.288 | 3.6 | 3.1 | 0 | 13.48
57 | 48 | 55 | 10.352 | 3.6 | 3.2 | 0 | 13.48
57 | 49 | 55 | 10.416 | 3.6 | 3.3 | 0 | 13.48
57 | 50 | 55 | 10.48 | 3.6 | 3.4 | 0 | 13.48
57 | 51 | 55 | 10.544 | 3.6 | 3.5 | 0 | 13.48
57 | 52 | 55 | 10.608 | 3.6 | 3.6 | 0 | 13.48
57 | 53 | 55 | 10.672 | 3.6 | 3.7 | 0 | 13.48
57 | 54 | 55 | 10.736 | 3.6 | 3.8 | 0 | 13.48
57 | 55 | 55 | 10.8 | 3.6 | 3.9 | 0 | 13.48
57 | 56 | 55 | 10.864 | 3.6 | 4 | 0 | 13.48
57 | 57 | 55 | 10.928 | 3.6 | 4.1 | 0 | 13.48
57 | 58 | 55 | 10.992 | 3.6 | 4.2 | 0 | 13.48
57 | 59 | 55 | 11.056 | 3.6 | 4.3 | 0 | 13.48
57 | 60 | 55 | 11.12 | 3.6 | 4.4 | 0 | 13.48
57 | 61 | 55 | 11.184 | 3.6 | 4.5 | 0 | 13.48
57 | 62 | 55 | 11.248 | 3.6 | 4.6 | 0 | 13.48
57 | 63 | 55 | 11.312 | 3.6 | 4.7 | 0 | 13.48
57 | 64 | 55 | 11.376 | 3.6 | 4.8 | 0 | 13.48
57 | 65 | 55 | 11.44 | 3.6 | 4.9 | 0 | 13.48
57 | 66 | 55 | 11.504 | 3.6 | 5 | 0 | 13.48
57 | 67 | 55 | 11.568 | 3.6 | 5.1 | 0 | 13.48
57 | 68 | 55 | 11.632 | 3.6 | 5.2 | 0 | 13.48
57 | 69 | 55 | 11.696 | 3.6 | 5.3 | 0 | 13.48
57 | 70 | 55 | 11.76 | 3.6 | 5.4 | 0 | 13.48
57 | 71 | 55 | 11.824 | 3.6 | 5.5 | 0 | 13.48
57 | 72 | 55 | 11.888 | 3.6 | 5.6 | 0 | 13.48
57 | 73 | 55 | 11.952 | 3.6 | 5.7 | 0 | 13.48
57 | 74 | 55 | 12.016 | 3.6 | 5.8 | 0 | 13.48
57 | 75 | 55 | 12.08 | 3.6 | 5.9 | 0 | 13.48
57 | 76 | 55 | 12.1504 | 3.6 | 6 | 0 | 13.48
57 | 77 | 55 | 12.2208 | 3.6 | 6.1 | 0 | 13.48
57 | 78 | 55 | 12.2912 | 3.6 | 6.2 | 0 | 13.48
57 | 79 | 55 | 12.3616 | 3.6 | 6.3 | 0 | 13.48
57 | 80 | 55 | 12.432 | 3.6 | 6.4 | 0 | 13.48
57 | 81 | 55 | 12.5024 | 3.6 | 6.5 | 0 | 13.48
57 | 82 | 55 | 12.5728 | 3.6 | 6.6 | 0 | 13.48
57 | 83 | 55 | 12.6432 | 3.6 | 6.7 | 0 | 13.48
57 | 84 | 55 | 12.7136 | 3.6 | 6.8 | 0 | 13.48
57 | 85 | 55 | 12.784 | 3.6 | 6.9 | 0 | 13.48
57 | 86 | 55 | 12.8544 | 3.6 | 7 | 0 | 13.48
57 | 87 | 55 | 12.9248 | 3.6 | 7.1 | 0 | 13.48
57 | 88 | 55 | 12.9952 | 3.6 | 7.2 | 0 | 13.48
57 | 89 | 55 | 13.0656 | 3.6 | 7.3 | 0 | 13.48
57 | 90 | 55 | 13.136 | 3.6 | 7.4 | 0 | 13.48
57 | 91 | 55 | 13.2064 | 3.6 | 7.5 | 0 | 13.48
57 | 92 | 55 | 13.2768 | 3.6 | 7.6 | 0 | 13.48
57 | 93 | 55 | 13.3472 | 3.6 | 7.7 | 0 | 13.48
57 | 94 | 55 | 13.4176 | 3.6 | 7.8 | 0 | 13.48
57 | 95 | 55 | 13.488 | 3.6 | 7.9 | 0 | 13.48
57 | 96 | 55 | 13.5584 | 3.6 | 8 | 0 | 13.48
57 | 97 | 55 | 13.6288 | 3.6 | 8.1 | 0 | 13.48
57 | 98 | 55 | 13.6992 | 3.6 | 8.2 | 0 | 13.48
57 | 99 | 55 | 13.7696 | 3.6 | 8.3 | 0 | 13.48
57 | 100 | 55 | 13.84 | 3.6 | 8.4 | 0 | 13.48
57 | 101 | 55 | 13.8576 | 3.6 | 8.5 | 0 | 13.48
57 | 102 | 55 | 13.8752 | 3.6 | 8.6 | 0 | 13.48
57 | 103 | 55 | 13.8928 | 3.6 | 8.7 | 0 | 13.48
57 | 104 | 55 | 13.9104 | 3.6 | 8.8 | 0 | 13.48
57 | 105 | 55 | 13.928 | 3.6 | 8.9 | 0 | 13.48
57 | 106 | 55 | 13.9456 | 3.6 | 9 | 0 | 13.48
57 | 107 | 55 | 13.9632 | 3.6 | 9.1 | 0 | 13.48
57 | 108 | 55 | 13.9808 | 3.6 | 9.2 | 0 | 13.48
57 | 109 | 55 | 13.9984 | 3.6 | 9.3 | 0 | 13.48
57 | 110 | 55 | 14.016 | 3.6 | 9.4 | 0 | 13.48
57 | 111 | 55 | 14.0336 | 3.6 | 9.5 | 0 | 13.48
57 | 112 | 55 | 14.0512 | 3.6 | 9.6 | 0 | 13.48
57 | 113 | 55 | 14.0688 | 3.6 | 9.7 | 0 | 13.48
57 | 114 | 55 | 14.0864 | 3.6 | 9.8 | 0 | 13.48
57 | 115 | 55 | 14.104 | 3.6 | 9.9 | 0 | 13.48
57 | 116 | 55 | 14.1216 | 3.6 | 10 | 0 | 13.48
57 | 117 | 55 | 14.1392 | 3.7 | 3 | 0 | 13.51
57 | 118 | 55 | 14.1568 | 3.7 | 3.1 | 0 | 13.51
57 | 119 | 55 | 14.1744 | 3.7 | 3.2 | 0 | 13.51
57 | 120 | 55 | 14.192 | 3.7 | 3.3 | 0 | 13.51
57 | 121 | 55 | 14.2096 | 3.7 | 3.4 | 0 | 13.51
57 | 122 | 55 | 14.2272 | 3.7 | 3.5 | 0 | 13.51
57 | 123 | 55 | 14.2448 | 3.7 | 3.6 | 0 | 13.51
57 | 124 | 55 | 14.2624 | 3.7 | 3.7 | 0 | 13.51
57 | 125 | 55 | 14.28 | 3.7 | 3.8 | 0 | 13.51
57 | 126 | 55 | 14.3304 | 3.7 | 3.9 | 0 | 13.51
57 | 127 | 55 | 14.3808 | 3.7 | 4 | 0 | 13.51
57 | 128 | 55 | 14.4312 | 3.7 | 4.1 | 0 | 13.51
57 | 129 | 55 | 14.4816 | 3.7 | 4.2 | 0 | 13.51
57 | 130 | 55 | 14.532 | 3.7 | 4.3 | 0 | 13.51
57 | 131 | 55 | 14.5824 | 3.7 | 4.4 | 0 | 13.51
57 | 132 | 55 | 14.6328 | 3.7 | 4.5 | 0 | 13.51
57 | 133 | 55 | 14.6832 | 3.7 | 4.6 | 0 | 13.51
57 | 134 | 55 | 14.7336 | 3.7 | 4.7 | 0 | 13.51
57 | 135 | 55 | 14.784 | 3.7 | 4.8 | 0 | 13.51
57 | 136 | 55 | 14.8344 | 3.7 | 4.9 | 0 | 13.51
57 | 137 | 55 | 14.8848 | 3.7 | 5 | 0 | 13.51
57 | 138 | 55 | 14.9352 | 3.7 | 5.1 | 0 | 13.51
57 | 139 | 55 | 14.9856 | 3.7 | 5.2 | 0 | 13.51
57 | 140 | 55 | 15.036 | 3.7 | 5.3 | 0 | 13.51
57 | 141 | 55 | 15.0864 | 3.7 | 5.4 | 0 | 13.51
57 | 142 | 55 | 15.1368 | 3.7 | 5.5 | 0 | 13.51
57 | 143 | 55 | 15.1872 | 3.7 | 5.6 | 0 | 13.51
57 | 144 | 55 | 15.2376 | 3.7 | 5.7 | 0 | 13.51
57 | 145 | 55 | 15.288 | 3.7 | 5.8 | 0 | 13.51
57 | 146 | 55 | 15.3384 | 3.7 | 5.9 | 0 | 13.51
57 | 147 | 55 | 15.3888 | 3.7 | 6 | 0 | 13.51
57 | 148 | 55 | 15.4392 | 3.7 | 6.1 | 0 | 13.51
57 | 149 | 55 | 15.4896 | 3.7 | 6.2 | 0 | 13.51
57 | 150 | 55 | 15.54 | 3.7 | 6.3 | 0 | 13.51
58 | 45 | 55 | 10.1733 | 3.7 | 6.4 | 0 | 13.51
58 | 46 | 55 | 10.2371 | 3.7 | 6.5 | 0 | 13.51
58 | 47 | 55 | 10.3009 | 3.7 | 6.6 | 0 | 13.51
58 | 48 | 55 | 10.3647 | 3.7 | 6.7 | 0 | 13.51
58 | 49 | 55 | 10.4284 | 3.7 | 6.8 | 0 | 13.51
58 | 50 | 55 | 10.4922 | 3.7 | 6.9 | 0 | 13.51
58 | 51 | 55 | 10.556 | 3.7 | 7 | 0 | 13.51
58 | 52 | 55 | 10.6198 | 3.7 | 7.1 | 0 | 13.51
58 | 53 | 55 | 10.6836 | 3.7 | 7.2 | 0 | 13.51
58 | 54 | 55 | 10.7473 | 3.7 | 7.3 | 0 | 13.51
58 | 55 | 55 | 10.8111 | 3.7 | 7.4 | 0 | 13.51
58 | 56 | 55 | 10.8749 | 3.7 | 7.5 | 0 | 13.51
58 | 57 | 55 | 10.9387 | 3.7 | 7.6 | 0 | 13.51
58 | 58 | 55 | 11.0024 | 3.7 | 7.7 | 0 | 13.51
58 | 59 | 55 | 11.0662 | 3.7 | 7.8 | 0 | 13.51
58 | 60 | 55 | 11.13 | 3.7 | 7.9 | 0 | 13.51
58 | 61 | 55 | 11.1938 | 3.7 | 8 | 0 | 13.51
58 | 62 | 55 | 11.2576 | 3.7 | 8.1 | 0 | 13.51
58 | 63 | 55 | 11.3213 | 3.7 | 8.2 | 0 | 13.51
58 | 64 | 55 | 11.3851 | 3.7 | 8.3 | 0 | 13.51
58 | 65 | 55 | 11.4489 | 3.7 | 8.4 | 0 | 13.51
58 | 66 | 55 | 11.5127 | 3.7 | 8.5 | 0 | 13.51
58 | 67 | 55 | 11.5764 | 3.7 | 8.6 | 0 | 13.51
58 | 68 | 55 | 11.6402 | 3.7 | 8.7 | 0 | 13.51
58 | 69 | 55 | 11.704 | 3.7 | 8.8 | 0 | 13.51
58 | 70 | 55 | 11.7678 | 3.7 | 8.9 | 0 | 13.51
58 | 71 | 55 | 11.8316 | 3.7 | 9 | 0 | 13.51
58 | 72 | 55 | 11.8953 | 3.7 | 9.1 | 0 | 13.51
58 | 73 | 55 | 11.9591 | 3.7 | 9.2 | 0 | 13.51
58 | 74 | 55 | 12.0229 | 3.7 | 9.3 | 0 | 13.51
58 | 75 | 55 | 12.0867 | 3.7 | 9.4 | 0 | 13.51
58 | 76 | 55 | 12.1589 | 3.7 | 9.5 | 0 | 13.51
58 | 77 | 55 | 12.2312 | 3.7 | 9.6 | 0 | 13.51
58 | 78 | 55 | 12.3035 | 3.7 | 9.7 | 0 | 13.51
58 | 79 | 55 | 12.3757 | 3.7 | 9.8 | 0 | 13.51
58 | 80 | 55 | 12.448 | 3.7 | 9.9 | 0 | 13.51
58 | 81 | 55 | 12.5203 | 3.7 | 10 | 0 | 13.51
58 | 82 | 55 | 12.5925 | 3.8 | 3 | 0 | 13.54
58 | 83 | 55 | 12.6648 | 3.8 | 3.1 | 0 | 13.54
58 | 84 | 55 | 12.7371 | 3.8 | 3.2 | 0 | 13.54
58 | 85 | 55 | 12.8093 | 3.8 | 3.3 | 0 | 13.54
58 | 86 | 55 | 12.8816 | 3.8 | 3.4 | 0 | 13.54
58 | 87 | 55 | 12.9539 | 3.8 | 3.5 | 0 | 13.54
58 | 88 | 55 | 13.0261 | 3.8 | 3.6 | 0 | 13.54
58 | 89 | 55 | 13.0984 | 3.8 | 3.7 | 0 | 13.54
58 | 90 | 55 | 13.1707 | 3.8 | 3.8 | 0 | 13.54
58 | 91 | 55 | 13.2429 | 3.8 | 3.9 | 0 | 13.54
58 | 92 | 55 | 13.3152 | 3.8 | 4 | 0 | 13.54
58 | 93 | 55 | 13.3875 | 3.8 | 4.1 | 0 | 13.54
58 | 94 | 55 | 13.4597 | 3.8 | 4.2 | 0 | 13.54
58 | 95 | 55 | 13.532 | 3.8 | 4.3 | 0 | 13.54
58 | 96 | 55 | 13.6043 | 3.8 | 4.4 | 0 | 13.54
58 | 97 | 55 | 13.6765 | 3.8 | 4.5 | 0 | 13.54
58 | 98 | 55 | 13.7488 | 3.8 | 4.6 | 0 | 13.54
58 | 99 | 55 | 13.8211 | 3.8 | 4.7 | 0 | 13.54
58 | 100 | 55 | 13.8933 | 3.8 | 4.8 | 0 | 13.54
58 | 101 | 55 | 13.9091 | 3.8 | 4.9 | 0 | 13.54
58 | 102 | 55 | 13.9248 | 3.8 | 5 | 0 | 13.54
58 | 103 | 55 | 13.9405 | 3.8 | 5.1 | 0 | 13.54
58 | 104 | 55 | 13.9563 | 3.8 | 5.2 | 0 | 13.54
58 | 105 | 55 | 13.972 | 3.8 | 5.3 | 0 | 13.54
58 | 106 | 55 | 13.9877 | 3.8 | 5.4 | 0 | 13.54
58 | 107 | 55 | 14.0035 | 3.8 | 5.5 | 0 | 13.54
58 | 108 | 55 | 14.0192 | 3.8 | 5.6 | 0 | 13.54
58 | 109 | 55 | 14.0349 | 3.8 | 5.7 | 0 | 13.54
58 | 110 | 55 | 14.0507 | 3.8 | 5.8 | 0 | 13.54
58 | 111 | 55 | 14.0664 | 3.8 | 5.9 | 0 | 13.54
58 | 112 | 55 | 14.0821 | 3.8 | 6 | 0 | 13.54
58 | 113 | 55 | 14.0979 | 3.8 | 6.1 | 0 | 13.54
58 | 114 | 55 | 14.1136 | 3.8 | 6.2 | 0 | 13.54
58 | 115 | 55 | 14.1293 | 3.8 | 6.3 | 0 | 13.54
58 | 116 | 55 | 14.1451 | 3.8 | 6.4 | 0 | 13.54
58 | 117 | 55 | 14.1608 | 3.8 | 6.5 | 0 | 13.54
58 | 118 | 55 | 14.1765 | 3.8 | 6.6 | 0 | 13.54
58 | 119 | 55 | 14.1923 | 3.8 | 6.7 | 0 | 13.54
58 | 120 | 55 | 14.208 | 3.8 | 6.8 | 0 | 13.54
58 | 121 | 55 | 14.2237 | 3.8 | 6.9 | 0 | 13.54
58 | 122 | 55 | 14.2395 | 3.8 | 7 | 0 | 13.54
58 | 123 | 55 | 14.2552 | 3.8 | 7.1 | 0 | 13.54
58 | 124 | 55 | 14.2709 | 3.8 | 7.2 | 0 | 13.54
58 | 125 | 55 | 14.2867 | 3.8 | 7.3 | 0 | 13.54
58 | 126 | 55 | 14.3376 | 3.8 | 7.4 | 0 | 13.54
58 | 127 | 55 | 14.3885 | 3.8 | 7.5 | 0 | 13.54
58 | 128 | 55 | 14.4395 | 3.8 | 7.6 | 0 | 13.54
58 | 129 | 55 | 14.4904 | 3.8 | 7.7 | 0 | 13.54
58 | 130 | 55 | 14.5413 | 3.8 | 7.8 | 0 | 13.54
58 | 131 | 55 | 14.5923 | 3.8 | 7.9 | 0 | 13.54
58 | 132 | 55 | 14.6432 | 3.8 | 8 | 0 | 13.54
58 | 133 | 55 | 14.6941 | 3.8 | 8.1 | 0 | 13.54
58 | 134 | 55 | 14.7451 | 3.8 | 8.2 | 0 | 13.54
58 | 135 | 55 | 14.796 | 3.8 | 8.3 | 0 | 13.54
58 | 136 | 55 | 14.8469 | 3.8 | 8.4 | 0 | 13.54
58 | 137 | 55 | 14.8979 | 3.8 | 8.5 | 0 | 13.54
58 | 138 | 55 | 14.9488 | 3.8 | 8.6 | 0 | 13.54
58 | 139 | 55 | 14.9997 | 3.8 | 8.7 | 0 | 13.54
58 | 140 | 55 | 15.0507 | 3.8 | 8.8 | 0 | 13.54
58 | 141 | 55 | 15.1016 | 3.8 | 8.9 | 0 | 13.54
58 | 142 | 55 | 15.1525 | 3.8 | 9 | 0 | 13.54
58 | 143 | 55 | 15.2035 | 3.8 | 9.1 | 0 | 13.54
58 | 144 | 55 | 15.2544 | 3.8 | 9.2 | 0 | 13.54
58 | 145 | 55 | 15.3053 | 3.8 | 9.3 | 0 | 13.54
58 | 146 | 55 | 15.3563 | 3.8 | 9.4 | 0 | 13.54
58 | 147 | 55 | 15.4072 | 3.8 | 9.5 | 0 | 13.54
58 | 148 | 55 | 15.4581 | 3.8 | 9.6 | 0 | 13.54
58 | 149 | 55 | 15.5091 | 3.8 | 9.7 | 0 | 13.54
58 | 150 | 55 | 15.56 | 3.8 | 9.8 | 0 | 13.54
59 | 45 | 55 | 10.1867 | 3.8 | 9.9 | 0 | 13.54
59 | 46 | 55 | 10.2502 | 3.8 | 10 | 0 | 13.54
59 | 47 | 55 | 10.3138 | 3.9 | 3 | 0 | 13.57
59 | 48 | 55 | 10.3773 | 3.9 | 3.1 | 0 | 13.57
59 | 49 | 55 | 10.4409 | 3.9 | 3.2 | 0 | 13.57
59 | 50 | 55 | 10.5044 | 3.9 | 3.3 | 0 | 13.57
59 | 51 | 55 | 10.568 | 3.9 | 3.4 | 0 | 13.57
59 | 52 | 55 | 10.6316 | 3.9 | 3.5 | 0 | 13.57
59 | 53 | 55 | 10.6951 | 3.9 | 3.6 | 0 | 13.57
59 | 54 | 55 | 10.7587 | 3.9 | 3.7 | 0 | 13.57
59 | 55 | 55 | 10.8222 | 3.9 | 3.8 | 0 | 13.57
59 | 56 | 55 | 10.8858 | 3.9 | 3.9 | 0 | 13.57
59 | 57 | 55 | 10.9493 | 3.9 | 4 | 0 | 13.57
59 | 58 | 55 | 11.0129 | 3.9 | 4.1 | 0 | 13.57
59 | 59 | 55 | 11.0764 | 3.9 | 4.2 | 0 | 13.57
59 | 60 | 55 | 11.14 | 3.9 | 4.3 | 0 | 13.57
59 | 61 | 55 | 11.2036 | 3.9 | 4.4 | 0 | 13.57
59 | 62 | 55 | 11.2671 | 3.9 | 4.5 | 0 | 13.57
59 | 63 | 55 | 11.3307 | 3.9 | 4.6 | 0 | 13.57
59 | 64 | 55 | 11.3942 | 3.9 | 4.7 | 0 | 13.57
59 | 65 | 55 | 11.4578 | 3.9 | 4.8 | 0 | 13.57
59 | 66 | 55 | 11.5213 | 3.9 | 4.9 | 0 | 13.57
59 | 67 | 55 | 11.5849 | 3.9 | 5 | 0 | 13.57
59 | 68 | 55 | 11.6484 | 3.9 | 5.1 | 0 | 13.57
59 | 69 | 55 | 11.712 | 3.9 | 5.2 | 0 | 13.57
59 | 70 | 55 | 11.7756 | 3.9 | 5.3 | 0 | 13.57
59 | 71 | 55 | 11.8391 | 3.9 | 5.4 | 0 | 13.57
59 | 72 | 55 | 11.9027 | 3.9 | 5.5 | 0 | 13.57
59 | 73 | 55 | 11.9662 | 3.9 | 5.6 | 0 | 13.57
59 | 74 | 55 | 12.0298 | 3.9 | 5.7 | 0 | 13.57
59 | 75 | 55 | 12.0933 | 3.9 | 5.8 | 0 | 13.57
59 | 76 | 55 | 12.1675 | 3.9 | 5.9 | 0 | 13.57
59 | 77 | 55 | 12.2416 | 3.9 | 6 | 0 | 13.57
59 | 78 | 55 | 12.3157 | 3.9 | 6.1 | 0 | 13.57
59 | 79 | 55 | 12.3899 | 3.9 | 6.2 | 0 | 13.57
59 | 80 | 55 | 12.464 | 3.9 | 6.3 | 0 | 13.57
59 | 81 | 55 | 12.5381 | 3.9 | 6.4 | 0 | 13.57
59 | 82 | 55 | 12.6123 | 3.9 | 6.5 | 0 | 13.57
59 | 83 | 55 | 12.6864 | 3.9 | 6.6 | 0 | 13.57
59 | 84 | 55 | 12.7605 | 3.9 | 6.7 | 0 | 13.57
59 | 85 | 55 | 12.8347 | 3.9 | 6.8 | 0 | 13.57
59 | 86 | 55 | 12.9088 | 3.9 | 6.9 | 0 | 13.57
59 | 87 | 55 | 12.9829 | 3.9 | 7 | 0 | 13.57
59 | 88 | 55 | 13.0571 | 3.9 | 7.1 | 0 | 13.57
59 | 89 | 55 | 13.1312 | 3.9 | 7.2 | 0 | 13.57
59 | 90 | 55 | 13.2053 | 3.9 | 7.3 | 0 | 13.57
59 | 91 | 55 | 13.2795 | 3.9 | 7.4 | 0 | 13.57
59 | 92 | 55 | 13.3536 | 3.9 | 7.5 | 0 | 13.57
59 | 93 | 55 | 13.4277 | 3.9 | 7.6 | 0 | 13.57
59 | 94 | 55 | 13.5019 | 3.9 | 7.7 | 0 | 13.57
59 | 95 | 55 | 13.576 | 3.9 | 7.8 | 0 | 13.57
59 | 96 | 55 | 13.6501 | 3.9 | 7.9 | 0 | 13.57
59 | 97 | 55 | 13.7243 | 3.9 | 8 | 0 | 13.57
59 | 98 | 55 | 13.7984 | 3.9 | 8.1 | 0 | 13.57
59 | 99 | 55 | 13.8725 | 3.9 | 8.2 | 0 | 13.57
59 | 100 | 55 | 13.9467 | 3.9 | 8.3 | 0 | 13.57
59 | 101 | 55 | 13.9605 | 3.9 | 8.4 | 0 | 13.57
59 | 102 | 55 | 13.9744 | 3.9 | 8.5 | 0 | 13.57
59 | 103 | 55 | 13.9883 | 3.9 | 8.6 | 0 | 13.57
59 | 104 | 55 | 14.0021 | 3.9 | 8.7 | 0 | 13.57
59 | 105 | 55 | 14.016 | 3.9 | 8.8 | 0 | 13.57
59 | 106 | 55 | 14.0299 | 3.9 | 8.9 | 0 | 13.57
59 | 107 | 55 | 14.0437 | 3.9 | 9 | 0 | 13.57
59 | 108 | 55 | 14.0576 | 3.9 | 9.1 | 0 | 13.57
59 | 109 | 55 | 14.0715 | 3.9 | 9.2 | 0 | 13.57
59 | 110 | 55 | 14.0853 | 3.9 | 9.3 | 0 | 13.57
59 | 111 | 55 | 14.0992 | 3.9 | 9.4 | 0 | 13.57
59 | 112 | 55 | 14.1131 | 3.9 | 9.5 | 0 | 13.57
59 | 113 | 55 | 14.1269 | 3.9 | 9.6 | 0 | 13.57
59 | 114 | 55 | 14.1408 | 3.9 | 9.7 | 0 | 13.57
59 | 115 | 55 | 14.1547 | 3.9 | 9.8 | 0 | 13.57
59 | 116 | 55 | 14.1685 | 3.9 | 9.9 | 0 | 13.57
59 | 117 | 55 | 14.1824 | 3.9 | 10 | 0 | 13.57
59 | 118 | 55 | 14.1963 | 4 | 3 | 0 | 13.6
59 | 119 | 55 | 14.2101 | 4 | 3.1 | 0 | 13.6
59 | 120 | 55 | 14.224 | 4 | 3.2 | 0 | 13.6
59 | 121 | 55 | 14.2379 | 4 | 3.3 | 0 | 13.6
59 | 122 | 55 | 14.2517 | 4 | 3.4 | 0 | 13.6
59 | 123 | 55 | 14.2656 | 4 | 3.5 | 0 | 13.6
59 | 124 | 55 | 14.2795 | 4 | 3.6 | 0 | 13.6
59 | 125 | 55 | 14.2933 | 4 | 3.7 | 0 | 13.6
59 | 126 | 55 | 14.3448 | 4 | 3.8 | 0 | 13.6
59 | 127 | 55 | 14.3963 | 4 | 3.9 | 0 | 13.6
59 | 128 | 55 | 14.4477 | 4 | 4 | 0 | 13.6
59 | 129 | 55 | 14.4992 | 4 | 4.1 | 0 | 13.6
59 | 130 | 55 | 14.5507 | 4 | 4.2 | 0 | 13.6
59 | 131 | 55 | 14.6021 | 4 | 4.3 | 0 | 13.6
59 | 132 | 55 | 14.6536 | 4 | 4.4 | 0 | 13.6
59 | 133 | 55 | 14.7051 | 4 | 4.5 | 0 | 13.6
59 | 134 | 55 | 14.7565 | 4 | 4.6 | 0 | 13.6
59 | 135 | 55 | 14.808 | 4 | 4.7 | 0 | 13.6
59 | 136 | 55 | 14.8595 | 4 | 4.8 | 0 | 13.6
59 | 137 | 55 | 14.9109 | 4 | 4.9 | 0 | 13.6
59 | 138 | 55 | 14.9624 | 4 | 5 | 0 | 13.6
59 | 139 | 55 | 15.0139 | 4 | 5.1 | 0 | 13.6
59 | 140 | 55 | 15.0653 | 4 | 5.2 | 0 | 13.6
59 | 141 | 55 | 15.1168 | 4 | 5.3 | 0 | 13.6
59 | 142 | 55 | 15.1683 | 4 | 5.4 | 0 | 13.6
59 | 143 | 55 | 15.2197 | 4 | 5.5 | 0 | 13.6
59 | 144 | 55 | 15.2712 | 4 | 5.6 | 0 | 13.6
59 | 145 | 55 | 15.3227 | 4 | 5.7 | 0 | 13.6
59 | 146 | 55 | 15.3741 | 4 | 5.8 | 0 | 13.6
59 | 147 | 55 | 15.4256 | 4 | 5.9 | 0 | 13.6
59 | 148 | 55 | 15.4771 | 4 | 6 | 0 | 13.6
59 | 149 | 55 | 15.5285 | 4 | 6.1 | 0 | 13.6
59 | 150 | 55 | 15.58 | 4 | 6.2 | 0 | 13.6
60 | 45 | 55 | 10.2 | 4 | 6.3 | 0 | 13.6
60 | 46 | 55 | 10.2633 | 4 | 6.4 | 0 | 13.6
60 | 47 | 55 | 10.3267 | 4 | 6.5 | 0 | 13.6
60 | 48 | 55 | 10.39 | 4 | 6.6 | 0 | 13.6
60 | 49 | 55 | 10.4533 | 4 | 6.7 | 0 | 13.6
60 | 50 | 55 | 10.5167 | 4 | 6.8 | 0 | 13.6
60 | 51 | 55 | 10.58 | 4 | 6.9 | 0 | 13.6
60 | 52 | 55 | 10.6433 | 4 | 7 | 0 | 13.6
60 | 53 | 55 | 10.7067 | 4 | 7.1 | 0 | 13.6
60 | 54 | 55 | 10.77 | 4 | 7.2 | 0 | 13.6
60 | 55 | 55 | 10.8333 | 4 | 7.3 | 0 | 13.6
60 | 56 | 55 | 10.8967 | 4 | 7.4 | 0 | 13.6
60 | 57 | 55 | 10.96 | 4 | 7.5 | 0 | 13.6
60 | 58 | 55 | 11.0233 | 4 | 7.6 | 0 | 13.6
60 | 59 | 55 | 11.0867 | 4 | 7.7 | 0 | 13.6
60 | 60 | 55 | 11.15 | 4 | 7.8 | 0 | 13.6
60 | 61 | 55 | 11.2133 | 4 | 7.9 | 0 | 13.6
60 | 62 | 55 | 11.2767 | 4 | 8 | 0 | 13.6
60 | 63 | 55 | 11.34 | 4 | 8.1 | 0 | 13.6
60 | 64 | 55 | 11.4033 | 4 | 8.2 | 0 | 13.6
60 | 65 | 55 | 11.4667 | 4 | 8.3 | 0 | 13.6
60 | 66 | 55 | 11.53 | 4 | 8.4 | 0 | 13.6
60 | 67 | 55 | 11.5933 | 4 | 8.5 | 0 | 13.6
60 | 68 | 55 | 11.6567 | 4 | 8.6 | 0 | 13.6
60 | 69 | 55 | 11.72 | 4 | 8.7 | 0 | 13.6
60 | 70 | 55 | 11.7833 | 4 | 8.8 | 0 | 13.6
60 | 71 | 55 | 11.8467 | 4 | 8.9 | 0 | 13.6
60 | 72 | 55 | 11.91 | 4 | 9 | 0 | 13.6
60 | 73 | 55 | 11.9733 | 4 | 9.1 | 0 | 13.6
60 | 74 | 55 | 12.0367 | 4 | 9.2 | 0 | 13.6
60 | 75 | 55 | 12.1 | 4 | 9.3 | 0 | 13.6
60 | 76 | 55 | 12.176 | 4 | 9.4 | 0 | 13.6
60 | 77 | 55 | 12.252 | 4 | 9.5 | 0 | 13.6
60 | 78 | 55 | 12.328 | 4 | 9.6 | 0 | 13.6
60 | 79 | 55 | 12.404 | 4 | 9.7 | 0 | 13.6
60 | 80 | 55 | 12.48 | 4 | 9.8 | 0 | 13.6
60 | 81 | 55 | 12.556 | 4 | 9.9 | 0 | 13.6
60 | 82 | 55 | 12.632 | 4 | 10 | 0 | 13.6
60 | 83 | 55 | 12.708 | 4.1 | 3 | 0 | 13.62
60 | 84 | 55 | 12.784 | 4.1 | 3.1 | 0 | 13.62
60 | 85 | 55 | 12.86 | 4.1 | 3.2 | 0 | 13.62
60 | 86 | 55 | 12.936 | 4.1 | 3.3 | 0 | 13.62
60 | 87 | 55 | 13.012 | 4.1 | 3.4 | 0 | 13.62
60 | 88 | 55 | 13.088 | 4.1 | 3.5 | 0 | 13.62
60 | 89 | 55 | 13.164 | 4.1 | 3.6 | 0 | 13.62
60 | 90 | 55 | 13.24 | 4.1 | 3.7 | 0 | 13.62
60 | 91 | 55 | 13.316 | 4.1 | 3.8 | 0 | 13.62
60 | 92 | 55 | 13.392 | 4.1 | 3.9 | 0 | 13.62
60 | 93 | 55 | 13.468 | 4.1 | 4 | 0 | 13.62
60 | 94 | 55 | 13.544 | 4.1 | 4.1 | 0 | 13.62
60 | 95 | 55 | 13.62 | 4.1 | 4.2 | 0 | 13.62
60 | 96 | 55 | 13.696 | 4.1 | 4.3 | 0 | 13.62
60 | 97 | 55 | 13.772 | 4.1 | 4.4 | 0 | 13.62
60 | 98 | 55 | 13.848 | 4.1 | 4.5 | 0 | 13.62
60 | 99 | 55 | 13.924 | 4.1 | 4.6 | 0 | 13.62
60 | 100 | 55 | 14 | 4.1 | 4.7 | 0 | 13.62
60 | 101 | 55 | 14.012 | 4.1 | 4.8 | 0 | 13.62
60 | 102 | 55 | 14.024 | 4.1 | 4.9 | 0 | 13.62
60 | 103 | 55 | 14.036 | 4.1 | 5 | 0 | 13.62
60 | 104 | 55 | 14.048 | 4.1 | 5.1 | 0 | 13.62
60 | 105 | 55 | 14.06 | 4.1 | 5.2 | 0 | 13.62
60 | 106 | 55 | 14.072 | 4.1 | 5.3 | 0 | 13.62
60 | 107 | 55 | 14.084 | 4.1 | 5.4 | 0 | 13.62
60 | 108 | 55 | 14.096 | 4.1 | 5.5 | 0 | 13.62
60 | 109 | 55 | 14.108 | 4.1 | 5.6 | 0 | 13.62
60 | 110 | 55 | 14.12 | 4.1 | 5.7 | 0 | 13.62
60 | 111 | 55 | 14.132 | 4.1 | 5.8 | 0 | 13.62
60 | 112 | 55 | 14.144 | 4.1 | 5.9 | 0 | 13.62
60 | 113 | 55 | 14.156 | 4.1 | 6 | 0 | 13.62
60 | 114 | 55 | 14.168 | 4.1 | 6.1 | 0 | 13.62
60 | 115 | 55 | 14.18 | 4.1 | 6.2 | 0 | 13.62
60 | 116 | 55 | 14.192 | 4.1 | 6.3 | 0 | 13.62
60 | 117 | 55 | 14.204 | 4.1 | 6.4 | 0 | 13.62
60 | 118 | 55 | 14.216 | 4.1 | 6.5 | 0 | 13.62
60 | 119 | 55 | 14.228 | 4.1 | 6.6 | 0 | 13.62
60 | 120 | 55 | 14.24 | 4.1 | 6.7 | 0 | 13.62
60 | 121 | 55 | 14.252 | 4.1 | 6.8 | 0 | 13.62
60 | 122 | 55 | 14.264 | 4.1 | 6.9 | 0 | 13.62
60 | 123 | 55 | 14.276 | 4.1 | 7 | 0 | 13.62
60 | 124 | 55 | 14.288 | 4.1 | 7.1 | 0 | 13.62
60 | 125 | 55 | 14.3 | 4.1 | 7.2 | 0 | 13.62
60 | 126 | 55 | 14.352 | 4.1 | 7.3 | 0 | 13.62
60 | 127 | 55 | 14.404 | 4.1 | 7.4 | 0 | 13.62
60 | 128 | 55 | 14.456 | 4.1 | 7.5 | 0 | 13.62
60 | 129 | 55 | 14.508 | 4.1 | 7.6 | 0 | 13.62
60 | 130 | 55 | 14.56 | 4.1 | 7.7 | 0 | 13.62
60 | 131 | 55 | 14.612 | 4.1 | 7.8 | 0 | 13.62
60 | 132 | 55 | 14.664 | 4.1 | 7.9 | 0 | 13.62
60 | 133 | 55 | 14.716 | 4.1 | 8 | 0 | 13.62
60 | 134 | 55 | 14.768 | 4.1 | 8.1 | 0 | 13.62
60 | 135 | 55 | 14.82 | 4.1 | 8.2 | 0 | 13.62
60 | 136 | 55 | 14.872 | 4.1 | 8.3 | 0 | 13.62
60 | 137 | 55 | 14.924 | 4.1 | 8.4 | 0 | 13.62
60 | 138 | 55 | 14.976 | 4.1 | 8.5 | 0 | 13.62
60 | 139 | 55 | 15.028 | 4.1 | 8.6 | 0 | 13.62
60 | 140 | 55 | 15.08 | 4.1 | 8.7 | 0 | 13.62
60 | 141 | 55 | 15.132 | 4.1 | 8.8 | 0 | 13.62
60 | 142 | 55 | 15.184 | 4.1 | 8.9 | 0 | 13.62
60 | 143 | 55 | 15.236 | 4.1 | 9 | 0 | 13.62
60 | 144 | 55 | 15.288 | 4.1 | 9.1 | 0 | 13.62
60 | 145 | 55 | 15.34 | 4.1 | 9.2 | 0 | 13.62
60 | 146 | 55 | 15.392 | 4.1 | 9.3 | 0 | 13.62
60 | 147 | 55 | 15.444 | 4.1 | 9.4 | 0 | 13.62
60 | 148 | 55 | 15.496 | 4.1 | 9.5 | 0 | 13.62
60 | 149 | 55 | 15.548 | 4.1 | 9.6 | 0 | 13.62
60 | 150 | 55 | 15.6 | 4.1 | 9.7 | 0 | 13.62
61 | 45 | 55 | 10.2067 | 4.1 | 9.8 | 0 | 13.62
61 | 46 | 55 | 10.2702 | 4.1 | 9.9 | 0 | 13.62
61 | 47 | 55 | 10.3338 | 4.1 | 10 | 0 | 13.62
61 | 48 | 55 | 10.3973 | 4.2 | 3 | 0 | 13.64
61 | 49 | 55 | 10.4609 | 4.2 | 3.1 | 0 | 13.64
61 | 50 | 55 | 10.5244 | 4.2 | 3.2 | 0 | 13.64
61 | 51 | 55 | 10.588 | 4.2 | 3.3 | 0 | 13.64
61 | 52 | 55 | 10.6516 | 4.2 | 3.4 | 0 | 13.64
61 | 53 | 55 | 10.7151 | 4.2 | 3.5 | 0 | 13.64
61 | 54 | 55 | 10.7787 | 4.2 | 3.6 | 0 | 13.64
61 | 55 | 55 | 10.8422 | 4.2 | 3.7 | 0 | 13.64
61 | 56 | 55 | 10.9058 | 4.2 | 3.8 | 0 | 13.64
61 | 57 | 55 | 10.9693 | 4.2 | 3.9 | 0 | 13.64
61 | 58 | 55 | 11.0329 | 4.2 | 4 | 0 | 13.64
61 | 59 | 55 | 11.0964 | 4.2 | 4.1 | 0 | 13.64
61 | 60 | 55 | 11.16 | 4.2 | 4.2 | 0 | 13.64
61 | 61 | 55 | 11.2236 | 4.2 | 4.3 | 0 | 13.64
61 | 62 | 55 | 11.2871 | 4.2 | 4.4 | 0 | 13.64
61 | 63 | 55 | 11.3507 | 4.2 | 4.5 | 0 | 13.64
61 | 64 | 55 | 11.4142 | 4.2 | 4.6 | 0 | 13.64
61 | 65 | 55 | 11.4778 | 4.2 | 4.7 | 0 | 13.64
61 | 66 | 55 | 11.5413 | 4.2 | 4.8 | 0 | 13.64
61 | 67 | 55 | 11.6049 | 4.2 | 4.9 | 0 | 13.64
61 | 68 | 55 | 11.6684 | 4.2 | 5 | 0 | 13.64
61 | 69 | 55 | 11.732 | 4.2 | 5.1 | 0 | 13.64
61 | 70 | 55 | 11.7956 | 4.2 | 5.2 | 0 | 13.64
61 | 71 | 55 | 11.8591 | 4.2 | 5.3 | 0 | 13.64
61 | 72 | 55 | 11.9227 | 4.2 | 5.4 | 0 | 13.64
61 | 73 | 55 | 11.9862 | 4.2 | 5.5 | 0 | 13.64
61 | 74 | 55 | 12.0498 | 4.2 | 5.6 | 0 | 13.64
61 | 75 | 55 | 12.1133 | 4.2 | 5.7 | 0 | 13.64
61 | 76 | 55 | 12.1893 | 4.2 | 5.8 | 0 | 13.64
61 | 77 | 55 | 12.2653 | 4.2 | 5.9 | 0 | 13.64
61 | 78 | 55 | 12.3413 | 4.2 | 6 | 0 | 13.64
61 | 79 | 55 | 12.4173 | 4.2 | 6.1 | 0 | 13.64
61 | 80 | 55 | 12.4933 | 4.2 | 6.2 | 0 | 13.64
61 | 81 | 55 | 12.5693 | 4.2 | 6.3 | 0 | 13.64
61 | 82 | 55 | 12.6453 | 4.2 | 6.4 | 0 | 13.64
61 | 83 | 55 | 12.7213 | 4.2 | 6.5 | 0 | 13.64
61 | 84 | 55 | 12.7973 | 4.2 | 6.6 | 0 | 13.64
61 | 85 | 55 | 12.8733 | 4.2 | 6.7 | 0 | 13.64
61 | 86 | 55 | 12.9493 | 4.2 | 6.8 | 0 | 13.64
61 | 87 | 55 | 13.0253 | 4.2 | 6.9 | 0 | 13.64
61 | 88 | 55 | 13.1013 | 4.2 | 7 | 0 | 13.64
61 | 89 | 55 | 13.1773 | 4.2 | 7.1 | 0 | 13.64
61 | 90 | 55 | 13.2533 | 4.2 | 7.2 | 0 | 13.64
61 | 91 | 55 | 13.3293 | 4.2 | 7.3 | 0 | 13.64
61 | 92 | 55 | 13.4053 | 4.2 | 7.4 | 0 | 13.64
61 | 93 | 55 | 13.4813 | 4.2 | 7.5 | 0 | 13.64
61 | 94 | 55 | 13.5573 | 4.2 | 7.6 | 0 | 13.64
61 | 95 | 55 | 13.6333 | 4.2 | 7.7 | 0 | 13.64
61 | 96 | 55 | 13.7093 | 4.2 | 7.8 | 0 | 13.64
61 | 97 | 55 | 13.7853 | 4.2 | 7.9 | 0 | 13.64
61 | 98 | 55 | 13.8613 | 4.2 | 8 | 0 | 13.64
61 | 99 | 55 | 13.9373 | 4.2 | 8.1 | 0 | 13.64
61 | 100 | 55 | 14.0133 | 4.2 | 8.2 | 0 | 13.64
61 | 101 | 55 | 14.0253 | 4.2 | 8.3 | 0 | 13.64
61 | 102 | 55 | 14.0373 | 4.2 | 8.4 | 0 | 13.64
61 | 103 | 55 | 14.0493 | 4.2 | 8.5 | 0 | 13.64
61 | 104 | 55 | 14.0613 | 4.2 | 8.6 | 0 | 13.64
61 | 105 | 55 | 14.0733 | 4.2 | 8.7 | 0 | 13.64
61 | 106 | 55 | 14.0853 | 4.2 | 8.8 | 0 | 13.64
61 | 107 | 55 | 14.0973 | 4.2 | 8.9 | 0 | 13.64
61 | 108 | 55 | 14.1093 | 4.2 | 9 | 0 | 13.64
61 | 109 | 55 | 14.1213 | 4.2 | 9.1 | 0 | 13.64
61 | 110 | 55 | 14.1333 | 4.2 | 9.2 | 0 | 13.64
61 | 111 | 55 | 14.1453 | 4.2 | 9.3 | 0 | 13.64
61 | 112 | 55 | 14.1573 | 4.2 | 9.4 | 0 | 13.64
61 | 113 | 55 | 14.1693 | 4.2 | 9.5 | 0 | 13.64
61 | 114 | 55 | 14.1813 | 4.2 | 9.6 | 0 | 13.64
61 | 115 | 55 | 14.1933 | 4.2 | 9.7 | 0 | 13.64
61 | 116 | 55 | 14.2053 | 4.2 | 9.8 | 0 | 13.64
61 | 117 | 55 | 14.2173 | 4.2 | 9.9 | 0 | 13.64
61 | 118 | 55 | 14.2293 | 4.2 | 10 | 0 | 13.64
61 | 119 | 55 | 14.2413 | 4.3 | 3 | 0 | 13.66
61 | 120 | 55 | 14.2533 | 4.3 | 3.1 | 0 | 13.66
61 | 121 | 55 | 14.2653 | 4.3 | 3.2 | 0 | 13.66
61 | 122 | 55 | 14.2773 | 4.3 | 3.3 | 0 | 13.66
61 | 123 | 55 | 14.2893 | 4.3 | 3.4 | 0 | 13.66
61 | 124 | 55 | 14.3013 | 4.3 | 3.5 | 0 | 13.66
61 | 125 | 55 | 14.3133 | 4.3 | 3.6 | 0 | 13.66
61 | 126 | 55 | 14.3651 | 4.3 | 3.7 | 0 | 13.66
61 | 127 | 55 | 14.4168 | 4.3 | 3.8 | 0 | 13.66
61 | 128 | 55 | 14.4685 | 4.3 | 3.9 | 0 | 13.66
61 | 129 | 55 | 14.5203 | 4.3 | 4 | 0 | 13.66
61 | 130 | 55 | 14.572 | 4.3 | 4.1 | 0 | 13.66
61 | 131 | 55 | 14.6237 | 4.3 | 4.2 | 0 | 13.66
61 | 132 | 55 | 14.6755 | 4.3 | 4.3 | 0 | 13.66
61 | 133 | 55 | 14.7272 | 4.3 | 4.4 | 0 | 13.66
61 | 134 | 55 | 14.7789 | 4.3 | 4.5 | 0 | 13.66
61 | 135 | 55 | 14.8307 | 4.3 | 4.6 | 0 | 13.66
61 | 136 | 55 | 14.8824 | 4.3 | 4.7 | 0 | 13.66
61 | 137 | 55 | 14.9341 | 4.3 | 4.8 | 0 | 13.66
61 | 138 | 55 | 14.9859 | 4.3 | 4.9 | 0 | 13.66
61 | 139 | 55 | 15.0376 | 4.3 | 5 | 0 | 13.66
61 | 140 | 55 | 15.0893 | 4.3 | 5.1 | 0 | 13.66
61 | 141 | 55 | 15.1411 | 4.3 | 5.2 | 0 | 13.66
61 | 142 | 55 | 15.1928 | 4.3 | 5.3 | 0 | 13.66
61 | 143 | 55 | 15.2445 | 4.3 | 5.4 | 0 | 13.66
61 | 144 | 55 | 15.2963 | 4.3 | 5.5 | 0 | 13.66
61 | 145 | 55 | 15.348 | 4.3 | 5.6 | 0 | 13.66
61 | 146 | 55 | 15.3997 | 4.3 | 5.7 | 0 | 13.66
61 | 147 | 55 | 15.4515 | 4.3 | 5.8 | 0 | 13.66
61 | 148 | 55 | 15.5032 | 4.3 | 5.9 | 0 | 13.66
61 | 149 | 55 | 15.5549 | 4.3 | 6 | 0 | 13.66
61 | 150 | 55 | 15.6067 | 4.3 | 6.1 | 0 | 13.66
62 | 45 | 55 | 10.2133 | 4.3 | 6.2 | 0 | 13.66
62 | 46 | 55 | 10.2771 | 4.3 | 6.3 | 0 | 13.66
62 | 47 | 55 | 10.3409 | 4.3 | 6.4 | 0 | 13.66
62 | 48 | 55 | 10.4047 | 4.3 | 6.5 | 0 | 13.66
62 | 49 | 55 | 10.4684 | 4.3 | 6.6 | 0 | 13.66
62 | 50 | 55 | 10.5322 | 4.3 | 6.7 | 0 | 13.66
62 | 51 | 55 | 10.596 | 4.3 | 6.8 | 0 | 13.66
62 | 52 | 55 | 10.6598 | 4.3 | 6.9 | 0 | 13.66
62 | 53 | 55 | 10.7236 | 4.3 | 7 | 0 | 13.66
62 | 54 | 55 | 10.7873 | 4.3 | 7.1 | 0 | 13.66
62 | 55 | 55 | 10.8511 | 4.3 | 7.2 | 0 | 13.66
62 | 56 | 55 | 10.9149 | 4.3 | 7.3 | 0 | 13.66
62 | 57 | 55 | 10.9787 | 4.3 | 7.4 | 0 | 13.66
62 | 58 | 55 | 11.0424 | 4.3 | 7.5 | 0 | 13.66
62 | 59 | 55 | 11.1062 | 4.3 | 7.6 | 0 | 13.66
62 | 60 | 55 | 11.17 | 4.3 | 7.7 | 0 | 13.66
62 | 61 | 55 | 11.2338 | 4.3 | 7.8 | 0 | 13.66
62 | 62 | 55 | 11.2976 | 4.3 | 7.9 | 0 | 13.66
62 | 63 | 55 | 11.3613 | 4.3 | 8 | 0 | 13.66
62 | 64 | 55 | 11.4251 | 4.3 | 8.1 | 0 | 13.66
62 | 65 | 55 | 11.4889 | 4.3 | 8.2 | 0 | 13.66
62 | 66 | 55 | 11.5527 | 4.3 | 8.3 | 0 | 13.66
62 | 67 | 55 | 11.6164 | 4.3 | 8.4 | 0 | 13.66
62 | 68 | 55 | 11.6802 | 4.3 | 8.5 | 0 | 13.66
62 | 69 | 55 | 11.744 | 4.3 | 8.6 | 0 | 13.66
62 | 70 | 55 | 11.8078 | 4.3 | 8.7 | 0 | 13.66
62 | 71 | 55 | 11.8716 | 4.3 | 8.8 | 0 | 13.66
62 | 72 | 55 | 11.9353 | 4.3 | 8.9 | 0 | 13.66
62 | 73 | 55 | 11.9991 | 4.3 | 9 | 0 | 13.66
62 | 74 | 55 | 12.0629 | 4.3 | 9.1 | 0 | 13.66
62 | 75 | 55 | 12.1267 | 4.3 | 9.2 | 0 | 13.66
62 | 76 | 55 | 12.2027 | 4.3 | 9.3 | 0 | 13.66
62 | 77 | 55 | 12.2787 | 4.3 | 9.4 | 0 | 13.66
62 | 78 | 55 | 12.3547 | 4.3 | 9.5 | 0 | 13.66
62 | 79 | 55 | 12.4307 | 4.3 | 9.6 | 0 | 13.66
62 | 80 | 55 | 12.5067 | 4.3 | 9.7 | 0 | 13.66
62 | 81 | 55 | 12.5827 | 4.3 | 9.8 | 0 | 13.66
62 | 82 | 55 | 12.6587 | 4.3 | 9.9 | 0 | 13.66
62 | 83 | 55 | 12.7347 | 4.3 | 10 | 0 | 13.66
62 | 84 | 55 | 12.8107 | 4.4 | 3 | 0 | 13.68
62 | 85 | 55 | 12.8867 | 4.4 | 3.1 | 0 | 13.68
62 | 86 | 55 | 12.9627 | 4.4 | 3.2 | 0 | 13.68
62 | 87 | 55 | 13.0387 | 4.4 | 3.3 | 0 | 13.68
62 | 88 | 55 | 13.1147 | 4.4 | 3.4 | 0 | 13.68
62 | 89 | 55 | 13.1907 | 4.4 | 3.5 | 0 | 13.68
62 | 90 | 55 | 13.2667 | 4.4 | 3.6 | 0 | 13.68
62 | 91 | 55 | 13.3427 | 4.4 | 3.7 | 0 | 13.68
62 | 92 | 55 | 13.4187 | 4.4 | 3.8 | 0 | 13.68
62 | 93 | 55 | 13.4947 | 4.4 | 3.9 | 0 | 13.68
62 | 94 | 55 | 13.5707 | 4.4 | 4 | 0 | 13.68
62 | 95 | 55 | 13.6467 | 4.4 | 4.1 | 0 | 13.68
62 | 96 | 55 | 13.7227 | 4.4 | 4.2 | 0 | 13.68
62 | 97 | 55 | 13.7987 | 4.4 | 4.3 | 0 | 13.68
62 | 98 | 55 | 13.8747 | 4.4 | 4.4 | 0 | 13.68
62 | 99 | 55 | 13.9507 | 4.4 | 4.5 | 0 | 13.68
62 | 100 | 55 | 14.0267 | 4.4 | 4.6 | 0 | 13.68
62 | 101 | 55 | 14.0387 | 4.4 | 4.7 | 0 | 13.68
62 | 102 | 55 | 14.0507 | 4.4 | 4.8 | 0 | 13.68
62 | 103 | 55 | 14.0627 | 4.4 | 4.9 | 0 | 13.68
62 | 104 | 55 | 14.0747 | 4.4 | 5 | 0 | 13.68
62 | 105 | 55 | 14.0867 | 4.4 | 5.1 | 0 | 13.68
62 | 106 | 55 | 14.0987 | 4.4 | 5.2 | 0 | 13.68
62 | 107 | 55 | 14.1107 | 4.4 | 5.3 | 0 | 13.68
62 | 108 | 55 | 14.1227 | 4.4 | 5.4 | 0 | 13.68
62 | 109 | 55 | 14.1347 | 4.4 | 5.5 | 0 | 13.68
62 | 110 | 55 | 14.1467 | 4.4 | 5.6 | 0 | 13.68
62 | 111 | 55 | 14.1587 | 4.4 | 5.7 | 0 | 13.68
62 | 112 | 55 | 14.1707 | 4.4 | 5.8 | 0 | 13.68
62 | 113 | 55 | 14.1827 | 4.4 | 5.9 | 0 | 13.68
62 | 114 | 55 | 14.1947 | 4.4 | 6 | 0 | 13.68
62 | 115 | 55 | 14.2067 | 4.4 | 6.1 | 0 | 13.68
62 | 116 | 55 | 14.2187 | 4.4 | 6.2 | 0 | 13.68
62 | 117 | 55 | 14.2307 | 4.4 | 6.3 | 0 | 13.68
62 | 118 | 55 | 14.2427 | 4.4 | 6.4 | 0 | 13.68
62 | 119 | 55 | 14.2547 | 4.4 | 6.5 | 0 | 13.68
62 | 120 | 55 | 14.2667 | 4.4 | 6.6 | 0 | 13.68
62 | 121 | 55 | 14.2787 | 4.4 | 6.7 | 0 | 13.68
62 | 122 | 55 | 14.2907 | 4.4 | 6.8 | 0 | 13.68
62 | 123 | 55 | 14.3027 | 4.4 | 6.9 | 0 | 13.68
62 | 124 | 55 | 14.3147 | 4.4 | 7 | 0 | 13.68
62 | 125 | 55 | 14.3267 | 4.4 | 7.1 | 0 | 13.68
62 | 126 | 55 | 14.3781 | 4.4 | 7.2 | 0 | 13.68
62 | 127 | 55 | 14.4296 | 4.4 | 7.3 | 0 | 13.68
62 | 128 | 55 | 14.4811 | 4.4 | 7.4 | 0 | 13.68
62 | 129 | 55 | 14.5325 | 4.4 | 7.5 | 0 | 13.68
62 | 130 | 55 | 14.584 | 4.4 | 7.6 | 0 | 13.68
62 | 131 | 55 | 14.6355 | 4.4 | 7.7 | 0 | 13.68
62 | 132 | 55 | 14.6869 | 4.4 | 7.8 | 0 | 13.68
62 | 133 | 55 | 14.7384 | 4.4 | 7.9 | 0 | 13.68
62 | 134 | 55 | 14.7899 | 4.4 | 8 | 0 | 13.68
62 | 135 | 55 | 14.8413 | 4.4 | 8.1 | 0 | 13.68
62 | 136 | 55 | 14.8928 | 4.4 | 8.2 | 0 | 13.68
62 | 137 | 55 | 14.9443 | 4.4 | 8.3 | 0 | 13.68
62 | 138 | 55 | 14.9957 | 4.4 | 8.4 | 0 | 13.68
62 | 139 | 55 | 15.0472 | 4.4 | 8.5 | 0 | 13.68
62 | 140 | 55 | 15.0987 | 4.4 | 8.6 | 0 | 13.68
62 | 141 | 55 | 15.1501 | 4.4 | 8.7 | 0 | 13.68
62 | 142 | 55 | 15.2016 | 4.4 | 8.8 | 0 | 13.68
62 | 143 | 55 | 15.2531 | 4.4 | 8.9 | 0 | 13.68
62 | 144 | 55 | 15.3045 | 4.4 | 9 | 0 | 13.68
62 | 145 | 55 | 15.356 | 4.4 | 9.1 | 0 | 13.68
62 | 146 | 55 | 15.4075 | 4.4 | 9.2 | 0 | 13.68
62 | 147 | 55 | 15.4589 | 4.4 | 9.3 | 0 | 13.68
62 | 148 | 55 | 15.5104 | 4.4 | 9.4 | 0 | 13.68
62 | 149 | 55 | 15.5619 | 4.4 | 9.5 | 0 | 13.68
62 | 150 | 55 | 15.6133 | 4.4 | 9.6 | 0 | 13.68
63 | 45 | 55 | 10.22 | 4.4 | 9.7 | 0 | 13.68
63 | 46 | 55 | 10.284 | 4.4 | 9.8 | 0 | 13.68
63 | 47 | 55 | 10.348 | 4.4 | 9.9 | 0 | 13.68
63 | 48 | 55 | 10.412 | 4.4 | 10 | 0 | 13.68
63 | 49 | 55 | 10.476 | 4.5 | 3 | 0 | 13.7
63 | 50 | 55 | 10.54 | 4.5 | 3.1 | 0 | 13.7
63 | 51 | 55 | 10.604 | 4.5 | 3.2 | 0 | 13.7
63 | 52 | 55 | 10.668 | 4.5 | 3.3 | 0 | 13.7
63 | 53 | 55 | 10.732 | 4.5 | 3.4 | 0 | 13.7
63 | 54 | 55 | 10.796 | 4.5 | 3.5 | 0 | 13.7
63 | 55 | 55 | 10.86 | 4.5 | 3.6 | 0 | 13.7
63 | 56 | 55 | 10.924 | 4.5 | 3.7 | 0 | 13.7
63 | 57 | 55 | 10.988 | 4.5 | 3.8 | 0 | 13.7
63 | 58 | 55 | 11.052 | 4.5 | 3.9 | 0 | 13.7
63 | 59 | 55 | 11.116 | 4.5 | 4 | 0 | 13.7
63 | 60 | 55 | 11.18 | 4.5 | 4.1 | 0 | 13.7
63 | 61 | 55 | 11.244 | 4.5 | 4.2 | 0 | 13.7
63 | 62 | 55 | 11.308 | 4.5 | 4.3 | 0 | 13.7
63 | 63 | 55 | 11.372 | 4.5 | 4.4 | 0 | 13.7
63 | 64 | 55 | 11.436 | 4.5 | 4.5 | 0 | 13.7
63 | 65 | 55 | 11.5 | 4.5 | 4.6 | 0 | 13.7
63 | 66 | 55 | 11.564 | 4.5 | 4.7 | 0 | 13.7
63 | 67 | 55 | 11.628 | 4.5 | 4.8 | 0 | 13.7
63 | 68 | 55 | 11.692 | 4.5 | 4.9 | 0 | 13.7
63 | 69 | 55 | 11.756 | 4.5 | 5 | 0 | 13.7
63 | 70 | 55 | 11.82 | 4.5 | 5.1 | 0 | 13.7
63 | 71 | 55 | 11.884 | 4.5 | 5.2 | 0 | 13.7
63 | 72 | 55 | 11.948 | 4.5 | 5.3 | 0 | 13.7
63 | 73 | 55 | 12.012 | 4.5 | 5.4 | 0 | 13.7
63 | 74 | 55 | 12.076 | 4.5 | 5.5 | 0 | 13.7
63 | 75 | 55 | 12.14 | 4.5 | 5.6 | 0 | 13.7
63 | 76 | 55 | 12.216 | 4.5 | 5.7 | 0 | 13.7
63 | 77 | 55 | 12.292 | 4.5 | 5.8 | 0 | 13.7
63 | 78 | 55 | 12.368 | 4.5 | 5.9 | 0 | 13.7
63 | 79 | 55 | 12.444 | 4.5 | 6 | 0 | 13.7
63 | 80 | 55 | 12.52 | 4.5 | 6.1 | 0 | 13.7
63 | 81 | 55 | 12.596 | 4.5 | 6.2 | 0 | 13.7
63 | 82 | 55 | 12.672 | 4.5 | 6.3 | 0 | 13.7
63 | 83 | 55 | 12.748 | 4.5 | 6.4 | 0 | 13.7
63 | 84 | 55 | 12.824 | 4.5 | 6.5 | 0 | 13.7
63 | 85 | 55 | 12.9 | 4.5 | 6.6 | 0 | 13.7
63 | 86 | 55 | 12.976 | 4.5 | 6.7 | 0 | 13.7
63 | 87 | 55 | 13.052 | 4.5 | 6.8 | 0 | 13.7
63 | 88 | 55 | 13.128 | 4.5 | 6.9 | 0 | 13.7
63 | 89 | 55 | 13.204 | 4.5 | 7 | 0 | 13.7
63 | 90 | 55 | 13.28 | 4.5 | 7.1 | 0 | 13.7
63 | 91 | 55 | 13.356 | 4.5 | 7.2 | 0 | 13.7
63 | 92 | 55 | 13.432 | 4.5 | 7.3 | 0 | 13.7
63 | 93 | 55 | 13.508 | 4.5 | 7.4 | 0 | 13.7
63 | 94 | 55 | 13.584 | 4.5 | 7.5 | 0 | 13.7
63 | 95 | 55 | 13.66 | 4.5 | 7.6 | 0 | 13.7
63 | 96 | 55 | 13.736 | 4.5 | 7.7 | 0 | 13.7
63 | 97 | 55 | 13.812 | 4.5 | 7.8 | 0 | 13.7
63 | 98 | 55 | 13.888 | 4.5 | 7.9 | 0 | 13.7
63 | 99 | 55 | 13.964 | 4.5 | 8 | 0 | 13.7
63 | 100 | 55 | 14.04 | 4.5 | 8.1 | 0 | 13.7
63 | 101 | 55 | 14.052 | 4.5 | 8.2 | 0 | 13.7
63 | 102 | 55 | 14.064 | 4.5 | 8.3 | 0 | 13.7
63 | 103 | 55 | 14.076 | 4.5 | 8.4 | 0 | 13.7
63 | 104 | 55 | 14.088 | 4.5 | 8.5 | 0 | 13.7
63 | 105 | 55 | 14.1 | 4.5 | 8.6 | 0 | 13.7
63 | 106 | 55 | 14.112 | 4.5 | 8.7 | 0 | 13.7
63 | 107 | 55 | 14.124 | 4.5 | 8.8 | 0 | 13.7
63 | 108 | 55 | 14.136 | 4.5 | 8.9 | 0 | 13.7
63 | 109 | 55 | 14.148 | 4.5 | 9 | 0 | 13.7
63 | 110 | 55 | 14.16 | 4.5 | 9.1 | 0 | 13.7
63 | 111 | 55 | 14.172 | 4.5 | 9.2 | 0 | 13.7
63 | 112 | 55 | 14.184 | 4.5 | 9.3 | 0 | 13.7
63 | 113 | 55 | 14.196 | 4.5 | 9.4 | 0 | 13.7
63 | 114 | 55 | 14.208 | 4.5 | 9.5 | 0 | 13.7
63 | 115 | 55 | 14.22 | 4.5 | 9.6 | 0 | 13.7
63 | 116 | 55 | 14.232 | 4.5 | 9.7 | 0 | 13.7
63 | 117 | 55 | 14.244 | 4.5 | 9.8 | 0 | 13.7
63 | 118 | 55 | 14.256 | 4.5 | 9.9 | 0 | 13.7
63 | 119 | 55 | 14.268 | 4.5 | 10 | 0 | 13.7
63 | 120 | 55 | 14.28 | 4.6 | 3 | 0 | 13.72
63 | 121 | 55 | 14.292 | 4.6 | 3.1 | 0 | 13.72
63 | 122 | 55 | 14.304 | 4.6 | 3.2 | 0 | 13.72
63 | 123 | 55 | 14.316 | 4.6 | 3.3 | 0 | 13.72
63 | 124 | 55 | 14.328 | 4.6 | 3.4 | 0 | 13.72
63 | 125 | 55 | 14.34 | 4.6 | 3.5 | 0 | 13.72
63 | 126 | 55 | 14.3912 | 4.6 | 3.6 | 0 | 13.72
63 | 127 | 55 | 14.4424 | 4.6 | 3.7 | 0 | 13.72
63 | 128 | 55 | 14.4936 | 4.6 | 3.8 | 0 | 13.72
63 | 129 | 55 | 14.5448 | 4.6 | 3.9 | 0 | 13.72
63 | 130 | 55 | 14.596 | 4.6 | 4 | 0 | 13.72
63 | 131 | 55 | 14.6472 | 4.6 | 4.1 | 0 | 13.72
63 | 132 | 55 | 14.6984 | 4.6 | 4.2 | 0 | 13.72
63 | 133 | 55 | 14.7496 | 4.6 | 4.3 | 0 | 13.72
63 | 134 | 55 | 14.8008 | 4.6 | 4.4 | 0 | 13.72
63 | 135 | 55 | 14.852 | 4.6 | 4.5 | 0 | 13.72
63 | 136 | 55 | 14.9032 | 4.6 | 4.6 | 0 | 13.72
63 | 137 | 55 | 14.9544 | 4.6 | 4.7 | 0 | 13.72
63 | 138 | 55 | 15.0056 | 4.6 | 4.8 | 0 | 13.72
63 | 139 | 55 | 15.0568 | 4.6 | 4.9 | 0 | 13.72
63 | 140 | 55 | 15.108 | 4.6 | 5 | 0 | 13.72
63 | 141 | 55 | 15.1592 | 4.6 | 5.1 | 0 | 13.72
63 | 142 | 55 | 15.2104 | 4.6 | 5.2 | 0 | 13.72
63 | 143 | 55 | 15.2616 | 4.6 | 5.3 | 0 | 13.72
63 | 144 | 55 | 15.3128 | 4.6 | 5.4 | 0 | 13.72
63 | 145 | 55 | 15.364 | 4.6 | 5.5 | 0 | 13.72
63 | 146 | 55 | 15.4152 | 4.6 | 5.6 | 0 | 13.72
63 | 147 | 55 | 15.4664 | 4.6 | 5.7 | 0 | 13.72
63 | 148 | 55 | 15.5176 | 4.6 | 5.8 | 0 | 13.72
63 | 149 | 55 | 15.5688 | 4.6 | 5.9 | 0 | 13.72
63 | 150 | 55 | 15.62 | 4.6 | 6 | 0 | 13.72
64 | 45 | 55 | 10.2267 | 4.6 | 6.1 | 0 | 13.72
64 | 46 | 55 | 10.2909 | 4.6 | 6.2 | 0 | 13.72
64 | 47 | 55 | 10.3551 | 4.6 | 6.3 | 0 | 13.72
64 | 48 | 55 | 10.4193 | 4.6 | 6.4 | 0 | 13.72
64 | 49 | 55 | 10.4836 | 4.6 | 6.5 | 0 | 13.72
64 | 50 | 55 | 10.5478 | 4.6 | 6.6 | 0 | 13.72
64 | 51 | 55 | 10.612 | 4.6 | 6.7 | 0 | 13.72
64 | 52 | 55 | 10.6762 | 4.6 | 6.8 | 0 | 13.72
64 | 53 | 55 | 10.7404 | 4.6 | 6.9 | 0 | 13.72
64 | 54 | 55 | 10.8047 | 4.6 | 7 | 0 | 13.72
64 | 55 | 55 | 10.8689 | 4.6 | 7.1 | 0 | 13.72
64 | 56 | 55 | 10.9331 | 4.6 | 7.2 | 0 | 13.72
64 | 57 | 55 | 10.9973 | 4.6 | 7.3 | 0 | 13.72
64 | 58 | 55 | 11.0616 | 4.6 | 7.4 | 0 | 13.72
64 | 59 | 55 | 11.1258 | 4.6 | 7.5 | 0 | 13.72
64 | 60 | 55 | 11.19 | 4.6 | 7.6 | 0 | 13.72
64 | 61 | 55 | 11.2542 | 4.6 | 7.7 | 0 | 13.72
64 | 62 | 55 | 11.3184 | 4.6 | 7.8 | 0 | 13.72
64 | 63 | 55 | 11.3827 | 4.6 | 7.9 | 0 | 13.72
64 | 64 | 55 | 11.4469 | 4.6 | 8 | 0 | 13.72
64 | 65 | 55 | 11.5111 | 4.6 | 8.1 | 0 | 13.72
64 | 66 | 55 | 11.5753 | 4.6 | 8.2 | 0 | 13.72
64 | 67 | 55 | 11.6396 | 4.6 | 8.3 | 0 | 13.72
64 | 68 | 55 | 11.7038 | 4.6 | 8.4 | 0 | 13.72
64 | 69 | 55 | 11.768 | 4.6 | 8.5 | 0 | 13.72
64 | 70 | 55 | 11.8322 | 4.6 | 8.6 | 0 | 13.72
64 | 71 | 55 | 11.8964 | 4.6 | 8.7 | 0 | 13.72
64 | 72 | 55 | 11.9607 | 4.6 | 8.8 | 0 | 13.72
64 | 73 | 55 | 12.0249 | 4.6 | 8.9 | 0 | 13.72
64 | 74 | 55 | 12.0891 | 4.6 | 9 | 0 | 13.72
64 | 75 | 55 | 12.1533 | 4.6 | 9.1 | 0 | 13.72
64 | 76 | 55 | 12.2293 | 4.6 | 9.2 | 0 | 13.72
64 | 77 | 55 | 12.3053 | 4.6 | 9.3 | 0 | 13.72
64 | 78 | 55 | 12.3813 | 4.6 | 9.4 | 0 | 13.72
64 | 79 | 55 | 12.4573 | 4.6 | 9.5 | 0 | 13.72
64 | 80 | 55 | 12.5333 | 4.6 | 9.6 | 0 | 13.72
64 | 81 | 55 | 12.6093 | 4.6 | 9.7 | 0 | 13.72
64 | 82 | 55 | 12.6853 | 4.6 | 9.8 | 0 | 13.72
64 | 83 | 55 | 12.7613 | 4.6 | 9.9 | 0 | 13.72
64 | 84 | 55 | 12.8373 | 4.6 | 10 | 0 | 13.72
64 | 85 | 55 | 12.9133 | 4.7 | 3 | 0 | 13.74
64 | 86 | 55 | 12.9893 | 4.7 | 3.1 | 0 | 13.74
64 | 87 | 55 | 13.0653 | 4.7 | 3.2 | 0 | 13.74
64 | 88 | 55 | 13.1413 | 4.7 | 3.3 | 0 | 13.74
64 | 89 | 55 | 13.2173 | 4.7 | 3.4 | 0 | 13.74
64 | 90 | 55 | 13.2933 | 4.7 | 3.5 | 0 | 13.74
64 | 91 | 55 | 13.3693 | 4.7 | 3.6 | 0 | 13.74
64 | 92 | 55 | 13.4453 | 4.7 | 3.7 | 0 | 13.74
64 | 93 | 55 | 13.5213 | 4.7 | 3.8 | 0 | 13.74
64 | 94 | 55 | 13.5973 | 4.7 | 3.9 | 0 | 13.74
64 | 95 | 55 | 13.6733 | 4.7 | 4 | 0 | 13.74
64 | 96 | 55 | 13.7493 | 4.7 | 4.1 | 0 | 13.74
64 | 97 | 55 | 13.8253 | 4.7 | 4.2 | 0 | 13.74
64 | 98 | 55 | 13.9013 | 4.7 | 4.3 | 0 | 13.74
64 | 99 | 55 | 13.9773 | 4.7 | 4.4 | 0 | 13.74
64 | 100 | 55 | 14.0533 | 4.7 | 4.5 | 0 | 13.74
64 | 101 | 55 | 14.0653 | 4.7 | 4.6 | 0 | 13.74
64 | 102 | 55 | 14.0773 | 4.7 | 4.7 | 0 | 13.74
64 | 103 | 55 | 14.0893 | 4.7 | 4.8 | 0 | 13.74
64 | 104 | 55 | 14.1013 | 4.7 | 4.9 | 0 | 13.74
64 | 105 | 55 | 14.1133 | 4.7 | 5 | 0 | 13.74
64 | 106 | 55 | 14.1253 | 4.7 | 5.1 | 0 | 13.74
64 | 107 | 55 | 14.1373 | 4.7 | 5.2 | 0 | 13.74
64 | 108 | 55 | 14.1493 | 4.7 | 5.3 | 0 | 13.74
64 | 109 | 55 | 14.1613 | 4.7 | 5.4 | 0 | 13.74
64 | 110 | 55 | 14.1733 | 4.7 | 5.5 | 0 | 13.74
64 | 111 | 55 | 14.1853 | 4.7 | 5.6 | 0 | 13.74
64 | 112 | 55 | 14.1973 | 4.7 | 5.7 | 0 | 13.74
64 | 113 | 55 | 14.2093 | 4.7 | 5.8 | 0 | 13.74
64 | 114 | 55 | 14.2213 | 4.7 | 5.9 | 0 | 13.74
64 | 115 | 55 | 14.2333 | 4.7 | 6 | 0 | 13.74
64 | 116 | 55 | 14.2453 | 4.7 | 6.1 | 0 | 13.74
64 | 117 | 55 | 14.2573 | 4.7 | 6.2 | 0 | 13.74
64 | 118 | 55 | 14.2693 | 4.7 | 6.3 | 0 | 13.74
64 | 119 | 55 | 14.2813 | 4.7 | 6.4 | 0 | 13.74
64 | 120 | 55 | 14.2933 | 4.7 | 6.5 | 0 | 13.74
64 | 121 | 55 | 14.3053 | 4.7 | 6.6 | 0 | 13.74
64 | 122 | 55 | 14.3173 | 4.7 | 6.7 | 0 | 13.74
64 | 123 | 55 | 14.3293 | 4.7 | 6.8 | 0 | 13.74
64 | 124 | 55 | 14.3413 | 4.7 | 6.9 | 0 | 13.74
64 | 125 | 55 | 14.3533 | 4.7 | 7 | 0 | 13.74
64 | 126 | 55 | 14.4043 | 4.7 | 7.1 | 0 | 13.74
64 | 127 | 55 | 14.4552 | 4.7 | 7.2 | 0 | 13.74
64 | 128 | 55 | 14.5061 | 4.7 | 7.3 | 0 | 13.74
64 | 129 | 55 | 14.5571 | 4.7 | 7.4 | 0 | 13.74
64 | 130 | 55 | 14.608 | 4.7 | 7.5 | 0 | 13.74
64 | 131 | 55 | 14.6589 | 4.7 | 7.6 | 0 | 13.74
64 | 132 | 55 | 14.7099 | 4.7 | 7.7 | 0 | 13.74
64 | 133 | 55 | 14.7608 | 4.7 | 7.8 | 0 | 13.74
64 | 134 | 55 | 14.8117 | 4.7 | 7.9 | 0 | 13.74
64 | 135 | 55 | 14.8627 | 4.7 | 8 | 0 | 13.74
64 | 136 | 55 | 14.9136 | 4.7 | 8.1 | 0 | 13.74
64 | 137 | 55 | 14.9645 | 4.7 | 8.2 | 0 | 13.74
64 | 138 | 55 | 15.0155 | 4.7 | 8.3 | 0 | 13.74
64 | 139 | 55 | 15.0664 | 4.7 | 8.4 | 0 | 13.74
64 | 140 | 55 | 15.1173 | 4.7 | 8.5 | 0 | 13.74
64 | 141 | 55 | 15.1683 | 4.7 | 8.6 | 0 | 13.74
64 | 142 | 55 | 15.2192 | 4.7 | 8.7 | 0 | 13.74
64 | 143 | 55 | 15.2701 | 4.7 | 8.8 | 0 | 13.74
64 | 144 | 55 | 15.3211 | 4.7 | 8.9 | 0 | 13.74
64 | 145 | 55 | 15.372 | 4.7 | 9 | 0 | 13.74
64 | 146 | 55 | 15.4229 | 4.7 | 9.1 | 0 | 13.74
64 | 147 | 55 | 15.4739 | 4.7 | 9.2 | 0 | 13.74
64 | 148 | 55 | 15.5248 | 4.7 | 9.3 | 0 | 13.74
64 | 149 | 55 | 15.5757 | 4.7 | 9.4 | 0 | 13.74
64 | 150 | 55 | 15.6267 | 4.7 | 9.5 | 0 | 13.74
65 | 45 | 55 | 10.2333 | 4.7 | 9.6 | 0 | 13.74
65 | 46 | 55 | 10.2978 | 4.7 | 9.7 | 0 | 13.74
65 | 47 | 55 | 10.3622 | 4.7 | 9.8 | 0 | 13.74
65 | 48 | 55 | 10.4267 | 4.7 | 9.9 | 0 | 13.74
65 | 49 | 55 | 10.4911 | 4.7 | 10 | 0 | 13.74
65 | 50 | 55 | 10.5556 | 4.8 | 3 | 0 | 13.76
65 | 51 | 55 | 10.62 | 4.8 | 3.1 | 0 | 13.76
65 | 52 | 55 | 10.6844 | 4.8 | 3.2 | 0 | 13.76
65 | 53 | 55 | 10.7489 | 4.8 | 3.3 | 0 | 13.76
65 | 54 | 55 | 10.8133 | 4.8 | 3.4 | 0 | 13.76
65 | 55 | 55 | 10.8778 | 4.8 | 3.5 | 0 | 13.76
65 | 56 | 55 | 10.9422 | 4.8 | 3.6 | 0 | 13.76
65 | 57 | 55 | 11.0067 | 4.8 | 3.7 | 0 | 13.76
65 | 58 | 55 | 11.0711 | 4.8 | 3.8 | 0 | 13.76
65 | 59 | 55 | 11.1356 | 4.8 | 3.9 | 0 | 13.76
65 | 60 | 55 | 11.2 | 4.8 | 4 | 0 | 13.76
65 | 61 | 55 | 11.2644 | 4.8 | 4.1 | 0 | 13.76
65 | 62 | 55 | 11.3289 | 4.8 | 4.2 | 0 | 13.76
65 | 63 | 55 | 11.3933 | 4.8 | 4.3 | 0 | 13.76
65 | 64 | 55 | 11.4578 | 4.8 | 4.4 | 0 | 13.76
65 | 65 | 55 | 11.5222 | 4.8 | 4.5 | 0 | 13.76
65 | 66 | 55 | 11.5867 | 4.8 | 4.6 | 0 | 13.76
65 | 67 | 55 | 11.6511 | 4.8 | 4.7 | 0 | 13.76
65 | 68 | 55 | 11.7156 | 4.8 | 4.8 | 0 | 13.76
65 | 69 | 55 | 11.78 | 4.8 | 4.9 | 0 | 13.76
65 | 70 | 55 | 11.8444 | 4.8 | 5 | 0 | 13.76
65 | 71 | 55 | 11.9089 | 4.8 | 5.1 | 0 | 13.76
65 | 72 | 55 | 11.9733 | 4.8 | 5.2 | 0 | 13.76
65 | 73 | 55 | 12.0378 | 4.8 | 5.3 | 0 | 13.76
65 | 74 | 55 | 12.1022 | 4.8 | 5.4 | 0 | 13.76
65 | 75 | 55 | 12.1667 | 4.8 | 5.5 | 0 | 13.76
65 | 76 | 55 | 12.2427 | 4.8 | 5.6 | 0 | 13.76
65 | 77 | 55 | 12.3187 | 4.8 | 5.7 | 0 | 13.76
65 | 78 | 55 | 12.3947 | 4.8 | 5.8 | 0 | 13.76
65 | 79 | 55 | 12.4707 | 4.8 | 5.9 | 0 | 13.76
65 | 80 | 55 | 12.5467 | 4.8 | 6 | 0 | 13.76
65 | 81 | 55 | 12.6227 | 4.8 | 6.1 | 0 | 13.76
65 | 82 | 55 | 12.6987 | 4.8 | 6.2 | 0 | 13.76
65 | 83 | 55 | 12.7747 | 4.8 | 6.3 | 0 | 13.76
65 | 84 | 55 | 12.8507 | 4.8 | 6.4 | 0 | 13.76
65 | 85 | 55 | 12.9267 | 4.8 | 6.5 | 0 | 13.76
65 | 86 | 55 | 13.0027 | 4.8 | 6.6 | 0 | 13.76
65 | 87 | 55 | 13.0787 | 4.8 | 6.7 | 0 | 13.76
65 | 88 | 55 | 13.1547 | 4.8 | 6.8 | 0 | 13.76
65 | 89 | 55 | 13.2307 | 4.8 | 6.9 | 0 | 13.76
65 | 90 | 55 | 13.3067 | 4.8 | 7 | 0 | 13.76
65 | 91 | 55 | 13.3827 | 4.8 | 7.1 | 0 | 13.76
65 | 92 | 55 | 13.4587 | 4.8 | 7.2 | 0 | 13.76
65 | 93 | 55 | 13.5347 | 4.8 | 7.3 | 0 | 13.76
65 | 94 | 55 | 13.6107 | 4.8 | 7.4 | 0 | 13.76
65 | 95 | 55 | 13.6867 | 4.8 | 7.5 | 0 | 13.76
65 | 96 | 55 | 13.7627 | 4.8 | 7.6 | 0 | 13.76
65 | 97 | 55 | 13.8387 | 4.8 | 7.7 | 0 | 13.76
65 | 98 | 55 | 13.9147 | 4.8 | 7.8 | 0 | 13.76
65 | 99 | 55 | 13.9907 | 4.8 | 7.9 | 0 | 13.76
65 | 100 | 55 | 14.0667 | 4.8 | 8 | 0 | 13.76
65 | 101 | 55 | 14.0787 | 4.8 | 8.1 | 0 | 13.76
65 | 102 | 55 | 14.0907 | 4.8 | 8.2 | 0 | 13.76
65 | 103 | 55 | 14.1027 | 4.8 | 8.3 | 0 | 13.76
65 | 104 | 55 | 14.1147 | 4.8 | 8.4 | 0 | 13.76
65 | 105 | 55 | 14.1267 | 4.8 | 8.5 | 0 | 13.76
65 | 106 | 55 | 14.1387 | 4.8 | 8.6 | 0 | 13.76
65 | 107 | 55 | 14.1507 | 4.8 | 8.7 | 0 | 13.76
65 | 108 | 55 | 14.1627 | 4.8 | 8.8 | 0 | 13.76
65 | 109 | 55 | 14.1747 | 4.8 | 8.9 | 0 | 13.76
65 | 110 | 55 | 14.1867 | 4.8 | 9 | 0 | 13.76
65 | 111 | 55 | 14.1987 | 4.8 | 9.1 | 0 | 13.76
65 | 112 | 55 | 14.2107 | 4.8 | 9.2 | 0 | 13.76
65 | 113 | 55 | 14.2227 | 4.8 | 9.3 | 0 | 13.76
65 | 114 | 55 | 14.2347 | 4.8 | 9.4 | 0 | 13.76
65 | 115 | 55 | 14.2467 | 4.8 | 9.5 | 0 | 13.76
65 | 116 | 55 | 14.2587 | 4.8 | 9.6 | 0 | 13.76
65 | 117 | 55 | 14.2707 | 4.8 | 9.7 | 0 | 13.76
65 | 118 | 55 | 14.2827 | 4.8 | 9.8 | 0 | 13.76
65 | 119 | 55 | 14.2947 | 4.8 | 9.9 | 0 | 13.76
65 | 120 | 55 | 14.3067 | 4.8 | 10 | 0 | 13.76
65 | 121 | 55 | 14.3187 | 4.9 | 3 | 0 | 13.78
65 | 122 | 55 | 14.3307 | 4.9 | 3.1 | 0 | 13.78
65 | 123 | 55 | 14.3427 | 4.9 | 3.2 | 0 | 13.78
65 | 124 | 55 | 14.3547 | 4.9 | 3.3 | 0 | 13.78
65 | 125 | 55 | 14.3667 | 4.9 | 3.4 | 0 | 13.78
65 | 126 | 55 | 14.4173 | 4.9 | 3.5 | 0 | 13.78
65 | 127 | 55 | 14.468 | 4.9 | 3.6 | 0 | 13.78
65 | 128 | 55 | 14.5187 | 4.9 | 3.7 | 0 | 13.78
65 | 129 | 55 | 14.5693 | 4.9 | 3.8 | 0 | 13.78
65 | 130 | 55 | 14.62 | 4.9 | 3.9 | 0 | 13.78
65 | 131 | 55 | 14.6707 | 4.9 | 4 | 0 | 13.78
65 | 132 | 55 | 14.7213 | 4.9 | 4.1 | 0 | 13.78
65 | 133 | 55 | 14.772 | 4.9 | 4.2 | 0 | 13.78
65 | 134 | 55 | 14.8227 | 4.9 | 4.3 | 0 | 13.78
65 | 135 | 55 | 14.8733 | 4.9 | 4.4 | 0 | 13.78
65 | 136 | 55 | 14.924 | 4.9 | 4.5 | 0 | 13.78
65 | 137 | 55 | 14.9747 | 4.9 | 4.6 | 0 | 13.78
65 | 138 | 55 | 15.0253 | 4.9 | 4.7 | 0 | 13.78
65 | 139 | 55 | 15.076 | 4.9 | 4.8 | 0 | 13.78
65 | 140 | 55 | 15.1267 | 4.9 | 4.9 | 0 | 13.78
65 | 141 | 55 | 15.1773 | 4.9 | 5 | 0 | 13.78
65 | 142 | 55 | 15.228 | 4.9 | 5.1 | 0 | 13.78
65 | 143 | 55 | 15.2787 | 4.9 | 5.2 | 0 | 13.78
65 | 144 | 55 | 15.3293 | 4.9 | 5.3 | 0 | 13.78
65 | 145 | 55 | 15.38 | 4.9 | 5.4 | 0 | 13.78
65 | 146 | 55 | 15.4307 | 4.9 | 5.5 | 0 | 13.78
65 | 147 | 55 | 15.4813 | 4.9 | 5.6 | 0 | 13.78
65 | 148 | 55 | 15.532 | 4.9 | 5.7 | 0 | 13.78
65 | 149 | 55 | 15.5827 | 4.9 | 5.8 | 0 | 13.78
65 | 150 | 55 | 15.6333 | 4.9 | 5.9 | 0 | 13.78
66 | 45 | 55 | 10.24 | 4.9 | 6 | 0 | 13.78
66 | 46 | 55 | 10.3047 | 4.9 | 6.1 | 0 | 13.78
66 | 47 | 55 | 10.3693 | 4.9 | 6.2 | 0 | 13.78
66 | 48 | 55 | 10.434 | 4.9 | 6.3 | 0 | 13.78
66 | 49 | 55 | 10.4987 | 4.9 | 6.4 | 0 | 13.78
66 | 50 | 55 | 10.5633 | 4.9 | 6.5 | 0 | 13.78
66 | 51 | 55 | 10.628 | 4.9 | 6.6 | 0 | 13.78
66 | 52 | 55 | 10.6927 | 4.9 | 6.7 | 0 | 13.78
66 | 53 | 55 | 10.7573 | 4.9 | 6.8 | 0 | 13.78
66 | 54 | 55 | 10.822 | 4.9 | 6.9 | 0 | 13.78
66 | 55 | 55 | 10.8867 | 4.9 | 7 | 0 | 13.78
66 | 56 | 55 | 10.9513 | 4.9 | 7.1 | 0 | 13.78
66 | 57 | 55 | 11.016 | 4.9 | 7.2 | 0 | 13.78
66 | 58 | 55 | 11.0807 | 4.9 | 7.3 | 0 | 13.78
66 | 59 | 55 | 11.1453 | 4.9 | 7.4 | 0 | 13.78
66 | 60 | 55 | 11.21 | 4.9 | 7.5 | 0 | 13.78
66 | 61 | 55 | 11.2747 | 4.9 | 7.6 | 0 | 13.78
66 | 62 | 55 | 11.3393 | 4.9 | 7.7 | 0 | 13.78
66 | 63 | 55 | 11.404 | 4.9 | 7.8 | 0 | 13.78
66 | 64 | 55 | 11.4687 | 4.9 | 7.9 | 0 | 13.78
66 | 65 | 55 | 11.5333 | 4.9 | 8 | 0 | 13.78
66 | 66 | 55 | 11.598 | 4.9 | 8.1 | 0 | 13.78
66 | 67 | 55 | 11.6627 | 4.9 | 8.2 | 0 | 13.78
66 | 68 | 55 | 11.7273 | 4.9 | 8.3 | 0 | 13.78
66 | 69 | 55 | 11.792 | 4.9 | 8.4 | 0 | 13.78
66 | 70 | 55 | 11.8567 | 4.9 | 8.5 | 0 | 13.78
66 | 71 | 55 | 11.9213 | 4.9 | 8.6 | 0 | 13.78
66 | 72 | 55 | 11.986 | 4.9 | 8.7 | 0 | 13.78
66 | 73 | 55 | 12.0507 | 4.9 | 8.8 | 0 | 13.78
66 | 74 | 55 | 12.1153 | 4.9 | 8.9 | 0 | 13.78
66 | 75 | 55 | 12.18 | 4.9 | 9 | 0 | 13.78
66 | 76 | 55 | 12.256 | 4.9 | 9.1 | 0 | 13.78
66 | 77 | 55 | 12.332 | 4.9 | 9.2 | 0 | 13.78
66 | 78 | 55 | 12.408 | 4.9 | 9.3 | 0 | 13.78
66 | 79 | 55 | 12.484 | 4.9 | 9.4 | 0 | 13.78
66 | 80 | 55 | 12.56 | 4.9 | 9.5 | 0 | 13.78
66 | 81 | 55 | 12.636 | 4.9 | 9.6 | 0 | 13.78
66 | 82 | 55 | 12.712 | 4.9 | 9.7 | 0 | 13.78
66 | 83 | 55 | 12.788 | 4.9 | 9.8 | 0 | 13.78
66 | 84 | 55 | 12.864 | 4.9 | 9.9 | 0 | 13.78
66 | 85 | 55 | 12.94 | 4.9 | 10 | 0 | 13.78
66 | 86 | 55 | 13.016 | 5 | 3 | 0 | 13.8
66 | 87 | 55 | 13.092 | 5 | 3.1 | 0 | 13.8
66 | 88 | 55 | 13.168 | 5 | 3.2 | 0 | 13.8
66 | 89 | 55 | 13.244 | 5 | 3.3 | 0 | 13.8
66 | 90 | 55 | 13.32 | 5 | 3.4 | 0 | 13.8
66 | 91 | 55 | 13.396 | 5 | 3.5 | 0 | 13.8
66 | 92 | 55 | 13.472 | 5 | 3.6 | 0 | 13.8
66 | 93 | 55 | 13.548 | 5 | 3.7 | 0 | 13.8
66 | 94 | 55 | 13.624 | 5 | 3.8 | 0 | 13.8
66 | 95 | 55 | 13.7 | 5 | 3.9 | 0 | 13.8
66 | 96 | 55 | 13.776 | 5 | 4 | 0 | 13.8
66 | 97 | 55 | 13.852 | 5 | 4.1 | 0 | 13.8
66 | 98 | 55 | 13.928 | 5 | 4.2 | 0 | 13.8
66 | 99 | 55 | 14.004 | 5 | 4.3 | 0 | 13.8
66 | 100 | 55 | 14.08 | 5 | 4.4 | 0 | 13.8
66 | 101 | 55 | 14.092 | 5 | 4.5 | 0 | 13.8
66 | 102 | 55 | 14.104 | 5 | 4.6 | 0 | 13.8
66 | 103 | 55 | 14.116 | 5 | 4.7 | 0 | 13.8
66 | 104 | 55 | 14.128 | 5 | 4.8 | 0 | 13.8
66 | 105 | 55 | 14.14 | 5 | 4.9 | 0 | 13.8
66 | 106 | 55 | 14.152 | 5 | 5 | 0 | 13.8
66 | 107 | 55 | 14.164 | 5 | 5.1 | 0 | 13.8
66 | 108 | 55 | 14.176 | 5 | 5.2 | 0 | 13.8
66 | 109 | 55 | 14.188 | 5 | 5.3 | 0 | 13.8
66 | 110 | 55 | 14.2 | 5 | 5.4 | 0 | 13.8
66 | 111 | 55 | 14.212 | 5 | 5.5 | 0 | 13.8
66 | 112 | 55 | 14.224 | 5 | 5.6 | 0 | 13.8
66 | 113 | 55 | 14.236 | 5 | 5.7 | 0 | 13.8
66 | 114 | 55 | 14.248 | 5 | 5.8 | 0 | 13.8
66 | 115 | 55 | 14.26 | 5 | 5.9 | 0 | 13.8
66 | 116 | 55 | 14.272 | 5 | 6 | 0 | 13.8
66 | 117 | 55 | 14.284 | 5 | 6.1 | 0 | 13.8
66 | 118 | 55 | 14.296 | 5 | 6.2 | 0 | 13.8
66 | 119 | 55 | 14.308 | 5 | 6.3 | 0 | 13.8
66 | 120 | 55 | 14.32 | 5 | 6.4 | 0 | 13.8
66 | 121 | 55 | 14.332 | 5 | 6.5 | 0 | 13.8
66 | 122 | 55 | 14.344 | 5 | 6.6 | 0 | 13.8
66 | 123 | 55 | 14.356 | 5 | 6.7 | 0 | 13.8
66 | 124 | 55 | 14.368 | 5 | 6.8 | 0 | 13.8
66 | 125 | 55 | 14.38 | 5 | 6.9 | 0 | 13.8
66 | 126 | 55 | 14.4304 | 5 | 7 | 0 | 13.8
66 | 127 | 55 | 14.4808 | 5 | 7.1 | 0 | 13.8
66 | 128 | 55 | 14.5312 | 5 | 7.2 | 0 | 13.8
66 | 129 | 55 | 14.5816 | 5 | 7.3 | 0 | 13.8
66 | 130 | 55 | 14.632 | 5 | 7.4 | 0 | 13.8
66 | 131 | 55 | 14.6824 | 5 | 7.5 | 0 | 13.8
66 | 132 | 55 | 14.7328 | 5 | 7.6 | 0 | 13.8
66 | 133 | 55 | 14.7832 | 5 | 7.7 | 0 | 13.8
66 | 134 | 55 | 14.8336 | 5 | 7.8 | 0 | 13.8
66 | 135 | 55 | 14.884 | 5 | 7.9 | 0 | 13.8
66 | 136 | 55 | 14.9344 | 5 | 8 | 0 | 13.8
66 | 137 | 55 | 14.9848 | 5 | 8.1 | 0 | 13.8
66 | 138 | 55 | 15.0352 | 5 | 8.2 | 0 | 13.8
66 | 139 | 55 | 15.0856 | 5 | 8.3 | 0 | 13.8
66 | 140 | 55 | 15.136 | 5 | 8.4 | 0 | 13.8
66 | 141 | 55 | 15.1864 | 5 | 8.5 | 0 | 13.8
66 | 142 | 55 | 15.2368 | 5 | 8.6 | 0 | 13.8
66 | 143 | 55 | 15.2872 | 5 | 8.7 | 0 | 13.8
66 | 144 | 55 | 15.3376 | 5 | 8.8 | 0 | 13.8
66 | 145 | 55 | 15.388 | 5 | 8.9 | 0 | 13.8
66 | 146 | 55 | 15.4384 | 5 | 9 | 0 | 13.8
66 | 147 | 55 | 15.4888 | 5 | 9.1 | 0 | 13.8
66 | 148 | 55 | 15.5392 | 5 | 9.2 | 0 | 13.8
66 | 149 | 55 | 15.5896 | 5 | 9.3 | 0 | 13.8
66 | 150 | 55 | 15.64 | 5 | 9.4 | 0 | 13.8
67 | 45 | 55 | 10.2467 | 5 | 9.5 | 0 | 13.8
67 | 46 | 55 | 10.3116 | 5 | 9.6 | 0 | 13.8
67 | 47 | 55 | 10.3764 | 5 | 9.7 | 0 | 13.8
67 | 48 | 55 | 10.4413 | 5 | 9.8 | 0 | 13.8
67 | 49 | 55 | 10.5062 | 5 | 9.9 | 0 | 13.8
67 | 50 | 55 | 10.5711 | 5 | 10 | 0 | 13.8
67 | 51 | 55 | 10.636
67 | 52 | 55 | 10.7009
67 | 53 | 55 | 10.7658
67 | 54 | 55 | 10.8307
67 | 55 | 55 | 10.8956
67 | 56 | 55 | 10.9604
67 | 57 | 55 | 11.0253
67 | 58 | 55 | 11.0902
67 | 59 | 55 | 11.1551
67 | 60 | 55 | 11.22
67 | 61 | 55 | 11.2849
67 | 62 | 55 | 11.3498
67 | 63 | 55 | 11.4147
67 | 64 | 55 | 11.4796
67 | 65 | 55 | 11.5444
67 | 66 | 55 | 11.6093
67 | 67 | 55 | 11.6742
67 | 68 | 55 | 11.7391
67 | 69 | 55 | 11.804
67 | 70 | 55 | 11.8689
67 | 71 | 55 | 11.9338
67 | 72 | 55 | 11.9987
67 | 73 | 55 | 12.0636
67 | 74 | 55 | 12.1284
67 | 75 | 55 | 12.1933
67 | 76 | 55 | 12.2693
67 | 77 | 55 | 12.3453
67 | 78 | 55 | 12.4213
67 | 79 | 55 | 12.4973
67 | 80 | 55 | 12.5733
67 | 81 | 55 | 12.6493
67 | 82 | 55 | 12.7253
67 | 83 | 55 | 12.8013
67 | 84 | 55 | 12.8773
67 | 85 | 55 | 12.9533
67 | 86 | 55 | 13.0293
67 | 87 | 55 | 13.1053
67 | 88 | 55 | 13.1813
67 | 89 | 55 | 13.2573
67 | 90 | 55 | 13.3333
67 | 91 | 55 | 13.4093
67 | 92 | 55 | 13.4853
67 | 93 | 55 | 13.5613
67 | 94 | 55 | 13.6373
67 | 95 | 55 | 13.7133
67 | 96 | 55 | 13.7893
67 | 97 | 55 | 13.8653
67 | 98 | 55 | 13.9413
67 | 99 | 55 | 14.0173
67 | 100 | 55 | 14.0933
67 | 101 | 55 | 14.1053
67 | 102 | 55 | 14.1173
67 | 103 | 55 | 14.1293
67 | 104 | 55 | 14.1413
67 | 105 | 55 | 14.1533
67 | 106 | 55 | 14.1653
67 | 107 | 55 | 14.1773
67 | 108 | 55 | 14.1893
67 | 109 | 55 | 14.2013
67 | 110 | 55 | 14.2133
67 | 111 | 55 | 14.2253
67 | 112 | 55 | 14.2373
67 | 113 | 55 | 14.2493
67 | 114 | 55 | 14.2613
67 | 115 | 55 | 14.2733
67 | 116 | 55 | 14.2853
67 | 117 | 55 | 14.2973
67 | 118 | 55 | 14.3093
67 | 119 | 55 | 14.3213
67 | 120 | 55 | 14.3333
67 | 121 | 55 | 14.3453
67 | 122 | 55 | 14.3573
67 | 123 | 55 | 14.3693
67 | 124 | 55 | 14.3813
67 | 125 | 55 | 14.3933
67 | 126 | 55 | 14.4435
67 | 127 | 55 | 14.4936
67 | 128 | 55 | 14.5437
67 | 129 | 55 | 14.5939
67 | 130 | 55 | 14.644
67 | 131 | 55 | 14.6941
67 | 132 | 55 | 14.7443
67 | 133 | 55 | 14.7944
67 | 134 | 55 | 14.8445
67 | 135 | 55 | 14.8947
67 | 136 | 55 | 14.9448
67 | 137 | 55 | 14.9949
67 | 138 | 55 | 15.0451
67 | 139 | 55 | 15.0952
67 | 140 | 55 | 15.1453
67 | 141 | 55 | 15.1955
67 | 142 | 55 | 15.2456
67 | 143 | 55 | 15.2957
67 | 144 | 55 | 15.3459
67 | 145 | 55 | 15.396
67 | 146 | 55 | 15.4461
67 | 147 | 55 | 15.4963
67 | 148 | 55 | 15.5464
67 | 149 | 55 | 15.5965
67 | 150 | 55 | 15.6467
68 | 45 | 55 | 10.2533
68 | 46 | 55 | 10.3184
68 | 47 | 55 | 10.3836
68 | 48 | 55 | 10.4487
68 | 49 | 55 | 10.5138
68 | 50 | 55 | 10.5789
68 | 51 | 55 | 10.644
68 | 52 | 55 | 10.7091
68 | 53 | 55 | 10.7742
68 | 54 | 55 | 10.8393
68 | 55 | 55 | 10.9044
68 | 56 | 55 | 10.9696
68 | 57 | 55 | 11.0347
68 | 58 | 55 | 11.0998
68 | 59 | 55 | 11.1649
68 | 60 | 55 | 11.23
68 | 61 | 55 | 11.2951
68 | 62 | 55 | 11.3602
68 | 63 | 55 | 11.4253
68 | 64 | 55 | 11.4904
68 | 65 | 55 | 11.5556
68 | 66 | 55 | 11.6207
68 | 67 | 55 | 11.6858
68 | 68 | 55 | 11.7509
68 | 69 | 55 | 11.816
68 | 70 | 55 | 11.8811
68 | 71 | 55 | 11.9462
68 | 72 | 55 | 12.0113
68 | 73 | 55 | 12.0764
68 | 74 | 55 | 12.1416
68 | 75 | 55 | 12.2067
68 | 76 | 55 | 12.2827
68 | 77 | 55 | 12.3587
68 | 78 | 55 | 12.4347
68 | 79 | 55 | 12.5107
68 | 80 | 55 | 12.5867
68 | 81 | 55 | 12.6627
68 | 82 | 55 | 12.7387
68 | 83 | 55 | 12.8147
68 | 84 | 55 | 12.8907
68 | 85 | 55 | 12.9667
68 | 86 | 55 | 13.0427
68 | 87 | 55 | 13.1187
68 | 88 | 55 | 13.1947
68 | 89 | 55 | 13.2707
68 | 90 | 55 | 13.3467
68 | 91 | 55 | 13.4227
68 | 92 | 55 | 13.4987
68 | 93 | 55 | 13.5747
68 | 94 | 55 | 13.6507
68 | 95 | 55 | 13.7267
68 | 96 | 55 | 13.8027
68 | 97 | 55 | 13.8787
68 | 98 | 55 | 13.9547
68 | 99 | 55 | 14.0307
68 | 100 | 55 | 14.1067
68 | 101 | 55 | 14.1187
68 | 102 | 55 | 14.1307
68 | 103 | 55 | 14.1427
68 | 104 | 55 | 14.1547
68 | 105 | 55 | 14.1667
68 | 106 | 55 | 14.1787
68 | 107 | 55 | 14.1907
68 | 108 | 55 | 14.2027
68 | 109 | 55 | 14.2147
68 | 110 | 55 | 14.2267
68 | 111 | 55 | 14.2387
68 | 112 | 55 | 14.2507
68 | 113 | 55 | 14.2627
68 | 114 | 55 | 14.2747
68 | 115 | 55 | 14.2867
68 | 116 | 55 | 14.2987
68 | 117 | 55 | 14.3107
68 | 118 | 55 | 14.3227
68 | 119 | 55 | 14.3347
68 | 120 | 55 | 14.3467
68 | 121 | 55 | 14.3587
68 | 122 | 55 | 14.3707
68 | 123 | 55 | 14.3827
68 | 124 | 55 | 14.3947
68 | 125 | 55 | 14.4067
68 | 126 | 55 | 14.4565
68 | 127 | 55 | 14.5064
68 | 128 | 55 | 14.5563
68 | 129 | 55 | 14.6061
68 | 130 | 55 | 14.656
68 | 131 | 55 | 14.7059
68 | 132 | 55 | 14.7557
68 | 133 | 55 | 14.8056
68 | 134 | 55 | 14.8555
68 | 135 | 55 | 14.9053
68 | 136 | 55 | 14.9552
68 | 137 | 55 | 15.0051
68 | 138 | 55 | 15.0549
68 | 139 | 55 | 15.1048
68 | 140 | 55 | 15.1547
68 | 141 | 55 | 15.2045
68 | 142 | 55 | 15.2544
68 | 143 | 55 | 15.3043
68 | 144 | 55 | 15.3541
68 | 145 | 55 | 15.404
68 | 146 | 55 | 15.4539
68 | 147 | 55 | 15.5037
68 | 148 | 55 | 15.5536
68 | 149 | 55 | 15.6035
68 | 150 | 55 | 15.6533
69 | 45 | 55 | 10.26
69 | 46 | 55 | 10.3253
69 | 47 | 55 | 10.3907
69 | 48 | 55 | 10.456
69 | 49 | 55 | 10.5213
69 | 50 | 55 | 10.5867
69 | 51 | 55 | 10.652
69 | 52 | 55 | 10.7173
69 | 53 | 55 | 10.7827
69 | 54 | 55 | 10.848
69 | 55 | 55 | 10.9133
69 | 56 | 55 | 10.9787
69 | 57 | 55 | 11.044
69 | 58 | 55 | 11.1093
69 | 59 | 55 | 11.1747
69 | 60 | 55 | 11.24
69 | 61 | 55 | 11.3053
69 | 62 | 55 | 11.3707
69 | 63 | 55 | 11.436
69 | 64 | 55 | 11.5013
69 | 65 | 55 | 11.5667
69 | 66 | 55 | 11.632
69 | 67 | 55 | 11.6973
69 | 68 | 55 | 11.7627
69 | 69 | 55 | 11.828
69 | 70 | 55 | 11.8933
69 | 71 | 55 | 11.9587
69 | 72 | 55 | 12.024
69 | 73 | 55 | 12.0893
69 | 74 | 55 | 12.1547
69 | 75 | 55 | 12.22
69 | 76 | 55 | 12.296
69 | 77 | 55 | 12.372
69 | 78 | 55 | 12.448
69 | 79 | 55 | 12.524
69 | 80 | 55 | 12.6
69 | 81 | 55 | 12.676
69 | 82 | 55 | 12.752
69 | 83 | 55 | 12.828
69 | 84 | 55 | 12.904
69 | 85 | 55 | 12.98
69 | 86 | 55 | 13.056
69 | 87 | 55 | 13.132
69 | 88 | 55 | 13.208
69 | 89 | 55 | 13.284
69 | 90 | 55 | 13.36
69 | 91 | 55 | 13.436
69 | 92 | 55 | 13.512
69 | 93 | 55 | 13.588
69 | 94 | 55 | 13.664
69 | 95 | 55 | 13.74
69 | 96 | 55 | 13.816
69 | 97 | 55 | 13.892
69 | 98 | 55 | 13.968
69 | 99 | 55 | 14.044
69 | 100 | 55 | 14.12
69 | 101 | 55 | 14.132
69 | 102 | 55 | 14.144
69 | 103 | 55 | 14.156
69 | 104 | 55 | 14.168
69 | 105 | 55 | 14.18
69 | 106 | 55 | 14.192
69 | 107 | 55 | 14.204
69 | 108 | 55 | 14.216
69 | 109 | 55 | 14.228
69 | 110 | 55 | 14.24
69 | 111 | 55 | 14.252
69 | 112 | 55 | 14.264
69 | 113 | 55 | 14.276
69 | 114 | 55 | 14.288
69 | 115 | 55 | 14.3
69 | 116 | 55 | 14.312
69 | 117 | 55 | 14.324
69 | 118 | 55 | 14.336
69 | 119 | 55 | 14.348
69 | 120 | 55 | 14.36
69 | 121 | 55 | 14.372
69 | 122 | 55 | 14.384
69 | 123 | 55 | 14.396
69 | 124 | 55 | 14.408
69 | 125 | 55 | 14.42
69 | 126 | 55 | 14.4696
69 | 127 | 55 | 14.5192
69 | 128 | 55 | 14.5688
69 | 129 | 55 | 14.6184
69 | 130 | 55 | 14.668
69 | 131 | 55 | 14.7176
69 | 132 | 55 | 14.7672
69 | 133 | 55 | 14.8168
69 | 134 | 55 | 14.8664
69 | 135 | 55 | 14.916
69 | 136 | 55 | 14.9656
69 | 137 | 55 | 15.0152
69 | 138 | 55 | 15.0648
69 | 139 | 55 | 15.1144
69 | 140 | 55 | 15.164
69 | 141 | 55 | 15.2136
69 | 142 | 55 | 15.2632
69 | 143 | 55 | 15.3128
69 | 144 | 55 | 15.3624
69 | 145 | 55 | 15.412
69 | 146 | 55 | 15.4616
69 | 147 | 55 | 15.5112
69 | 148 | 55 | 15.5608
69 | 149 | 55 | 15.6104
69 | 150 | 55 | 15.66
70 | 45 | 55 | 10.2667
70 | 46 | 55 | 10.3322
70 | 47 | 55 | 10.3978
70 | 48 | 55 | 10.4633
70 | 49 | 55 | 10.5289
70 | 50 | 55 | 10.5944
70 | 51 | 55 | 10.66
70 | 52 | 55 | 10.7256
70 | 53 | 55 | 10.7911
70 | 54 | 55 | 10.8567
70 | 55 | 55 | 10.9222
70 | 56 | 55 | 10.9878
70 | 57 | 55 | 11.0533
70 | 58 | 55 | 11.1189
70 | 59 | 55 | 11.1844
70 | 60 | 55 | 11.25
70 | 61 | 55 | 11.3156
70 | 62 | 55 | 11.3811
70 | 63 | 55 | 11.4467
70 | 64 | 55 | 11.5122
70 | 65 | 55 | 11.5778
70 | 66 | 55 | 11.6433
70 | 67 | 55 | 11.7089
70 | 68 | 55 | 11.7744
70 | 69 | 55 | 11.84
70 | 70 | 55 | 11.9056
70 | 71 | 55 | 11.9711
70 | 72 | 55 | 12.0367
70 | 73 | 55 | 12.1022
70 | 74 | 55 | 12.1678
70 | 75 | 55 | 12.2333
70 | 76 | 55 | 12.3093
70 | 77 | 55 | 12.3853
70 | 78 | 55 | 12.4613
70 | 79 | 55 | 12.5373
70 | 80 | 55 | 12.6133
70 | 81 | 55 | 12.6893
70 | 82 | 55 | 12.7653
70 | 83 | 55 | 12.8413
70 | 84 | 55 | 12.9173
70 | 85 | 55 | 12.9933
70 | 86 | 55 | 13.0693
70 | 87 | 55 | 13.1453
70 | 88 | 55 | 13.2213
70 | 89 | 55 | 13.2973
70 | 90 | 55 | 13.3733
70 | 91 | 55 | 13.4493
70 | 92 | 55 | 13.5253
70 | 93 | 55 | 13.6013
70 | 94 | 55 | 13.6773
70 | 95 | 55 | 13.7533
70 | 96 | 55 | 13.8293
70 | 97 | 55 | 13.9053
70 | 98 | 55 | 13.9813
70 | 99 | 55 | 14.0573
70 | 100 | 55 | 14.1333
70 | 101 | 55 | 14.1453
70 | 102 | 55 | 14.1573
70 | 103 | 55 | 14.1693
70 | 104 | 55 | 14.1813
70 | 105 | 55 | 14.1933
70 | 106 | 55 | 14.2053
70 | 107 | 55 | 14.2173
70 | 108 | 55 | 14.2293
70 | 109 | 55 | 14.2413
70 | 110 | 55 | 14.2533
70 | 111 | 55 | 14.2653
70 | 112 | 55 | 14.2773
70 | 113 | 55 | 14.2893
70 | 114 | 55 | 14.3013
70 | 115 | 55 | 14.3133
70 | 116 | 55 | 14.3253
70 | 117 | 55 | 14.3373
70 | 118 | 55 | 14.3493
70 | 119 | 55 | 14.3613
70 | 120 | 55 | 14.3733
70 | 121 | 55 | 14.3853
70 | 122 | 55 | 14.3973
70 | 123 | 55 | 14.4093
70 | 124 | 55 | 14.4213
70 | 125 | 55 | 14.4333
70 | 126 | 55 | 14.4827
70 | 127 | 55 | 14.532
70 | 128 | 55 | 14.5813
70 | 129 | 55 | 14.6307
70 | 130 | 55 | 14.68
70 | 131 | 55 | 14.7293
70 | 132 | 55 | 14.7787
70 | 133 | 55 | 14.828
70 | 134 | 55 | 14.8773
70 | 135 | 55 | 14.9267
70 | 136 | 55 | 14.976
70 | 137 | 55 | 15.0253
70 | 138 | 55 | 15.0747
70 | 139 | 55 | 15.124
70 | 140 | 55 | 15.1733
70 | 141 | 55 | 15.2227
70 | 142 | 55 | 15.272
70 | 143 | 55 | 15.3213
70 | 144 | 55 | 15.3707
70 | 145 | 55 | 15.42
70 | 146 | 55 | 15.4693
70 | 147 | 55 | 15.5187
70 | 148 | 55 | 15.568
70 | 149 | 55 | 15.6173
70 | 150 | 55 | 15.6667
71 | 45 | 55 | 10.2733
71 | 46 | 55 | 10.3391
71 | 47 | 55 | 10.4049
71 | 48 | 55 | 10.4707
71 | 49 | 55 | 10.5364
71 | 50 | 55 | 10.6022
71 | 51 | 55 | 10.668
71 | 52 | 55 | 10.7338
71 | 53 | 55 | 10.7996
71 | 54 | 55 | 10.8653
71 | 55 | 55 | 10.9311
71 | 56 | 55 | 10.9969
71 | 57 | 55 | 11.0627
71 | 58 | 55 | 11.1284
71 | 59 | 55 | 11.1942
71 | 60 | 55 | 11.26
71 | 61 | 55 | 11.3258
71 | 62 | 55 | 11.3916
71 | 63 | 55 | 11.4573
71 | 64 | 55 | 11.5231
71 | 65 | 55 | 11.5889
71 | 66 | 55 | 11.6547
71 | 67 | 55 | 11.7204
71 | 68 | 55 | 11.7862
71 | 69 | 55 | 11.852
71 | 70 | 55 | 11.9178
71 | 71 | 55 | 11.9836
71 | 72 | 55 | 12.0493
71 | 73 | 55 | 12.1151
71 | 74 | 55 | 12.1809
71 | 75 | 55 | 12.2467
71 | 76 | 55 | 12.3227
71 | 77 | 55 | 12.3987
71 | 78 | 55 | 12.4747
71 | 79 | 55 | 12.5507
71 | 80 | 55 | 12.6267
71 | 81 | 55 | 12.7027
71 | 82 | 55 | 12.7787
71 | 83 | 55 | 12.8547
71 | 84 | 55 | 12.9307
71 | 85 | 55 | 13.0067
71 | 86 | 55 | 13.0827
71 | 87 | 55 | 13.1587
71 | 88 | 55 | 13.2347
71 | 89 | 55 | 13.3107
71 | 90 | 55 | 13.3867
71 | 91 | 55 | 13.4627
71 | 92 | 55 | 13.5387
71 | 93 | 55 | 13.6147
71 | 94 | 55 | 13.6907
71 | 95 | 55 | 13.7667
71 | 96 | 55 | 13.8427
71 | 97 | 55 | 13.9187
71 | 98 | 55 | 13.9947
71 | 99 | 55 | 14.0707
71 | 100 | 55 | 14.1467
71 | 101 | 55 | 14.1587
71 | 102 | 55 | 14.1707
71 | 103 | 55 | 14.1827
71 | 104 | 55 | 14.1947
71 | 105 | 55 | 14.2067
71 | 106 | 55 | 14.2187
71 | 107 | 55 | 14.2307
71 | 108 | 55 | 14.2427
71 | 109 | 55 | 14.2547
71 | 110 | 55 | 14.2667
71 | 111 | 55 | 14.2787
71 | 112 | 55 | 14.2907
71 | 113 | 55 | 14.3027
71 | 114 | 55 | 14.3147
71 | 115 | 55 | 14.3267
71 | 116 | 55 | 14.3387
71 | 117 | 55 | 14.3507
71 | 118 | 55 | 14.3627
71 | 119 | 55 | 14.3747
71 | 120 | 55 | 14.3867
71 | 121 | 55 | 14.3987
71 | 122 | 55 | 14.4107
71 | 123 | 55 | 14.4227
71 | 124 | 55 | 14.4347
71 | 125 | 55 | 14.4467
71 | 126 | 55 | 14.4957
71 | 127 | 55 | 14.5448
71 | 128 | 55 | 14.5939
71 | 129 | 55 | 14.6429
71 | 130 | 55 | 14.692
71 | 131 | 55 | 14.7411
71 | 132 | 55 | 14.7901
71 | 133 | 55 | 14.8392
71 | 134 | 55 | 14.8883
71 | 135 | 55 | 14.9373
71 | 136 | 55 | 14.9864
71 | 137 | 55 | 15.0355
71 | 138 | 55 | 15.0845
71 | 139 | 55 | 15.1336
71 | 140 | 55 | 15.1827
71 | 141 | 55 | 15.2317
71 | 142 | 55 | 15.2808
71 | 143 | 55 | 15.3299
71 | 144 | 55 | 15.3789
71 | 145 | 55 | 15.428
71 | 146 | 55 | 15.4771
71 | 147 | 55 | 15.5261
71 | 148 | 55 | 15.5752
71 | 149 | 55 | 15.6243
71 | 150 | 55 | 15.6733
72 | 45 | 55 | 10.28
72 | 46 | 55 | 10.346
72 | 47 | 55 | 10.412
72 | 48 | 55 | 10.478
72 | 49 | 55 | 10.544
72 | 50 | 55 | 10.61
72 | 51 | 55 | 10.676
72 | 52 | 55 | 10.742
72 | 53 | 55 | 10.808
72 | 54 | 55 | 10.874
72 | 55 | 55 | 10.94
72 | 56 | 55 | 11.006
72 | 57 | 55 | 11.072
72 | 58 | 55 | 11.138
72 | 59 | 55 | 11.204
72 | 60 | 55 | 11.27
72 | 61 | 55 | 11.336
72 | 62 | 55 | 11.402
72 | 63 | 55 | 11.468
72 | 64 | 55 | 11.534
72 | 65 | 55 | 11.6
72 | 66 | 55 | 11.666
72 | 67 | 55 | 11.732
72 | 68 | 55 | 11.798
72 | 69 | 55 | 11.864
72 | 70 | 55 | 11.93
72 | 71 | 55 | 11.996
72 | 72 | 55 | 12.062
72 | 73 | 55 | 12.128
72 | 74 | 55 | 12.194
72 | 75 | 55 | 12.26
72 | 76 | 55 | 12.336
72 | 77 | 55 | 12.412
72 | 78 | 55 | 12.488
72 | 79 | 55 | 12.564
72 | 80 | 55 | 12.64
72 | 81 | 55 | 12.716
72 | 82 | 55 | 12.792
72 | 83 | 55 | 12.868
72 | 84 | 55 | 12.944
72 | 85 | 55 | 13.02
72 | 86 | 55 | 13.096
72 | 87 | 55 | 13.172
72 | 88 | 55 | 13.248
72 | 89 | 55 | 13.324
72 | 90 | 55 | 13.4
72 | 91 | 55 | 13.476
72 | 92 | 55 | 13.552
72 | 93 | 55 | 13.628
72 | 94 | 55 | 13.704
72 | 95 | 55 | 13.78
72 | 96 | 55 | 13.856
72 | 97 | 55 | 13.932
72 | 98 | 55 | 14.008
72 | 99 | 55 | 14.084
72 | 100 | 55 | 14.16
72 | 101 | 55 | 14.172
72 | 102 | 55 | 14.184
72 | 103 | 55 | 14.196
72 | 104 | 55 | 14.208
72 | 105 | 55 | 14.22
72 | 106 | 55 | 14.232
72 | 107 | 55 | 14.244
72 | 108 | 55 | 14.256
72 | 109 | 55 | 14.268
72 | 110 | 55 | 14.28
72 | 111 | 55 | 14.292
72 | 112 | 55 | 14.304
72 | 113 | 55 | 14.316
72 | 114 | 55 | 14.328
72 | 115 | 55 | 14.34
72 | 116 | 55 | 14.352
72 | 117 | 55 | 14.364
72 | 118 | 55 | 14.376
72 | 119 | 55 | 14.388
72 | 120 | 55 | 14.4
72 | 121 | 55 | 14.412
72 | 122 | 55 | 14.424
72 | 123 | 55 | 14.436
72 | 124 | 55 | 14.448
72 | 125 | 55 | 14.46
72 | 126 | 55 | 14.5088
72 | 127 | 55 | 14.5576
72 | 128 | 55 | 14.6064
72 | 129 | 55 | 14.6552
72 | 130 | 55 | 14.704
72 | 131 | 55 | 14.7528
72 | 132 | 55 | 14.8016
72 | 133 | 55 | 14.8504
72 | 134 | 55 | 14.8992
72 | 135 | 55 | 14.948
72 | 136 | 55 | 14.9968
72 | 137 | 55 | 15.0456
72 | 138 | 55 | 15.0944
72 | 139 | 55 | 15.1432
72 | 140 | 55 | 15.192
72 | 141 | 55 | 15.2408
72 | 142 | 55 | 15.2896
72 | 143 | 55 | 15.3384
72 | 144 | 55 | 15.3872
72 | 145 | 55 | 15.436
72 | 146 | 55 | 15.4848
72 | 147 | 55 | 15.5336
72 | 148 | 55 | 15.5824
72 | 149 | 55 | 15.6312
72 | 150 | 55 | 15.68
73 | 45 | 55 | 10.2867
73 | 46 | 55 | 10.3529
73 | 47 | 55 | 10.4191
73 | 48 | 55 | 10.4853
73 | 49 | 55 | 10.5516
73 | 50 | 55 | 10.6178
73 | 51 | 55 | 10.684
73 | 52 | 55 | 10.7502
73 | 53 | 55 | 10.8164
73 | 54 | 55 | 10.8827
73 | 55 | 55 | 10.9489
73 | 56 | 55 | 11.0151
73 | 57 | 55 | 11.0813
73 | 58 | 55 | 11.1476
73 | 59 | 55 | 11.2138
73 | 60 | 55 | 11.28
73 | 61 | 55 | 11.3462
73 | 62 | 55 | 11.4124
73 | 63 | 55 | 11.4787
73 | 64 | 55 | 11.5449
73 | 65 | 55 | 11.6111
73 | 66 | 55 | 11.6773
73 | 67 | 55 | 11.7436
73 | 68 | 55 | 11.8098
73 | 69 | 55 | 11.876
73 | 70 | 55 | 11.9422
73 | 71 | 55 | 12.0084
73 | 72 | 55 | 12.0747
73 | 73 | 55 | 12.1409
73 | 74 | 55 | 12.2071
73 | 75 | 55 | 12.2733
73 | 76 | 55 | 12.3493
73 | 77 | 55 | 12.4253
73 | 78 | 55 | 12.5013
73 | 79 | 55 | 12.5773
73 | 80 | 55 | 12.6533
73 | 81 | 55 | 12.7293
73 | 82 | 55 | 12.8053
73 | 83 | 55 | 12.8813
73 | 84 | 55 | 12.9573
73 | 85 | 55 | 13.0333
73 | 86 | 55 | 13.1093
73 | 87 | 55 | 13.1853
73 | 88 | 55 | 13.2613
73 | 89 | 55 | 13.3373
73 | 90 | 55 | 13.4133
73 | 91 | 55 | 13.4893
73 | 92 | 55 | 13.5653
73 | 93 | 55 | 13.6413
73 | 94 | 55 | 13.7173
73 | 95 | 55 | 13.7933
73 | 96 | 55 | 13.8693
73 | 97 | 55 | 13.9453
73 | 98 | 55 | 14.0213
73 | 99 | 55 | 14.0973
73 | 100 | 55 | 14.1733
73 | 101 | 55 | 14.1853
73 | 102 | 55 | 14.1973
73 | 103 | 55 | 14.2093
73 | 104 | 55 | 14.2213
73 | 105 | 55 | 14.2333
73 | 106 | 55 | 14.2453
73 | 107 | 55 | 14.2573
73 | 108 | 55 | 14.2693
73 | 109 | 55 | 14.2813
73 | 110 | 55 | 14.2933
73 | 111 | 55 | 14.3053
73 | 112 | 55 | 14.3173
73 | 113 | 55 | 14.3293
73 | 114 | 55 | 14.3413
73 | 115 | 55 | 14.3533
73 | 116 | 55 | 14.3653
73 | 117 | 55 | 14.3773
73 | 118 | 55 | 14.3893
73 | 119 | 55 | 14.4013
73 | 120 | 55 | 14.4133
73 | 121 | 55 | 14.4253
73 | 122 | 55 | 14.4373
73 | 123 | 55 | 14.4493
73 | 124 | 55 | 14.4613
73 | 125 | 55 | 14.4733
73 | 126 | 55 | 14.5219
73 | 127 | 55 | 14.5704
73 | 128 | 55 | 14.6189
73 | 129 | 55 | 14.6675
73 | 130 | 55 | 14.716
73 | 131 | 55 | 14.7645
73 | 132 | 55 | 14.8131
73 | 133 | 55 | 14.8616
73 | 134 | 55 | 14.9101
73 | 135 | 55 | 14.9587
73 | 136 | 55 | 15.0072
73 | 137 | 55 | 15.0557
73 | 138 | 55 | 15.1043
73 | 139 | 55 | 15.1528
73 | 140 | 55 | 15.2013
73 | 141 | 55 | 15.2499
73 | 142 | 55 | 15.2984
73 | 143 | 55 | 15.3469
73 | 144 | 55 | 15.3955
73 | 145 | 55 | 15.444
73 | 146 | 55 | 15.4925
73 | 147 | 55 | 15.5411
73 | 148 | 55 | 15.5896
73 | 149 | 55 | 15.6381
73 | 150 | 55 | 15.6867
74 | 45 | 55 | 10.2933
74 | 46 | 55 | 10.3598
74 | 47 | 55 | 10.4262
74 | 48 | 55 | 10.4927
74 | 49 | 55 | 10.5591
74 | 50 | 55 | 10.6256
74 | 51 | 55 | 10.692
74 | 52 | 55 | 10.7584
74 | 53 | 55 | 10.8249
74 | 54 | 55 | 10.8913
74 | 55 | 55 | 10.9578
74 | 56 | 55 | 11.0242
74 | 57 | 55 | 11.0907
74 | 58 | 55 | 11.1571
74 | 59 | 55 | 11.2236
74 | 60 | 55 | 11.29
74 | 61 | 55 | 11.3564
74 | 62 | 55 | 11.4229
74 | 63 | 55 | 11.4893
74 | 64 | 55 | 11.5558
74 | 65 | 55 | 11.6222
74 | 66 | 55 | 11.6887
74 | 67 | 55 | 11.7551
74 | 68 | 55 | 11.8216
74 | 69 | 55 | 11.888
74 | 70 | 55 | 11.9544
74 | 71 | 55 | 12.0209
74 | 72 | 55 | 12.0873
74 | 73 | 55 | 12.1538
74 | 74 | 55 | 12.2202
74 | 75 | 55 | 12.2867
74 | 76 | 55 | 12.3627
74 | 77 | 55 | 12.4387
74 | 78 | 55 | 12.5147
74 | 79 | 55 | 12.5907
74 | 80 | 55 | 12.6667
74 | 81 | 55 | 12.7427
74 | 82 | 55 | 12.8187
74 | 83 | 55 | 12.8947
74 | 84 | 55 | 12.9707
74 | 85 | 55 | 13.0467
74 | 86 | 55 | 13.1227
74 | 87 | 55 | 13.1987
74 | 88 | 55 | 13.2747
74 | 89 | 55 | 13.3507
74 | 90 | 55 | 13.4267
74 | 91 | 55 | 13.5027
74 | 92 | 55 | 13.5787
74 | 93 | 55 | 13.6547
74 | 94 | 55 | 13.7307
74 | 95 | 55 | 13.8067
74 | 96 | 55 | 13.8827
74 | 97 | 55 | 13.9587
74 | 98 | 55 | 14.0347
74 | 99 | 55 | 14.1107
74 | 100 | 55 | 14.1867
74 | 101 | 55 | 14.1987
74 | 102 | 55 | 14.2107
74 | 103 | 55 | 14.2227
74 | 104 | 55 | 14.2347
74 | 105 | 55 | 14.2467
74 | 106 | 55 | 14.2587
74 | 107 | 55 | 14.2707
74 | 108 | 55 | 14.2827
74 | 109 | 55 | 14.2947
74 | 110 | 55 | 14.3067
74 | 111 | 55 | 14.3187
74 | 112 | 55 | 14.3307
74 | 113 | 55 | 14.3427
74 | 114 | 55 | 14.3547
74 | 115 | 55 | 14.3667
74 | 116 | 55 | 14.3787
74 | 117 | 55 | 14.3907
74 | 118 | 55 | 14.4027
74 | 119 | 55 | 14.4147
74 | 120 | 55 | 14.4267
74 | 121 | 55 | 14.4387
74 | 122 | 55 | 14.4507
74 | 123 | 55 | 14.4627
74 | 124 | 55 | 14.4747
74 | 125 | 55 | 14.4867
74 | 126 | 55 | 14.5349
74 | 127 | 55 | 14.5832
74 | 128 | 55 | 14.6315
74 | 129 | 55 | 14.6797
74 | 130 | 55 | 14.728
74 | 131 | 55 | 14.7763
74 | 132 | 55 | 14.8245
74 | 133 | 55 | 14.8728
74 | 134 | 55 | 14.9211
74 | 135 | 55 | 14.9693
74 | 136 | 55 | 15.0176
74 | 137 | 55 | 15.0659
74 | 138 | 55 | 15.1141
74 | 139 | 55 | 15.1624
74 | 140 | 55 | 15.2107
74 | 141 | 55 | 15.2589
74 | 142 | 55 | 15.3072
74 | 143 | 55 | 15.3555
74 | 144 | 55 | 15.4037
74 | 145 | 55 | 15.452
74 | 146 | 55 | 15.5003
74 | 147 | 55 | 15.5485
74 | 148 | 55 | 15.5968
74 | 149 | 55 | 15.6451
74 | 150 | 55 | 15.6933
75 | 45 | 55 | 10.3
75 | 46 | 55 | 10.3667
75 | 47 | 55 | 10.4333
75 | 48 | 55 | 10.5
75 | 49 | 55 | 10.5667
75 | 50 | 55 | 10.6333
75 | 51 | 55 | 10.7
75 | 52 | 55 | 10.7667
75 | 53 | 55 | 10.8333
75 | 54 | 55 | 10.9
75 | 55 | 55 | 10.9667
75 | 56 | 55 | 11.0333
75 | 57 | 55 | 11.1
75 | 58 | 55 | 11.1667
75 | 59 | 55 | 11.2333
75 | 60 | 55 | 11.3
75 | 61 | 55 | 11.3667
75 | 62 | 55 | 11.4333
75 | 63 | 55 | 11.5
75 | 64 | 55 | 11.5667
75 | 65 | 55 | 11.6333
75 | 66 | 55 | 11.7
75 | 67 | 55 | 11.7667
75 | 68 | 55 | 11.8333
75 | 69 | 55 | 11.9
75 | 70 | 55 | 11.9667
75 | 71 | 55 | 12.0333
75 | 72 | 55 | 12.1
75 | 73 | 55 | 12.1667
75 | 74 | 55 | 12.2333
75 | 75 | 55 | 12.3
75 | 76 | 55 | 12.376
75 | 77 | 55 | 12.452
75 | 78 | 55 | 12.528
75 | 79 | 55 | 12.604
75 | 80 | 55 | 12.68
75 | 81 | 55 | 12.756
75 | 82 | 55 | 12.832
75 | 83 | 55 | 12.908
75 | 84 | 55 | 12.984
75 | 85 | 55 | 13.06
75 | 86 | 55 | 13.136
75 | 87 | 55 | 13.212
75 | 88 | 55 | 13.288
75 | 89 | 55 | 13.364
75 | 90 | 55 | 13.44
75 | 91 | 55 | 13.516
75 | 92 | 55 | 13.592
75 | 93 | 55 | 13.668
75 | 94 | 55 | 13.744
75 | 95 | 55 | 13.82
75 | 96 | 55 | 13.896
75 | 97 | 55 | 13.972
75 | 98 | 55 | 14.048
75 | 99 | 55 | 14.124
75 | 100 | 55 | 14.2
75 | 101 | 55 | 14.212
75 | 102 | 55 | 14.224
75 | 103 | 55 | 14.236
75 | 104 | 55 | 14.248
75 | 105 | 55 | 14.26
75 | 106 | 55 | 14.272
75 | 107 | 55 | 14.284
75 | 108 | 55 | 14.296
75 | 109 | 55 | 14.308
75 | 110 | 55 | 14.32
75 | 111 | 55 | 14.332
75 | 112 | 55 | 14.344
75 | 113 | 55 | 14.356
75 | 114 | 55 | 14.368
75 | 115 | 55 | 14.38
75 | 116 | 55 | 14.392
75 | 117 | 55 | 14.404
75 | 118 | 55 | 14.416
75 | 119 | 55 | 14.428
75 | 120 | 55 | 14.44
75 | 121 | 55 | 14.452
75 | 122 | 55 | 14.464
75 | 123 | 55 | 14.476
75 | 124 | 55 | 14.488
75 | 125 | 55 | 14.5
75 | 126 | 55 | 14.548
75 | 127 | 55 | 14.596
75 | 128 | 55 | 14.644
75 | 129 | 55 | 14.692
75 | 130 | 55 | 14.74
75 | 131 | 55 | 14.788
75 | 132 | 55 | 14.836
75 | 133 | 55 | 14.884
75 | 134 | 55 | 14.932
75 | 135 | 55 | 14.98
75 | 136 | 55 | 15.028
75 | 137 | 55 | 15.076
75 | 138 | 55 | 15.124
75 | 139 | 55 | 15.172
75 | 140 | 55 | 15.22
75 | 141 | 55 | 15.268
75 | 142 | 55 | 15.316
75 | 143 | 55 | 15.364
75 | 144 | 55 | 15.412
75 | 145 | 55 | 15.46
75 | 146 | 55 | 15.508
75 | 147 | 55 | 15.556
75 | 148 | 55 | 15.604
75 | 149 | 55 | 15.652
75 | 150 | 55 | 15.7
30 | 45 | 100 | 6.5
30 | 46 | 100 | 6.55
30 | 47 | 100 | 6.6
30 | 48 | 100 | 6.65
30 | 49 | 100 | 6.7
30 | 50 | 100 | 6.75
30 | 51 | 100 | 6.8
30 | 52 | 100 | 6.85
30 | 53 | 100 | 6.9
30 | 54 | 100 | 6.95
30 | 55 | 100 | 7
30 | 56 | 100 | 7.05
30 | 57 | 100 | 7.1
30 | 58 | 100 | 7.15
30 | 59 | 100 | 7.2
30 | 60 | 100 | 7.25
30 | 61 | 100 | 7.3
30 | 62 | 100 | 7.35
30 | 63 | 100 | 7.4
30 | 64 | 100 | 7.45
30 | 65 | 100 | 7.5
30 | 66 | 100 | 7.55
30 | 67 | 100 | 7.6
30 | 68 | 100 | 7.65
30 | 69 | 100 | 7.7
30 | 70 | 100 | 7.75
30 | 71 | 100 | 7.8
30 | 72 | 100 | 7.85
30 | 73 | 100 | 7.9
30 | 74 | 100 | 7.95
30 | 75 | 100 | 8
30 | 76 | 100 | 8.02
30 | 77 | 100 | 8.04
30 | 78 | 100 | 8.06
30 | 79 | 100 | 8.08
30 | 80 | 100 | 8.1
30 | 81 | 100 | 8.12
30 | 82 | 100 | 8.14
30 | 83 | 100 | 8.16
30 | 84 | 100 | 8.18
30 | 85 | 100 | 8.2
30 | 86 | 100 | 8.22
30 | 87 | 100 | 8.24
30 | 88 | 100 | 8.26
30 | 89 | 100 | 8.28
30 | 90 | 100 | 8.3
30 | 91 | 100 | 8.32
30 | 92 | 100 | 8.34
30 | 93 | 100 | 8.36
30 | 94 | 100 | 8.38
30 | 95 | 100 | 8.4
30 | 96 | 100 | 8.42
30 | 97 | 100 | 8.44
30 | 98 | 100 | 8.46
30 | 99 | 100 | 8.48
30 | 100 | 100 | 8.5
30 | 101 | 100 | 8.536
30 | 102 | 100 | 8.572
30 | 103 | 100 | 8.608
30 | 104 | 100 | 8.644
30 | 105 | 100 | 8.68
30 | 106 | 100 | 8.716
30 | 107 | 100 | 8.752
30 | 108 | 100 | 8.788
30 | 109 | 100 | 8.824
30 | 110 | 100 | 8.86
30 | 111 | 100 | 8.896
30 | 112 | 100 | 8.932
30 | 113 | 100 | 8.968
30 | 114 | 100 | 9.004
30 | 115 | 100 | 9.04
30 | 116 | 100 | 9.076
30 | 117 | 100 | 9.112
30 | 118 | 100 | 9.148
30 | 119 | 100 | 9.184
30 | 120 | 100 | 9.22
30 | 121 | 100 | 9.256
30 | 122 | 100 | 9.292
30 | 123 | 100 | 9.328
30 | 124 | 100 | 9.364
30 | 125 | 100 | 9.4
30 | 126 | 100 | 9.432
30 | 127 | 100 | 9.464
30 | 128 | 100 | 9.496
30 | 129 | 100 | 9.528
30 | 130 | 100 | 9.56
30 | 131 | 100 | 9.592
30 | 132 | 100 | 9.624
30 | 133 | 100 | 9.656
30 | 134 | 100 | 9.688
30 | 135 | 100 | 9.72
30 | 136 | 100 | 9.752
30 | 137 | 100 | 9.784
30 | 138 | 100 | 9.816
30 | 139 | 100 | 9.848
30 | 140 | 100 | 9.88
30 | 141 | 100 | 9.912
30 | 142 | 100 | 9.944
30 | 143 | 100 | 9.976
30 | 144 | 100 | 10.008
30 | 145 | 100 | 10.04
30 | 146 | 100 | 10.072
30 | 147 | 100 | 10.104
30 | 148 | 100 | 10.136
30 | 149 | 100 | 10.168
30 | 150 | 100 | 10.2
31 | 45 | 100 | 6.5
31 | 46 | 100 | 6.5504
31 | 47 | 100 | 6.6009
31 | 48 | 100 | 6.6513
31 | 49 | 100 | 6.7018
31 | 50 | 100 | 6.7522
31 | 51 | 100 | 6.8027
31 | 52 | 100 | 6.8531
31 | 53 | 100 | 6.9036
31 | 54 | 100 | 6.954
31 | 55 | 100 | 7.0044
31 | 56 | 100 | 7.0549
31 | 57 | 100 | 7.1053
31 | 58 | 100 | 7.1558
31 | 59 | 100 | 7.2062
31 | 60 | 100 | 7.2567
31 | 61 | 100 | 7.3071
31 | 62 | 100 | 7.3576
31 | 63 | 100 | 7.408
31 | 64 | 100 | 7.4584
31 | 65 | 100 | 7.5089
31 | 66 | 100 | 7.5593
31 | 67 | 100 | 7.6098
31 | 68 | 100 | 7.6602
31 | 69 | 100 | 7.7107
31 | 70 | 100 | 7.7611
31 | 71 | 100 | 7.8116
31 | 72 | 100 | 7.862
31 | 73 | 100 | 7.9124
31 | 74 | 100 | 7.9629
31 | 75 | 100 | 8.0133
31 | 76 | 100 | 8.0341
31 | 77 | 100 | 8.0549
31 | 78 | 100 | 8.0757
31 | 79 | 100 | 8.0965
31 | 80 | 100 | 8.1173
31 | 81 | 100 | 8.1381
31 | 82 | 100 | 8.1589
31 | 83 | 100 | 8.1797
31 | 84 | 100 | 8.2005
31 | 85 | 100 | 8.2213
31 | 86 | 100 | 8.2421
31 | 87 | 100 | 8.2629
31 | 88 | 100 | 8.2837
31 | 89 | 100 | 8.3045
31 | 90 | 100 | 8.3253
31 | 91 | 100 | 8.3461
31 | 92 | 100 | 8.3669
31 | 93 | 100 | 8.3877
31 | 94 | 100 | 8.4085
31 | 95 | 100 | 8.4293
31 | 96 | 100 | 8.4501
31 | 97 | 100 | 8.4709
31 | 98 | 100 | 8.4917
31 | 99 | 100 | 8.5125
31 | 100 | 100 | 8.5333
31 | 101 | 100 | 8.5685
31 | 102 | 100 | 8.6037
31 | 103 | 100 | 8.6389
31 | 104 | 100 | 8.6741
31 | 105 | 100 | 8.7093
31 | 106 | 100 | 8.7445
31 | 107 | 100 | 8.7797
31 | 108 | 100 | 8.8149
31 | 109 | 100 | 8.8501
31 | 110 | 100 | 8.8853
31 | 111 | 100 | 8.9205
31 | 112 | 100 | 8.9557
31 | 113 | 100 | 8.9909
31 | 114 | 100 | 9.0261
31 | 115 | 100 | 9.0613
31 | 116 | 100 | 9.0965
31 | 117 | 100 | 9.1317
31 | 118 | 100 | 9.1669
31 | 119 | 100 | 9.2021
31 | 120 | 100 | 9.2373
31 | 121 | 100 | 9.2725
31 | 122 | 100 | 9.3077
31 | 123 | 100 | 9.3429
31 | 124 | 100 | 9.3781
31 | 125 | 100 | 9.4133
31 | 126 | 100 | 9.4456
31 | 127 | 100 | 9.4779
31 | 128 | 100 | 9.5101
31 | 129 | 100 | 9.5424
31 | 130 | 100 | 9.5747
31 | 131 | 100 | 9.6069
31 | 132 | 100 | 9.6392
31 | 133 | 100 | 9.6715
31 | 134 | 100 | 9.7037
31 | 135 | 100 | 9.736
31 | 136 | 100 | 9.7683
31 | 137 | 100 | 9.8005
31 | 138 | 100 | 9.8328
31 | 139 | 100 | 9.8651
31 | 140 | 100 | 9.8973
31 | 141 | 100 | 9.9296
31 | 142 | 100 | 9.9619
31 | 143 | 100 | 9.9941
31 | 144 | 100 | 10.0264
31 | 145 | 100 | 10.0587
31 | 146 | 100 | 10.0909
31 | 147 | 100 | 10.1232
31 | 148 | 100 | 10.1555
31 | 149 | 100 | 10.1877
31 | 150 | 100 | 10.22
32 | 45 | 100 | 6.5
32 | 46 | 100 | 6.5509
32 | 47 | 100 | 6.6018
32 | 48 | 100 | 6.6527
32 | 49 | 100 | 6.7036
32 | 50 | 100 | 6.7544
32 | 51 | 100 | 6.8053
32 | 52 | 100 | 6.8562
32 | 53 | 100 | 6.9071
32 | 54 | 100 | 6.958
32 | 55 | 100 | 7.0089
32 | 56 | 100 | 7.0598
32 | 57 | 100 | 7.1107
32 | 58 | 100 | 7.1616
32 | 59 | 100 | 7.2124
32 | 60 | 100 | 7.2633
32 | 61 | 100 | 7.3142
32 | 62 | 100 | 7.3651
32 | 63 | 100 | 7.416
32 | 64 | 100 | 7.4669
32 | 65 | 100 | 7.5178
32 | 66 | 100 | 7.5687
32 | 67 | 100 | 7.6196
32 | 68 | 100 | 7.6704
32 | 69 | 100 | 7.7213
32 | 70 | 100 | 7.7722
32 | 71 | 100 | 7.8231
32 | 72 | 100 | 7.874
32 | 73 | 100 | 7.9249
32 | 74 | 100 | 7.9758
32 | 75 | 100 | 8.0267
32 | 76 | 100 | 8.0483
32 | 77 | 100 | 8.0699
32 | 78 | 100 | 8.0915
32 | 79 | 100 | 8.1131
32 | 80 | 100 | 8.1347
32 | 81 | 100 | 8.1563
32 | 82 | 100 | 8.1779
32 | 83 | 100 | 8.1995
32 | 84 | 100 | 8.2211
32 | 85 | 100 | 8.2427
32 | 86 | 100 | 8.2643
32 | 87 | 100 | 8.2859
32 | 88 | 100 | 8.3075
32 | 89 | 100 | 8.3291
32 | 90 | 100 | 8.3507
32 | 91 | 100 | 8.3723
32 | 92 | 100 | 8.3939
32 | 93 | 100 | 8.4155
32 | 94 | 100 | 8.4371
32 | 95 | 100 | 8.4587
32 | 96 | 100 | 8.4803
32 | 97 | 100 | 8.5019
32 | 98 | 100 | 8.5235
32 | 99 | 100 | 8.5451
32 | 100 | 100 | 8.5667
32 | 101 | 100 | 8.6011
32 | 102 | 100 | 8.6355
32 | 103 | 100 | 8.6699
32 | 104 | 100 | 8.7043
32 | 105 | 100 | 8.7387
32 | 106 | 100 | 8.7731
32 | 107 | 100 | 8.8075
32 | 108 | 100 | 8.8419
32 | 109 | 100 | 8.8763
32 | 110 | 100 | 8.9107
32 | 111 | 100 | 8.9451
32 | 112 | 100 | 8.9795
32 | 113 | 100 | 9.0139
32 | 114 | 100 | 9.0483
32 | 115 | 100 | 9.0827
32 | 116 | 100 | 9.1171
32 | 117 | 100 | 9.1515
32 | 118 | 100 | 9.1859
32 | 119 | 100 | 9.2203
32 | 120 | 100 | 9.2547
32 | 121 | 100 | 9.2891
32 | 122 | 100 | 9.3235
32 | 123 | 100 | 9.3579
32 | 124 | 100 | 9.3923
32 | 125 | 100 | 9.4267
32 | 126 | 100 | 9.4592
32 | 127 | 100 | 9.4917
32 | 128 | 100 | 9.5243
32 | 129 | 100 | 9.5568
32 | 130 | 100 | 9.5893
32 | 131 | 100 | 9.6219
32 | 132 | 100 | 9.6544
32 | 133 | 100 | 9.6869
32 | 134 | 100 | 9.7195
32 | 135 | 100 | 9.752
32 | 136 | 100 | 9.7845
32 | 137 | 100 | 9.8171
32 | 138 | 100 | 9.8496
32 | 139 | 100 | 9.8821
32 | 140 | 100 | 9.9147
32 | 141 | 100 | 9.9472
32 | 142 | 100 | 9.9797
32 | 143 | 100 | 10.0123
32 | 144 | 100 | 10.0448
32 | 145 | 100 | 10.0773
32 | 146 | 100 | 10.1099
32 | 147 | 100 | 10.1424
32 | 148 | 100 | 10.1749
32 | 149 | 100 | 10.2075
32 | 150 | 100 | 10.24
33 | 45 | 100 | 6.5
33 | 46 | 100 | 6.5513
33 | 47 | 100 | 6.6027
33 | 48 | 100 | 6.654
33 | 49 | 100 | 6.7053
33 | 50 | 100 | 6.7567
33 | 51 | 100 | 6.808
33 | 52 | 100 | 6.8593
33 | 53 | 100 | 6.9107
33 | 54 | 100 | 6.962
33 | 55 | 100 | 7.0133
33 | 56 | 100 | 7.0647
33 | 57 | 100 | 7.116
33 | 58 | 100 | 7.1673
33 | 59 | 100 | 7.2187
33 | 60 | 100 | 7.27
33 | 61 | 100 | 7.3213
33 | 62 | 100 | 7.3727
33 | 63 | 100 | 7.424
33 | 64 | 100 | 7.4753
33 | 65 | 100 | 7.5267
33 | 66 | 100 | 7.578
33 | 67 | 100 | 7.6293
33 | 68 | 100 | 7.6807
33 | 69 | 100 | 7.732
33 | 70 | 100 | 7.7833
33 | 71 | 100 | 7.8347
33 | 72 | 100 | 7.886
33 | 73 | 100 | 7.9373
33 | 74 | 100 | 7.9887
33 | 75 | 100 | 8.04
33 | 76 | 100 | 8.0624
33 | 77 | 100 | 8.0848
33 | 78 | 100 | 8.1072
33 | 79 | 100 | 8.1296
33 | 80 | 100 | 8.152
33 | 81 | 100 | 8.1744
33 | 82 | 100 | 8.1968
33 | 83 | 100 | 8.2192
33 | 84 | 100 | 8.2416
33 | 85 | 100 | 8.264
33 | 86 | 100 | 8.2864
33 | 87 | 100 | 8.3088
33 | 88 | 100 | 8.3312
33 | 89 | 100 | 8.3536
33 | 90 | 100 | 8.376
33 | 91 | 100 | 8.3984
33 | 92 | 100 | 8.4208
33 | 93 | 100 | 8.4432
33 | 94 | 100 | 8.4656
33 | 95 | 100 | 8.488
33 | 96 | 100 | 8.5104
33 | 97 | 100 | 8.5328
33 | 98 | 100 | 8.5552
33 | 99 | 100 | 8.5776
33 | 100 | 100 | 8.6
33 | 101 | 100 | 8.6336
33 | 102 | 100 | 8.6672
33 | 103 | 100 | 8.7008
33 | 104 | 100 | 8.7344
33 | 105 | 100 | 8.768
33 | 106 | 100 | 8.8016
33 | 107 | 100 | 8.8352
33 | 108 | 100 | 8.8688
33 | 109 | 100 | 8.9024
33 | 110 | 100 | 8.936
33 | 111 | 100 | 8.9696
33 | 112 | 100 | 9.0032
33 | 113 | 100 | 9.0368
33 | 114 | 100 | 9.0704
33 | 115 | 100 | 9.104
33 | 116 | 100 | 9.1376
33 | 117 | 100 | 9.1712
33 | 118 | 100 | 9.2048
33 | 119 | 100 | 9.2384
33 | 120 | 100 | 9.272
33 | 121 | 100 | 9.3056
33 | 122 | 100 | 9.3392
33 | 123 | 100 | 9.3728
33 | 124 | 100 | 9.4064
33 | 125 | 100 | 9.44
33 | 126 | 100 | 9.4728
33 | 127 | 100 | 9.5056
33 | 128 | 100 | 9.5384
33 | 129 | 100 | 9.5712
33 | 130 | 100 | 9.604
33 | 131 | 100 | 9.6368
33 | 132 | 100 | 9.6696
33 | 133 | 100 | 9.7024
33 | 134 | 100 | 9.7352
33 | 135 | 100 | 9.768
33 | 136 | 100 | 9.8008
33 | 137 | 100 | 9.8336
33 | 138 | 100 | 9.8664
33 | 139 | 100 | 9.8992
33 | 140 | 100 | 9.932
33 | 141 | 100 | 9.9648
33 | 142 | 100 | 9.9976
33 | 143 | 100 | 10.0304
33 | 144 | 100 | 10.0632
33 | 145 | 100 | 10.096
33 | 146 | 100 | 10.1288
33 | 147 | 100 | 10.1616
33 | 148 | 100 | 10.1944
33 | 149 | 100 | 10.2272
33 | 150 | 100 | 10.26
34 | 45 | 100 | 6.5
34 | 46 | 100 | 6.5518
34 | 47 | 100 | 6.6036
34 | 48 | 100 | 6.6553
34 | 49 | 100 | 6.7071
34 | 50 | 100 | 6.7589
34 | 51 | 100 | 6.8107
34 | 52 | 100 | 6.8624
34 | 53 | 100 | 6.9142
34 | 54 | 100 | 6.966
34 | 55 | 100 | 7.0178
34 | 56 | 100 | 7.0696
34 | 57 | 100 | 7.1213
34 | 58 | 100 | 7.1731
34 | 59 | 100 | 7.2249
34 | 60 | 100 | 7.2767
34 | 61 | 100 | 7.3284
34 | 62 | 100 | 7.3802
34 | 63 | 100 | 7.432
34 | 64 | 100 | 7.4838
34 | 65 | 100 | 7.5356
34 | 66 | 100 | 7.5873
34 | 67 | 100 | 7.6391
34 | 68 | 100 | 7.6909
34 | 69 | 100 | 7.7427
34 | 70 | 100 | 7.7944
34 | 71 | 100 | 7.8462
34 | 72 | 100 | 7.898
34 | 73 | 100 | 7.9498
34 | 74 | 100 | 8.0016
34 | 75 | 100 | 8.0533
34 | 76 | 100 | 8.0765
34 | 77 | 100 | 8.0997
34 | 78 | 100 | 8.1229
34 | 79 | 100 | 8.1461
34 | 80 | 100 | 8.1693
34 | 81 | 100 | 8.1925
34 | 82 | 100 | 8.2157
34 | 83 | 100 | 8.2389
34 | 84 | 100 | 8.2621
34 | 85 | 100 | 8.2853
34 | 86 | 100 | 8.3085
34 | 87 | 100 | 8.3317
34 | 88 | 100 | 8.3549
34 | 89 | 100 | 8.3781
34 | 90 | 100 | 8.4013
34 | 91 | 100 | 8.4245
34 | 92 | 100 | 8.4477
34 | 93 | 100 | 8.4709
34 | 94 | 100 | 8.4941
34 | 95 | 100 | 8.5173
34 | 96 | 100 | 8.5405
34 | 97 | 100 | 8.5637
34 | 98 | 100 | 8.5869
34 | 99 | 100 | 8.6101
34 | 100 | 100 | 8.6333
34 | 101 | 100 | 8.6661
34 | 102 | 100 | 8.6989
34 | 103 | 100 | 8.7317
34 | 104 | 100 | 8.7645
34 | 105 | 100 | 8.7973
34 | 106 | 100 | 8.8301
34 | 107 | 100 | 8.8629
34 | 108 | 100 | 8.8957
34 | 109 | 100 | 8.9285
34 | 110 | 100 | 8.9613
34 | 111 | 100 | 8.9941
34 | 112 | 100 | 9.0269
34 | 113 | 100 | 9.0597
34 | 114 | 100 | 9.0925
34 | 115 | 100 | 9.1253
34 | 116 | 100 | 9.1581
34 | 117 | 100 | 9.1909
34 | 118 | 100 | 9.2237
34 | 119 | 100 | 9.2565
34 | 120 | 100 | 9.2893
34 | 121 | 100 | 9.3221
34 | 122 | 100 | 9.3549
34 | 123 | 100 | 9.3877
34 | 124 | 100 | 9.4205
34 | 125 | 100 | 9.4533
34 | 126 | 100 | 9.4864
34 | 127 | 100 | 9.5195
34 | 128 | 100 | 9.5525
34 | 129 | 100 | 9.5856
34 | 130 | 100 | 9.6187
34 | 131 | 100 | 9.6517
34 | 132 | 100 | 9.6848
34 | 133 | 100 | 9.7179
34 | 134 | 100 | 9.7509
34 | 135 | 100 | 9.784
34 | 136 | 100 | 9.8171
34 | 137 | 100 | 9.8501
34 | 138 | 100 | 9.8832
34 | 139 | 100 | 9.9163
34 | 140 | 100 | 9.9493
34 | 141 | 100 | 9.9824
34 | 142 | 100 | 10.0155
34 | 143 | 100 | 10.0485
34 | 144 | 100 | 10.0816
34 | 145 | 100 | 10.1147
34 | 146 | 100 | 10.1477
34 | 147 | 100 | 10.1808
34 | 148 | 100 | 10.2139
34 | 149 | 100 | 10.2469
34 | 150 | 100 | 10.28
35 | 45 | 100 | 6.5
35 | 46 | 100 | 6.5522
35 | 47 | 100 | 6.6044
35 | 48 | 100 | 6.6567
35 | 49 | 100 | 6.7089
35 | 50 | 100 | 6.7611
35 | 51 | 100 | 6.8133
35 | 52 | 100 | 6.8656
35 | 53 | 100 | 6.9178
35 | 54 | 100 | 6.97
35 | 55 | 100 | 7.0222
35 | 56 | 100 | 7.0744
35 | 57 | 100 | 7.1267
35 | 58 | 100 | 7.1789
35 | 59 | 100 | 7.2311
35 | 60 | 100 | 7.2833
35 | 61 | 100 | 7.3356
35 | 62 | 100 | 7.3878
35 | 63 | 100 | 7.44
35 | 64 | 100 | 7.4922
35 | 65 | 100 | 7.5444
35 | 66 | 100 | 7.5967
35 | 67 | 100 | 7.6489
35 | 68 | 100 | 7.7011
35 | 69 | 100 | 7.7533
35 | 70 | 100 | 7.8056
35 | 71 | 100 | 7.8578
35 | 72 | 100 | 7.91
35 | 73 | 100 | 7.9622
35 | 74 | 100 | 8.0144
35 | 75 | 100 | 8.0667
35 | 76 | 100 | 8.0907
35 | 77 | 100 | 8.1147
35 | 78 | 100 | 8.1387
35 | 79 | 100 | 8.1627
35 | 80 | 100 | 8.1867
35 | 81 | 100 | 8.2107
35 | 82 | 100 | 8.2347
35 | 83 | 100 | 8.2587
35 | 84 | 100 | 8.2827
35 | 85 | 100 | 8.3067
35 | 86 | 100 | 8.3307
35 | 87 | 100 | 8.3547
35 | 88 | 100 | 8.3787
35 | 89 | 100 | 8.4027
35 | 90 | 100 | 8.4267
35 | 91 | 100 | 8.4507
35 | 92 | 100 | 8.4747
35 | 93 | 100 | 8.4987
35 | 94 | 100 | 8.5227
35 | 95 | 100 | 8.5467
35 | 96 | 100 | 8.5707
35 | 97 | 100 | 8.5947
35 | 98 | 100 | 8.6187
35 | 99 | 100 | 8.6427
35 | 100 | 100 | 8.6667
35 | 101 | 100 | 8.6987
35 | 102 | 100 | 8.7307
35 | 103 | 100 | 8.7627
35 | 104 | 100 | 8.7947
35 | 105 | 100 | 8.8267
35 | 106 | 100 | 8.8587
35 | 107 | 100 | 8.8907
35 | 108 | 100 | 8.9227
35 | 109 | 100 | 8.9547
35 | 110 | 100 | 8.9867
35 | 111 | 100 | 9.0187
35 | 112 | 100 | 9.0507
35 | 113 | 100 | 9.0827
35 | 114 | 100 | 9.1147
35 | 115 | 100 | 9.1467
35 | 116 | 100 | 9.1787
35 | 117 | 100 | 9.2107
35 | 118 | 100 | 9.2427
35 | 119 | 100 | 9.2747
35 | 120 | 100 | 9.3067
35 | 121 | 100 | 9.3387
35 | 122 | 100 | 9.3707
35 | 123 | 100 | 9.4027
35 | 124 | 100 | 9.4347
35 | 125 | 100 | 9.4667
35 | 126 | 100 | 9.5
35 | 127 | 100 | 9.5333
35 | 128 | 100 | 9.5667
35 | 129 | 100 | 9.6
35 | 130 | 100 | 9.6333
35 | 131 | 100 | 9.6667
35 | 132 | 100 | 9.7
35 | 133 | 100 | 9.7333
35 | 134 | 100 | 9.7667
35 | 135 | 100 | 9.8
35 | 136 | 100 | 9.8333
35 | 137 | 100 | 9.8667
35 | 138 | 100 | 9.9
35 | 139 | 100 | 9.9333
35 | 140 | 100 | 9.9667
35 | 141 | 100 | 10
35 | 142 | 100 | 10.0333
35 | 143 | 100 | 10.0667
35 | 144 | 100 | 10.1
35 | 145 | 100 | 10.1333
35 | 146 | 100 | 10.1667
35 | 147 | 100 | 10.2
35 | 148 | 100 | 10.2333
35 | 149 | 100 | 10.2667
35 | 150 | 100 | 10.3
36 | 45 | 100 | 6.5
36 | 46 | 100 | 6.5527
36 | 47 | 100 | 6.6053
36 | 48 | 100 | 6.658
36 | 49 | 100 | 6.7107
36 | 50 | 100 | 6.7633
36 | 51 | 100 | 6.816
36 | 52 | 100 | 6.8687
36 | 53 | 100 | 6.9213
36 | 54 | 100 | 6.974
36 | 55 | 100 | 7.0267
36 | 56 | 100 | 7.0793
36 | 57 | 100 | 7.132
36 | 58 | 100 | 7.1847
36 | 59 | 100 | 7.2373
36 | 60 | 100 | 7.29
36 | 61 | 100 | 7.3427
36 | 62 | 100 | 7.3953
36 | 63 | 100 | 7.448
36 | 64 | 100 | 7.5007
36 | 65 | 100 | 7.5533
36 | 66 | 100 | 7.606
36 | 67 | 100 | 7.6587
36 | 68 | 100 | 7.7113
36 | 69 | 100 | 7.764
36 | 70 | 100 | 7.8167
36 | 71 | 100 | 7.8693
36 | 72 | 100 | 7.922
36 | 73 | 100 | 7.9747
36 | 74 | 100 | 8.0273
36 | 75 | 100 | 8.08
36 | 76 | 100 | 8.1048
36 | 77 | 100 | 8.1296
36 | 78 | 100 | 8.1544
36 | 79 | 100 | 8.1792
36 | 80 | 100 | 8.204
36 | 81 | 100 | 8.2288
36 | 82 | 100 | 8.2536
36 | 83 | 100 | 8.2784
36 | 84 | 100 | 8.3032
36 | 85 | 100 | 8.328
36 | 86 | 100 | 8.3528
36 | 87 | 100 | 8.3776
36 | 88 | 100 | 8.4024
36 | 89 | 100 | 8.4272
36 | 90 | 100 | 8.452
36 | 91 | 100 | 8.4768
36 | 92 | 100 | 8.5016
36 | 93 | 100 | 8.5264
36 | 94 | 100 | 8.5512
36 | 95 | 100 | 8.576
36 | 96 | 100 | 8.6008
36 | 97 | 100 | 8.6256
36 | 98 | 100 | 8.6504
36 | 99 | 100 | 8.6752
36 | 100 | 100 | 8.7
36 | 101 | 100 | 8.7312
36 | 102 | 100 | 8.7624
36 | 103 | 100 | 8.7936
36 | 104 | 100 | 8.8248
36 | 105 | 100 | 8.856
36 | 106 | 100 | 8.8872
36 | 107 | 100 | 8.9184
36 | 108 | 100 | 8.9496
36 | 109 | 100 | 8.9808
36 | 110 | 100 | 9.012
36 | 111 | 100 | 9.0432
36 | 112 | 100 | 9.0744
36 | 113 | 100 | 9.1056
36 | 114 | 100 | 9.1368
36 | 115 | 100 | 9.168
36 | 116 | 100 | 9.1992
36 | 117 | 100 | 9.2304
36 | 118 | 100 | 9.2616
36 | 119 | 100 | 9.2928
36 | 120 | 100 | 9.324
36 | 121 | 100 | 9.3552
36 | 122 | 100 | 9.3864
36 | 123 | 100 | 9.4176
36 | 124 | 100 | 9.4488
36 | 125 | 100 | 9.48
36 | 126 | 100 | 9.5136
36 | 127 | 100 | 9.5472
36 | 128 | 100 | 9.5808
36 | 129 | 100 | 9.6144
36 | 130 | 100 | 9.648
36 | 131 | 100 | 9.6816
36 | 132 | 100 | 9.7152
36 | 133 | 100 | 9.7488
36 | 134 | 100 | 9.7824
36 | 135 | 100 | 9.816
36 | 136 | 100 | 9.8496
36 | 137 | 100 | 9.8832
36 | 138 | 100 | 9.9168
36 | 139 | 100 | 9.9504
36 | 140 | 100 | 9.984
36 | 141 | 100 | 10.0176
36 | 142 | 100 | 10.0512
36 | 143 | 100 | 10.0848
36 | 144 | 100 | 10.1184
36 | 145 | 100 | 10.152
36 | 146 | 100 | 10.1856
36 | 147 | 100 | 10.2192
36 | 148 | 100 | 10.2528
36 | 149 | 100 | 10.2864
36 | 150 | 100 | 10.32
37 | 45 | 100 | 6.5
37 | 46 | 100 | 6.5531
37 | 47 | 100 | 6.6062
37 | 48 | 100 | 6.6593
37 | 49 | 100 | 6.7124
37 | 50 | 100 | 6.7656
37 | 51 | 100 | 6.8187
37 | 52 | 100 | 6.8718
37 | 53 | 100 | 6.9249
37 | 54 | 100 | 6.978
37 | 55 | 100 | 7.0311
37 | 56 | 100 | 7.0842
37 | 57 | 100 | 7.1373
37 | 58 | 100 | 7.1904
37 | 59 | 100 | 7.2436
37 | 60 | 100 | 7.2967
37 | 61 | 100 | 7.3498
37 | 62 | 100 | 7.4029
37 | 63 | 100 | 7.456
37 | 64 | 100 | 7.5091
37 | 65 | 100 | 7.5622
37 | 66 | 100 | 7.6153
37 | 67 | 100 | 7.6684
37 | 68 | 100 | 7.7216
37 | 69 | 100 | 7.7747
37 | 70 | 100 | 7.8278
37 | 71 | 100 | 7.8809
37 | 72 | 100 | 7.934
37 | 73 | 100 | 7.9871
37 | 74 | 100 | 8.0402
37 | 75 | 100 | 8.0933
37 | 76 | 100 | 8.1189
37 | 77 | 100 | 8.1445
37 | 78 | 100 | 8.1701
37 | 79 | 100 | 8.1957
37 | 80 | 100 | 8.2213
37 | 81 | 100 | 8.2469
37 | 82 | 100 | 8.2725
37 | 83 | 100 | 8.2981
37 | 84 | 100 | 8.3237
37 | 85 | 100 | 8.3493
37 | 86 | 100 | 8.3749
37 | 87 | 100 | 8.4005
37 | 88 | 100 | 8.4261
37 | 89 | 100 | 8.4517
37 | 90 | 100 | 8.4773
37 | 91 | 100 | 8.5029
37 | 92 | 100 | 8.5285
37 | 93 | 100 | 8.5541
37 | 94 | 100 | 8.5797
37 | 95 | 100 | 8.6053
37 | 96 | 100 | 8.6309
37 | 97 | 100 | 8.6565
37 | 98 | 100 | 8.6821
37 | 99 | 100 | 8.7077
37 | 100 | 100 | 8.7333
37 | 101 | 100 | 8.7637
37 | 102 | 100 | 8.7941
37 | 103 | 100 | 8.8245
37 | 104 | 100 | 8.8549
37 | 105 | 100 | 8.8853
37 | 106 | 100 | 8.9157
37 | 107 | 100 | 8.9461
37 | 108 | 100 | 8.9765
37 | 109 | 100 | 9.0069
37 | 110 | 100 | 9.0373
37 | 111 | 100 | 9.0677
37 | 112 | 100 | 9.0981
37 | 113 | 100 | 9.1285
37 | 114 | 100 | 9.1589
37 | 115 | 100 | 9.1893
37 | 116 | 100 | 9.2197
37 | 117 | 100 | 9.2501
37 | 118 | 100 | 9.2805
37 | 119 | 100 | 9.3109
37 | 120 | 100 | 9.3413
37 | 121 | 100 | 9.3717
37 | 122 | 100 | 9.4021
37 | 123 | 100 | 9.4325
37 | 124 | 100 | 9.4629
37 | 125 | 100 | 9.4933
37 | 126 | 100 | 9.5272
37 | 127 | 100 | 9.5611
37 | 128 | 100 | 9.5949
37 | 129 | 100 | 9.6288
37 | 130 | 100 | 9.6627
37 | 131 | 100 | 9.6965
37 | 132 | 100 | 9.7304
37 | 133 | 100 | 9.7643
37 | 134 | 100 | 9.7981
37 | 135 | 100 | 9.832
37 | 136 | 100 | 9.8659
37 | 137 | 100 | 9.8997
37 | 138 | 100 | 9.9336
37 | 139 | 100 | 9.9675
37 | 140 | 100 | 10.0013
37 | 141 | 100 | 10.0352
37 | 142 | 100 | 10.0691
37 | 143 | 100 | 10.1029
37 | 144 | 100 | 10.1368
37 | 145 | 100 | 10.1707
37 | 146 | 100 | 10.2045
37 | 147 | 100 | 10.2384
37 | 148 | 100 | 10.2723
37 | 149 | 100 | 10.3061
37 | 150 | 100 | 10.34
38 | 45 | 100 | 6.5
38 | 46 | 100 | 6.5536
38 | 47 | 100 | 6.6071
38 | 48 | 100 | 6.6607
38 | 49 | 100 | 6.7142
38 | 50 | 100 | 6.7678
38 | 51 | 100 | 6.8213
38 | 52 | 100 | 6.8749
38 | 53 | 100 | 6.9284
38 | 54 | 100 | 6.982
38 | 55 | 100 | 7.0356
38 | 56 | 100 | 7.0891
38 | 57 | 100 | 7.1427
38 | 58 | 100 | 7.1962
38 | 59 | 100 | 7.2498
38 | 60 | 100 | 7.3033
38 | 61 | 100 | 7.3569
38 | 62 | 100 | 7.4104
38 | 63 | 100 | 7.464
38 | 64 | 100 | 7.5176
38 | 65 | 100 | 7.5711
38 | 66 | 100 | 7.6247
38 | 67 | 100 | 7.6782
38 | 68 | 100 | 7.7318
38 | 69 | 100 | 7.7853
38 | 70 | 100 | 7.8389
38 | 71 | 100 | 7.8924
38 | 72 | 100 | 7.946
38 | 73 | 100 | 7.9996
38 | 74 | 100 | 8.0531
38 | 75 | 100 | 8.1067
38 | 76 | 100 | 8.1331
38 | 77 | 100 | 8.1595
38 | 78 | 100 | 8.1859
38 | 79 | 100 | 8.2123
38 | 80 | 100 | 8.2387
38 | 81 | 100 | 8.2651
38 | 82 | 100 | 8.2915
38 | 83 | 100 | 8.3179
38 | 84 | 100 | 8.3443
38 | 85 | 100 | 8.3707
38 | 86 | 100 | 8.3971
38 | 87 | 100 | 8.4235
38 | 88 | 100 | 8.4499
38 | 89 | 100 | 8.4763
38 | 90 | 100 | 8.5027
38 | 91 | 100 | 8.5291
38 | 92 | 100 | 8.5555
38 | 93 | 100 | 8.5819
38 | 94 | 100 | 8.6083
38 | 95 | 100 | 8.6347
38 | 96 | 100 | 8.6611
38 | 97 | 100 | 8.6875
38 | 98 | 100 | 8.7139
38 | 99 | 100 | 8.7403
38 | 100 | 100 | 8.7667
38 | 101 | 100 | 8.7963
38 | 102 | 100 | 8.8259
38 | 103 | 100 | 8.8555
38 | 104 | 100 | 8.8851
38 | 105 | 100 | 8.9147
38 | 106 | 100 | 8.9443
38 | 107 | 100 | 8.9739
38 | 108 | 100 | 9.0035
38 | 109 | 100 | 9.0331
38 | 110 | 100 | 9.0627
38 | 111 | 100 | 9.0923
38 | 112 | 100 | 9.1219
38 | 113 | 100 | 9.1515
38 | 114 | 100 | 9.1811
38 | 115 | 100 | 9.2107
38 | 116 | 100 | 9.2403
38 | 117 | 100 | 9.2699
38 | 118 | 100 | 9.2995
38 | 119 | 100 | 9.3291
38 | 120 | 100 | 9.3587
38 | 121 | 100 | 9.3883
38 | 122 | 100 | 9.4179
38 | 123 | 100 | 9.4475
38 | 124 | 100 | 9.4771
38 | 125 | 100 | 9.5067
38 | 126 | 100 | 9.5408
38 | 127 | 100 | 9.5749
38 | 128 | 100 | 9.6091
38 | 129 | 100 | 9.6432
38 | 130 | 100 | 9.6773
38 | 131 | 100 | 9.7115
38 | 132 | 100 | 9.7456
38 | 133 | 100 | 9.7797
38 | 134 | 100 | 9.8139
38 | 135 | 100 | 9.848
38 | 136 | 100 | 9.8821
38 | 137 | 100 | 9.9163
38 | 138 | 100 | 9.9504
38 | 139 | 100 | 9.9845
38 | 140 | 100 | 10.0187
38 | 141 | 100 | 10.0528
38 | 142 | 100 | 10.0869
38 | 143 | 100 | 10.1211
38 | 144 | 100 | 10.1552
38 | 145 | 100 | 10.1893
38 | 146 | 100 | 10.2235
38 | 147 | 100 | 10.2576
38 | 148 | 100 | 10.2917
38 | 149 | 100 | 10.3259
38 | 150 | 100 | 10.36
39 | 45 | 100 | 6.5
39 | 46 | 100 | 6.554
39 | 47 | 100 | 6.608
39 | 48 | 100 | 6.662
39 | 49 | 100 | 6.716
39 | 50 | 100 | 6.77
39 | 51 | 100 | 6.824
39 | 52 | 100 | 6.878
39 | 53 | 100 | 6.932
39 | 54 | 100 | 6.986
39 | 55 | 100 | 7.04
39 | 56 | 100 | 7.094
39 | 57 | 100 | 7.148
39 | 58 | 100 | 7.202
39 | 59 | 100 | 7.256
39 | 60 | 100 | 7.31
39 | 61 | 100 | 7.364
39 | 62 | 100 | 7.418
39 | 63 | 100 | 7.472
39 | 64 | 100 | 7.526
39 | 65 | 100 | 7.58
39 | 66 | 100 | 7.634
39 | 67 | 100 | 7.688
39 | 68 | 100 | 7.742
39 | 69 | 100 | 7.796
39 | 70 | 100 | 7.85
39 | 71 | 100 | 7.904
39 | 72 | 100 | 7.958
39 | 73 | 100 | 8.012
39 | 74 | 100 | 8.066
39 | 75 | 100 | 8.12
39 | 76 | 100 | 8.1472
39 | 77 | 100 | 8.1744
39 | 78 | 100 | 8.2016
39 | 79 | 100 | 8.2288
39 | 80 | 100 | 8.256
39 | 81 | 100 | 8.2832
39 | 82 | 100 | 8.3104
39 | 83 | 100 | 8.3376
39 | 84 | 100 | 8.3648
39 | 85 | 100 | 8.392
39 | 86 | 100 | 8.4192
39 | 87 | 100 | 8.4464
39 | 88 | 100 | 8.4736
39 | 89 | 100 | 8.5008
39 | 90 | 100 | 8.528
39 | 91 | 100 | 8.5552
39 | 92 | 100 | 8.5824
39 | 93 | 100 | 8.6096
39 | 94 | 100 | 8.6368
39 | 95 | 100 | 8.664
39 | 96 | 100 | 8.6912
39 | 97 | 100 | 8.7184
39 | 98 | 100 | 8.7456
39 | 99 | 100 | 8.7728
39 | 100 | 100 | 8.8
39 | 101 | 100 | 8.8288
39 | 102 | 100 | 8.8576
39 | 103 | 100 | 8.8864
39 | 104 | 100 | 8.9152
39 | 105 | 100 | 8.944
39 | 106 | 100 | 8.9728
39 | 107 | 100 | 9.0016
39 | 108 | 100 | 9.0304
39 | 109 | 100 | 9.0592
39 | 110 | 100 | 9.088
39 | 111 | 100 | 9.1168
39 | 112 | 100 | 9.1456
39 | 113 | 100 | 9.1744
39 | 114 | 100 | 9.2032
39 | 115 | 100 | 9.232
39 | 116 | 100 | 9.2608
39 | 117 | 100 | 9.2896
39 | 118 | 100 | 9.3184
39 | 119 | 100 | 9.3472
39 | 120 | 100 | 9.376
39 | 121 | 100 | 9.4048
39 | 122 | 100 | 9.4336
39 | 123 | 100 | 9.4624
39 | 124 | 100 | 9.4912
39 | 125 | 100 | 9.52
39 | 126 | 100 | 9.5544
39 | 127 | 100 | 9.5888
39 | 128 | 100 | 9.6232
39 | 129 | 100 | 9.6576
39 | 130 | 100 | 9.692
39 | 131 | 100 | 9.7264
39 | 132 | 100 | 9.7608
39 | 133 | 100 | 9.7952
39 | 134 | 100 | 9.8296
39 | 135 | 100 | 9.864
39 | 136 | 100 | 9.8984
39 | 137 | 100 | 9.9328
39 | 138 | 100 | 9.9672
39 | 139 | 100 | 10.0016
39 | 140 | 100 | 10.036
39 | 141 | 100 | 10.0704
39 | 142 | 100 | 10.1048
39 | 143 | 100 | 10.1392
39 | 144 | 100 | 10.1736
39 | 145 | 100 | 10.208
39 | 146 | 100 | 10.2424
39 | 147 | 100 | 10.2768
39 | 148 | 100 | 10.3112
39 | 149 | 100 | 10.3456
39 | 150 | 100 | 10.38
40 | 45 | 100 | 6.5
40 | 46 | 100 | 6.5544
40 | 47 | 100 | 6.6089
40 | 48 | 100 | 6.6633
40 | 49 | 100 | 6.7178
40 | 50 | 100 | 6.7722
40 | 51 | 100 | 6.8267
40 | 52 | 100 | 6.8811
40 | 53 | 100 | 6.9356
40 | 54 | 100 | 6.99
40 | 55 | 100 | 7.0444
40 | 56 | 100 | 7.0989
40 | 57 | 100 | 7.1533
40 | 58 | 100 | 7.2078
40 | 59 | 100 | 7.2622
40 | 60 | 100 | 7.3167
40 | 61 | 100 | 7.3711
40 | 62 | 100 | 7.4256
40 | 63 | 100 | 7.48
40 | 64 | 100 | 7.5344
40 | 65 | 100 | 7.5889
40 | 66 | 100 | 7.6433
40 | 67 | 100 | 7.6978
40 | 68 | 100 | 7.7522
40 | 69 | 100 | 7.8067
40 | 70 | 100 | 7.8611
40 | 71 | 100 | 7.9156
40 | 72 | 100 | 7.97
40 | 73 | 100 | 8.0244
40 | 74 | 100 | 8.0789
40 | 75 | 100 | 8.1333
40 | 76 | 100 | 8.1613
40 | 77 | 100 | 8.1893
40 | 78 | 100 | 8.2173
40 | 79 | 100 | 8.2453
40 | 80 | 100 | 8.2733
40 | 81 | 100 | 8.3013
40 | 82 | 100 | 8.3293
40 | 83 | 100 | 8.3573
40 | 84 | 100 | 8.3853
40 | 85 | 100 | 8.4133
40 | 86 | 100 | 8.4413
40 | 87 | 100 | 8.4693
40 | 88 | 100 | 8.4973
40 | 89 | 100 | 8.5253
40 | 90 | 100 | 8.5533
40 | 91 | 100 | 8.5813
40 | 92 | 100 | 8.6093
40 | 93 | 100 | 8.6373
40 | 94 | 100 | 8.6653
40 | 95 | 100 | 8.6933
40 | 96 | 100 | 8.7213
40 | 97 | 100 | 8.7493
40 | 98 | 100 | 8.7773
40 | 99 | 100 | 8.8053
40 | 100 | 100 | 8.8333
40 | 101 | 100 | 8.8613
40 | 102 | 100 | 8.8893
40 | 103 | 100 | 8.9173
40 | 104 | 100 | 8.9453
40 | 105 | 100 | 8.9733
40 | 106 | 100 | 9.0013
40 | 107 | 100 | 9.0293
40 | 108 | 100 | 9.0573
40 | 109 | 100 | 9.0853
40 | 110 | 100 | 9.1133
40 | 111 | 100 | 9.1413
40 | 112 | 100 | 9.1693
40 | 113 | 100 | 9.1973
40 | 114 | 100 | 9.2253
40 | 115 | 100 | 9.2533
40 | 116 | 100 | 9.2813
40 | 117 | 100 | 9.3093
40 | 118 | 100 | 9.3373
40 | 119 | 100 | 9.3653
40 | 120 | 100 | 9.3933
40 | 121 | 100 | 9.4213
40 | 122 | 100 | 9.4493
40 | 123 | 100 | 9.4773
40 | 124 | 100 | 9.5053
40 | 125 | 100 | 9.5333
40 | 126 | 100 | 9.568
40 | 127 | 100 | 9.6027
40 | 128 | 100 | 9.6373
40 | 129 | 100 | 9.672
40 | 130 | 100 | 9.7067
40 | 131 | 100 | 9.7413
40 | 132 | 100 | 9.776
40 | 133 | 100 | 9.8107
40 | 134 | 100 | 9.8453
40 | 135 | 100 | 9.88
40 | 136 | 100 | 9.9147
40 | 137 | 100 | 9.9493
40 | 138 | 100 | 9.984
40 | 139 | 100 | 10.0187
40 | 140 | 100 | 10.0533
40 | 141 | 100 | 10.088
40 | 142 | 100 | 10.1227
40 | 143 | 100 | 10.1573
40 | 144 | 100 | 10.192
40 | 145 | 100 | 10.2267
40 | 146 | 100 | 10.2613
40 | 147 | 100 | 10.296
40 | 148 | 100 | 10.3307
40 | 149 | 100 | 10.3653
40 | 150 | 100 | 10.4
41 | 45 | 100 | 6.5
41 | 46 | 100 | 6.5549
41 | 47 | 100 | 6.6098
41 | 48 | 100 | 6.6647
41 | 49 | 100 | 6.7196
41 | 50 | 100 | 6.7744
41 | 51 | 100 | 6.8293
41 | 52 | 100 | 6.8842
41 | 53 | 100 | 6.9391
41 | 54 | 100 | 6.994
41 | 55 | 100 | 7.0489
41 | 56 | 100 | 7.1038
41 | 57 | 100 | 7.1587
41 | 58 | 100 | 7.2136
41 | 59 | 100 | 7.2684
41 | 60 | 100 | 7.3233
41 | 61 | 100 | 7.3782
41 | 62 | 100 | 7.4331
41 | 63 | 100 | 7.488
41 | 64 | 100 | 7.5429
41 | 65 | 100 | 7.5978
41 | 66 | 100 | 7.6527
41 | 67 | 100 | 7.7076
41 | 68 | 100 | 7.7624
41 | 69 | 100 | 7.8173
41 | 70 | 100 | 7.8722
41 | 71 | 100 | 7.9271
41 | 72 | 100 | 7.982
41 | 73 | 100 | 8.0369
41 | 74 | 100 | 8.0918
41 | 75 | 100 | 8.1467
41 | 76 | 100 | 8.1755
41 | 77 | 100 | 8.2043
41 | 78 | 100 | 8.2331
41 | 79 | 100 | 8.2619
41 | 80 | 100 | 8.2907
41 | 81 | 100 | 8.3195
41 | 82 | 100 | 8.3483
41 | 83 | 100 | 8.3771
41 | 84 | 100 | 8.4059
41 | 85 | 100 | 8.4347
41 | 86 | 100 | 8.4635
41 | 87 | 100 | 8.4923
41 | 88 | 100 | 8.5211
41 | 89 | 100 | 8.5499
41 | 90 | 100 | 8.5787
41 | 91 | 100 | 8.6075
41 | 92 | 100 | 8.6363
41 | 93 | 100 | 8.6651
41 | 94 | 100 | 8.6939
41 | 95 | 100 | 8.7227
41 | 96 | 100 | 8.7515
41 | 97 | 100 | 8.7803
41 | 98 | 100 | 8.8091
41 | 99 | 100 | 8.8379
41 | 100 | 100 | 8.8667
41 | 101 | 100 | 8.8939
41 | 102 | 100 | 8.9211
41 | 103 | 100 | 8.9483
41 | 104 | 100 | 8.9755
41 | 105 | 100 | 9.0027
41 | 106 | 100 | 9.0299
41 | 107 | 100 | 9.0571
41 | 108 | 100 | 9.0843
41 | 109 | 100 | 9.1115
41 | 110 | 100 | 9.1387
41 | 111 | 100 | 9.1659
41 | 112 | 100 | 9.1931
41 | 113 | 100 | 9.2203
41 | 114 | 100 | 9.2475
41 | 115 | 100 | 9.2747
41 | 116 | 100 | 9.3019
41 | 117 | 100 | 9.3291
41 | 118 | 100 | 9.3563
41 | 119 | 100 | 9.3835
41 | 120 | 100 | 9.4107
41 | 121 | 100 | 9.4379
41 | 122 | 100 | 9.4651
41 | 123 | 100 | 9.4923
41 | 124 | 100 | 9.5195
41 | 125 | 100 | 9.5467
41 | 126 | 100 | 9.5816
41 | 127 | 100 | 9.6165
41 | 128 | 100 | 9.6515
41 | 129 | 100 | 9.6864
41 | 130 | 100 | 9.7213
41 | 131 | 100 | 9.7563
41 | 132 | 100 | 9.7912
41 | 133 | 100 | 9.8261
41 | 134 | 100 | 9.8611
41 | 135 | 100 | 9.896
41 | 136 | 100 | 9.9309
41 | 137 | 100 | 9.9659
41 | 138 | 100 | 10.0008
41 | 139 | 100 | 10.0357
41 | 140 | 100 | 10.0707
41 | 141 | 100 | 10.1056
41 | 142 | 100 | 10.1405
41 | 143 | 100 | 10.1755
41 | 144 | 100 | 10.2104
41 | 145 | 100 | 10.2453
41 | 146 | 100 | 10.2803
41 | 147 | 100 | 10.3152
41 | 148 | 100 | 10.3501
41 | 149 | 100 | 10.3851
41 | 150 | 100 | 10.42
42 | 45 | 100 | 6.5
42 | 46 | 100 | 6.5553
42 | 47 | 100 | 6.6107
42 | 48 | 100 | 6.666
42 | 49 | 100 | 6.7213
42 | 50 | 100 | 6.7767
42 | 51 | 100 | 6.832
42 | 52 | 100 | 6.8873
42 | 53 | 100 | 6.9427
42 | 54 | 100 | 6.998
42 | 55 | 100 | 7.0533
42 | 56 | 100 | 7.1087
42 | 57 | 100 | 7.164
42 | 58 | 100 | 7.2193
42 | 59 | 100 | 7.2747
42 | 60 | 100 | 7.33
42 | 61 | 100 | 7.3853
42 | 62 | 100 | 7.4407
42 | 63 | 100 | 7.496
42 | 64 | 100 | 7.5513
42 | 65 | 100 | 7.6067
42 | 66 | 100 | 7.662
42 | 67 | 100 | 7.7173
42 | 68 | 100 | 7.7727
42 | 69 | 100 | 7.828
42 | 70 | 100 | 7.8833
42 | 71 | 100 | 7.9387
42 | 72 | 100 | 7.994
42 | 73 | 100 | 8.0493
42 | 74 | 100 | 8.1047
42 | 75 | 100 | 8.16
42 | 76 | 100 | 8.1896
42 | 77 | 100 | 8.2192
42 | 78 | 100 | 8.2488
42 | 79 | 100 | 8.2784
42 | 80 | 100 | 8.308
42 | 81 | 100 | 8.3376
42 | 82 | 100 | 8.3672
42 | 83 | 100 | 8.3968
42 | 84 | 100 | 8.4264
42 | 85 | 100 | 8.456
42 | 86 | 100 | 8.4856
42 | 87 | 100 | 8.5152
42 | 88 | 100 | 8.5448
42 | 89 | 100 | 8.5744
42 | 90 | 100 | 8.604
42 | 91 | 100 | 8.6336
42 | 92 | 100 | 8.6632
42 | 93 | 100 | 8.6928
42 | 94 | 100 | 8.7224
42 | 95 | 100 | 8.752
42 | 96 | 100 | 8.7816
42 | 97 | 100 | 8.8112
42 | 98 | 100 | 8.8408
42 | 99 | 100 | 8.8704
42 | 100 | 100 | 8.9
42 | 101 | 100 | 8.9264
42 | 102 | 100 | 8.9528
42 | 103 | 100 | 8.9792
42 | 104 | 100 | 9.0056
42 | 105 | 100 | 9.032
42 | 106 | 100 | 9.0584
42 | 107 | 100 | 9.0848
42 | 108 | 100 | 9.1112
42 | 109 | 100 | 9.1376
42 | 110 | 100 | 9.164
42 | 111 | 100 | 9.1904
42 | 112 | 100 | 9.2168
42 | 113 | 100 | 9.2432
42 | 114 | 100 | 9.2696
42 | 115 | 100 | 9.296
42 | 116 | 100 | 9.3224
42 | 117 | 100 | 9.3488
42 | 118 | 100 | 9.3752
42 | 119 | 100 | 9.4016
42 | 120 | 100 | 9.428
42 | 121 | 100 | 9.4544
42 | 122 | 100 | 9.4808
42 | 123 | 100 | 9.5072
42 | 124 | 100 | 9.5336
42 | 125 | 100 | 9.56
42 | 126 | 100 | 9.5952
42 | 127 | 100 | 9.6304
42 | 128 | 100 | 9.6656
42 | 129 | 100 | 9.7008
42 | 130 | 100 | 9.736
42 | 131 | 100 | 9.7712
42 | 132 | 100 | 9.8064
42 | 133 | 100 | 9.8416
42 | 134 | 100 | 9.8768
42 | 135 | 100 | 9.912
42 | 136 | 100 | 9.9472
42 | 137 | 100 | 9.9824
42 | 138 | 100 | 10.0176
42 | 139 | 100 | 10.0528
42 | 140 | 100 | 10.088
42 | 141 | 100 | 10.1232
42 | 142 | 100 | 10.1584
42 | 143 | 100 | 10.1936
42 | 144 | 100 | 10.2288
42 | 145 | 100 | 10.264
42 | 146 | 100 | 10.2992
42 | 147 | 100 | 10.3344
42 | 148 | 100 | 10.3696
42 | 149 | 100 | 10.4048
42 | 150 | 100 | 10.44
43 | 45 | 100 | 6.5
43 | 46 | 100 | 6.5558
43 | 47 | 100 | 6.6116
43 | 48 | 100 | 6.6673
43 | 49 | 100 | 6.7231
43 | 50 | 100 | 6.7789
43 | 51 | 100 | 6.8347
43 | 52 | 100 | 6.8904
43 | 53 | 100 | 6.9462
43 | 54 | 100 | 7.002
43 | 55 | 100 | 7.0578
43 | 56 | 100 | 7.1136
43 | 57 | 100 | 7.1693
43 | 58 | 100 | 7.2251
43 | 59 | 100 | 7.2809
43 | 60 | 100 | 7.3367
43 | 61 | 100 | 7.3924
43 | 62 | 100 | 7.4482
43 | 63 | 100 | 7.504
43 | 64 | 100 | 7.5598
43 | 65 | 100 | 7.6156
43 | 66 | 100 | 7.6713
43 | 67 | 100 | 7.7271
43 | 68 | 100 | 7.7829
43 | 69 | 100 | 7.8387
43 | 70 | 100 | 7.8944
43 | 71 | 100 | 7.9502
43 | 72 | 100 | 8.006
43 | 73 | 100 | 8.0618
43 | 74 | 100 | 8.1176
43 | 75 | 100 | 8.1733
43 | 76 | 100 | 8.2037
43 | 77 | 100 | 8.2341
43 | 78 | 100 | 8.2645
43 | 79 | 100 | 8.2949
43 | 80 | 100 | 8.3253
43 | 81 | 100 | 8.3557
43 | 82 | 100 | 8.3861
43 | 83 | 100 | 8.4165
43 | 84 | 100 | 8.4469
43 | 85 | 100 | 8.4773
43 | 86 | 100 | 8.5077
43 | 87 | 100 | 8.5381
43 | 88 | 100 | 8.5685
43 | 89 | 100 | 8.5989
43 | 90 | 100 | 8.6293
43 | 91 | 100 | 8.6597
43 | 92 | 100 | 8.6901
43 | 93 | 100 | 8.7205
43 | 94 | 100 | 8.7509
43 | 95 | 100 | 8.7813
43 | 96 | 100 | 8.8117
43 | 97 | 100 | 8.8421
43 | 98 | 100 | 8.8725
43 | 99 | 100 | 8.9029
43 | 100 | 100 | 8.9333
43 | 101 | 100 | 8.9589
43 | 102 | 100 | 8.9845
43 | 103 | 100 | 9.0101
43 | 104 | 100 | 9.0357
43 | 105 | 100 | 9.0613
43 | 106 | 100 | 9.0869
43 | 107 | 100 | 9.1125
43 | 108 | 100 | 9.1381
43 | 109 | 100 | 9.1637
43 | 110 | 100 | 9.1893
43 | 111 | 100 | 9.2149
43 | 112 | 100 | 9.2405
43 | 113 | 100 | 9.2661
43 | 114 | 100 | 9.2917
43 | 115 | 100 | 9.3173
43 | 116 | 100 | 9.3429
43 | 117 | 100 | 9.3685
43 | 118 | 100 | 9.3941
43 | 119 | 100 | 9.4197
43 | 120 | 100 | 9.4453
43 | 121 | 100 | 9.4709
43 | 122 | 100 | 9.4965
43 | 123 | 100 | 9.5221
43 | 124 | 100 | 9.5477
43 | 125 | 100 | 9.5733
43 | 126 | 100 | 9.6088
43 | 127 | 100 | 9.6443
43 | 128 | 100 | 9.6797
43 | 129 | 100 | 9.7152
43 | 130 | 100 | 9.7507
43 | 131 | 100 | 9.7861
43 | 132 | 100 | 9.8216
43 | 133 | 100 | 9.8571
43 | 134 | 100 | 9.8925
43 | 135 | 100 | 9.928
43 | 136 | 100 | 9.9635
43 | 137 | 100 | 9.9989
43 | 138 | 100 | 10.0344
43 | 139 | 100 | 10.0699
43 | 140 | 100 | 10.1053
43 | 141 | 100 | 10.1408
43 | 142 | 100 | 10.1763
43 | 143 | 100 | 10.2117
43 | 144 | 100 | 10.2472
43 | 145 | 100 | 10.2827
43 | 146 | 100 | 10.3181
43 | 147 | 100 | 10.3536
43 | 148 | 100 | 10.3891
43 | 149 | 100 | 10.4245
43 | 150 | 100 | 10.46
44 | 45 | 100 | 6.5
44 | 46 | 100 | 6.5562
44 | 47 | 100 | 6.6124
44 | 48 | 100 | 6.6687
44 | 49 | 100 | 6.7249
44 | 50 | 100 | 6.7811
44 | 51 | 100 | 6.8373
44 | 52 | 100 | 6.8936
44 | 53 | 100 | 6.9498
44 | 54 | 100 | 7.006
44 | 55 | 100 | 7.0622
44 | 56 | 100 | 7.1184
44 | 57 | 100 | 7.1747
44 | 58 | 100 | 7.2309
44 | 59 | 100 | 7.2871
44 | 60 | 100 | 7.3433
44 | 61 | 100 | 7.3996
44 | 62 | 100 | 7.4558
44 | 63 | 100 | 7.512
44 | 64 | 100 | 7.5682
44 | 65 | 100 | 7.6244
44 | 66 | 100 | 7.6807
44 | 67 | 100 | 7.7369
44 | 68 | 100 | 7.7931
44 | 69 | 100 | 7.8493
44 | 70 | 100 | 7.9056
44 | 71 | 100 | 7.9618
44 | 72 | 100 | 8.018
44 | 73 | 100 | 8.0742
44 | 74 | 100 | 8.1304
44 | 75 | 100 | 8.1867
44 | 76 | 100 | 8.2179
44 | 77 | 100 | 8.2491
44 | 78 | 100 | 8.2803
44 | 79 | 100 | 8.3115
44 | 80 | 100 | 8.3427
44 | 81 | 100 | 8.3739
44 | 82 | 100 | 8.4051
44 | 83 | 100 | 8.4363
44 | 84 | 100 | 8.4675
44 | 85 | 100 | 8.4987
44 | 86 | 100 | 8.5299
44 | 87 | 100 | 8.5611
44 | 88 | 100 | 8.5923
44 | 89 | 100 | 8.6235
44 | 90 | 100 | 8.6547
44 | 91 | 100 | 8.6859
44 | 92 | 100 | 8.7171
44 | 93 | 100 | 8.7483
44 | 94 | 100 | 8.7795
44 | 95 | 100 | 8.8107
44 | 96 | 100 | 8.8419
44 | 97 | 100 | 8.8731
44 | 98 | 100 | 8.9043
44 | 99 | 100 | 8.9355
44 | 100 | 100 | 8.9667
44 | 101 | 100 | 8.9915
44 | 102 | 100 | 9.0163
44 | 103 | 100 | 9.0411
44 | 104 | 100 | 9.0659
44 | 105 | 100 | 9.0907
44 | 106 | 100 | 9.1155
44 | 107 | 100 | 9.1403
44 | 108 | 100 | 9.1651
44 | 109 | 100 | 9.1899
44 | 110 | 100 | 9.2147
44 | 111 | 100 | 9.2395
44 | 112 | 100 | 9.2643
44 | 113 | 100 | 9.2891
44 | 114 | 100 | 9.3139
44 | 115 | 100 | 9.3387
44 | 116 | 100 | 9.3635
44 | 117 | 100 | 9.3883
44 | 118 | 100 | 9.4131
44 | 119 | 100 | 9.4379
44 | 120 | 100 | 9.4627
44 | 121 | 100 | 9.4875
44 | 122 | 100 | 9.5123
44 | 123 | 100 | 9.5371
44 | 124 | 100 | 9.5619
44 | 125 | 100 | 9.5867
44 | 126 | 100 | 9.6224
44 | 127 | 100 | 9.6581
44 | 128 | 100 | 9.6939
44 | 129 | 100 | 9.7296
44 | 130 | 100 | 9.7653
44 | 131 | 100 | 9.8011
44 | 132 | 100 | 9.8368
44 | 133 | 100 | 9.8725
44 | 134 | 100 | 9.9083
44 | 135 | 100 | 9.944
44 | 136 | 100 | 9.9797
44 | 137 | 100 | 10.0155
44 | 138 | 100 | 10.0512
44 | 139 | 100 | 10.0869
44 | 140 | 100 | 10.1227
44 | 141 | 100 | 10.1584
44 | 142 | 100 | 10.1941
44 | 143 | 100 | 10.2299
44 | 144 | 100 | 10.2656
44 | 145 | 100 | 10.3013
44 | 146 | 100 | 10.3371
44 | 147 | 100 | 10.3728
44 | 148 | 100 | 10.4085
44 | 149 | 100 | 10.4443
44 | 150 | 100 | 10.48
45 | 45 | 100 | 6.5
45 | 46 | 100 | 6.5567
45 | 47 | 100 | 6.6133
45 | 48 | 100 | 6.67
45 | 49 | 100 | 6.7267
45 | 50 | 100 | 6.7833
45 | 51 | 100 | 6.84
45 | 52 | 100 | 6.8967
45 | 53 | 100 | 6.9533
45 | 54 | 100 | 7.01
45 | 55 | 100 | 7.0667
45 | 56 | 100 | 7.1233
45 | 57 | 100 | 7.18
45 | 58 | 100 | 7.2367
45 | 59 | 100 | 7.2933
45 | 60 | 100 | 7.35
45 | 61 | 100 | 7.4067
45 | 62 | 100 | 7.4633
45 | 63 | 100 | 7.52
45 | 64 | 100 | 7.5767
45 | 65 | 100 | 7.6333
45 | 66 | 100 | 7.69
45 | 67 | 100 | 7.7467
45 | 68 | 100 | 7.8033
45 | 69 | 100 | 7.86
45 | 70 | 100 | 7.9167
45 | 71 | 100 | 7.9733
45 | 72 | 100 | 8.03
45 | 73 | 100 | 8.0867
45 | 74 | 100 | 8.1433
45 | 75 | 100 | 8.2
45 | 76 | 100 | 8.232
45 | 77 | 100 | 8.264
45 | 78 | 100 | 8.296
45 | 79 | 100 | 8.328
45 | 80 | 100 | 8.36
45 | 81 | 100 | 8.392
45 | 82 | 100 | 8.424
45 | 83 | 100 | 8.456
45 | 84 | 100 | 8.488
45 | 85 | 100 | 8.52
45 | 86 | 100 | 8.552
45 | 87 | 100 | 8.584
45 | 88 | 100 | 8.616
45 | 89 | 100 | 8.648
45 | 90 | 100 | 8.68
45 | 91 | 100 | 8.712
45 | 92 | 100 | 8.744
45 | 93 | 100 | 8.776
45 | 94 | 100 | 8.808
45 | 95 | 100 | 8.84
45 | 96 | 100 | 8.872
45 | 97 | 100 | 8.904
45 | 98 | 100 | 8.936
45 | 99 | 100 | 8.968
45 | 100 | 100 | 9
45 | 101 | 100 | 9.024
45 | 102 | 100 | 9.048
45 | 103 | 100 | 9.072
45 | 104 | 100 | 9.096
45 | 105 | 100 | 9.12
45 | 106 | 100 | 9.144
45 | 107 | 100 | 9.168
45 | 108 | 100 | 9.192
45 | 109 | 100 | 9.216
45 | 110 | 100 | 9.24
45 | 111 | 100 | 9.264
45 | 112 | 100 | 9.288
45 | 113 | 100 | 9.312
45 | 114 | 100 | 9.336
45 | 115 | 100 | 9.36
45 | 116 | 100 | 9.384
45 | 117 | 100 | 9.408
45 | 118 | 100 | 9.432
45 | 119 | 100 | 9.456
45 | 120 | 100 | 9.48
45 | 121 | 100 | 9.504
45 | 122 | 100 | 9.528
45 | 123 | 100 | 9.552
45 | 124 | 100 | 9.576
45 | 125 | 100 | 9.6
45 | 126 | 100 | 9.636
45 | 127 | 100 | 9.672
45 | 128 | 100 | 9.708
45 | 129 | 100 | 9.744
45 | 130 | 100 | 9.78
45 | 131 | 100 | 9.816
45 | 132 | 100 | 9.852
45 | 133 | 100 | 9.888
45 | 134 | 100 | 9.924
45 | 135 | 100 | 9.96
45 | 136 | 100 | 9.996
45 | 137 | 100 | 10.032
45 | 138 | 100 | 10.068
45 | 139 | 100 | 10.104
45 | 140 | 100 | 10.14
45 | 141 | 100 | 10.176
45 | 142 | 100 | 10.212
45 | 143 | 100 | 10.248
45 | 144 | 100 | 10.284
45 | 145 | 100 | 10.32
45 | 146 | 100 | 10.356
45 | 147 | 100 | 10.392
45 | 148 | 100 | 10.428
45 | 149 | 100 | 10.464
45 | 150 | 100 | 10.5
46 | 45 | 100 | 6.52
46 | 46 | 100 | 6.576
46 | 47 | 100 | 6.632
46 | 48 | 100 | 6.688
46 | 49 | 100 | 6.744
46 | 50 | 100 | 6.8
46 | 51 | 100 | 6.856
46 | 52 | 100 | 6.912
46 | 53 | 100 | 6.968
46 | 54 | 100 | 7.024
46 | 55 | 100 | 7.08
46 | 56 | 100 | 7.136
46 | 57 | 100 | 7.192
46 | 58 | 100 | 7.248
46 | 59 | 100 | 7.304
46 | 60 | 100 | 7.36
46 | 61 | 100 | 7.416
46 | 62 | 100 | 7.472
46 | 63 | 100 | 7.528
46 | 64 | 100 | 7.584
46 | 65 | 100 | 7.64
46 | 66 | 100 | 7.696
46 | 67 | 100 | 7.752
46 | 68 | 100 | 7.808
46 | 69 | 100 | 7.864
46 | 70 | 100 | 7.92
46 | 71 | 100 | 7.976
46 | 72 | 100 | 8.032
46 | 73 | 100 | 8.088
46 | 74 | 100 | 8.144
46 | 75 | 100 | 8.2
46 | 76 | 100 | 8.2344
46 | 77 | 100 | 8.2688
46 | 78 | 100 | 8.3032
46 | 79 | 100 | 8.3376
46 | 80 | 100 | 8.372
46 | 81 | 100 | 8.4064
46 | 82 | 100 | 8.4408
46 | 83 | 100 | 8.4752
46 | 84 | 100 | 8.5096
46 | 85 | 100 | 8.544
46 | 86 | 100 | 8.5784
46 | 87 | 100 | 8.6128
46 | 88 | 100 | 8.6472
46 | 89 | 100 | 8.6816
46 | 90 | 100 | 8.716
46 | 91 | 100 | 8.7504
46 | 92 | 100 | 8.7848
46 | 93 | 100 | 8.8192
46 | 94 | 100 | 8.8536
46 | 95 | 100 | 8.888
46 | 96 | 100 | 8.9224
46 | 97 | 100 | 8.9568
46 | 98 | 100 | 8.9912
46 | 99 | 100 | 9.0256
46 | 100 | 100 | 9.06
46 | 101 | 100 | 9.0827
46 | 102 | 100 | 9.1053
46 | 103 | 100 | 9.128
46 | 104 | 100 | 9.1507
46 | 105 | 100 | 9.1733
46 | 106 | 100 | 9.196
46 | 107 | 100 | 9.2187
46 | 108 | 100 | 9.2413
46 | 109 | 100 | 9.264
46 | 110 | 100 | 9.2867
46 | 111 | 100 | 9.3093
46 | 112 | 100 | 9.332
46 | 113 | 100 | 9.3547
46 | 114 | 100 | 9.3773
46 | 115 | 100 | 9.4
46 | 116 | 100 | 9.4227
46 | 117 | 100 | 9.4453
46 | 118 | 100 | 9.468
46 | 119 | 100 | 9.4907
46 | 120 | 100 | 9.5133
46 | 121 | 100 | 9.536
46 | 122 | 100 | 9.5587
46 | 123 | 100 | 9.5813
46 | 124 | 100 | 9.604
46 | 125 | 100 | 9.6267
46 | 126 | 100 | 9.6621
46 | 127 | 100 | 9.6976
46 | 128 | 100 | 9.7331
46 | 129 | 100 | 9.7685
46 | 130 | 100 | 9.804
46 | 131 | 100 | 9.8395
46 | 132 | 100 | 9.8749
46 | 133 | 100 | 9.9104
46 | 134 | 100 | 9.9459
46 | 135 | 100 | 9.9813
46 | 136 | 100 | 10.0168
46 | 137 | 100 | 10.0523
46 | 138 | 100 | 10.0877
46 | 139 | 100 | 10.1232
46 | 140 | 100 | 10.1587
46 | 141 | 100 | 10.1941
46 | 142 | 100 | 10.2296
46 | 143 | 100 | 10.2651
46 | 144 | 100 | 10.3005
46 | 145 | 100 | 10.336
46 | 146 | 100 | 10.3715
46 | 147 | 100 | 10.4069
46 | 148 | 100 | 10.4424
46 | 149 | 100 | 10.4779
46 | 150 | 100 | 10.5133
47 | 45 | 100 | 6.54
47 | 46 | 100 | 6.5953
47 | 47 | 100 | 6.6507
47 | 48 | 100 | 6.706
47 | 49 | 100 | 6.7613
47 | 50 | 100 | 6.8167
47 | 51 | 100 | 6.872
47 | 52 | 100 | 6.9273
47 | 53 | 100 | 6.9827
47 | 54 | 100 | 7.038
47 | 55 | 100 | 7.0933
47 | 56 | 100 | 7.1487
47 | 57 | 100 | 7.204
47 | 58 | 100 | 7.2593
47 | 59 | 100 | 7.3147
47 | 60 | 100 | 7.37
47 | 61 | 100 | 7.4253
47 | 62 | 100 | 7.4807
47 | 63 | 100 | 7.536
47 | 64 | 100 | 7.5913
47 | 65 | 100 | 7.6467
47 | 66 | 100 | 7.702
47 | 67 | 100 | 7.7573
47 | 68 | 100 | 7.8127
47 | 69 | 100 | 7.868
47 | 70 | 100 | 7.9233
47 | 71 | 100 | 7.9787
47 | 72 | 100 | 8.034
47 | 73 | 100 | 8.0893
47 | 74 | 100 | 8.1447
47 | 75 | 100 | 8.2
47 | 76 | 100 | 8.2368
47 | 77 | 100 | 8.2736
47 | 78 | 100 | 8.3104
47 | 79 | 100 | 8.3472
47 | 80 | 100 | 8.384
47 | 81 | 100 | 8.4208
47 | 82 | 100 | 8.4576
47 | 83 | 100 | 8.4944
47 | 84 | 100 | 8.5312
47 | 85 | 100 | 8.568
47 | 86 | 100 | 8.6048
47 | 87 | 100 | 8.6416
47 | 88 | 100 | 8.6784
47 | 89 | 100 | 8.7152
47 | 90 | 100 | 8.752
47 | 91 | 100 | 8.7888
47 | 92 | 100 | 8.8256
47 | 93 | 100 | 8.8624
47 | 94 | 100 | 8.8992
47 | 95 | 100 | 8.936
47 | 96 | 100 | 8.9728
47 | 97 | 100 | 9.0096
47 | 98 | 100 | 9.0464
47 | 99 | 100 | 9.0832
47 | 100 | 100 | 9.12
47 | 101 | 100 | 9.1413
47 | 102 | 100 | 9.1627
47 | 103 | 100 | 9.184
47 | 104 | 100 | 9.2053
47 | 105 | 100 | 9.2267
47 | 106 | 100 | 9.248
47 | 107 | 100 | 9.2693
47 | 108 | 100 | 9.2907
47 | 109 | 100 | 9.312
47 | 110 | 100 | 9.3333
47 | 111 | 100 | 9.3547
47 | 112 | 100 | 9.376
47 | 113 | 100 | 9.3973
47 | 114 | 100 | 9.4187
47 | 115 | 100 | 9.44
47 | 116 | 100 | 9.4613
47 | 117 | 100 | 9.4827
47 | 118 | 100 | 9.504
47 | 119 | 100 | 9.5253
47 | 120 | 100 | 9.5467
47 | 121 | 100 | 9.568
47 | 122 | 100 | 9.5893
47 | 123 | 100 | 9.6107
47 | 124 | 100 | 9.632
47 | 125 | 100 | 9.6533
47 | 126 | 100 | 9.6883
47 | 127 | 100 | 9.7232
47 | 128 | 100 | 9.7581
47 | 129 | 100 | 9.7931
47 | 130 | 100 | 9.828
47 | 131 | 100 | 9.8629
47 | 132 | 100 | 9.8979
47 | 133 | 100 | 9.9328
47 | 134 | 100 | 9.9677
47 | 135 | 100 | 10.0027
47 | 136 | 100 | 10.0376
47 | 137 | 100 | 10.0725
47 | 138 | 100 | 10.1075
47 | 139 | 100 | 10.1424
47 | 140 | 100 | 10.1773
47 | 141 | 100 | 10.2123
47 | 142 | 100 | 10.2472
47 | 143 | 100 | 10.2821
47 | 144 | 100 | 10.3171
47 | 145 | 100 | 10.352
47 | 146 | 100 | 10.3869
47 | 147 | 100 | 10.4219
47 | 148 | 100 | 10.4568
47 | 149 | 100 | 10.4917
47 | 150 | 100 | 10.5267
48 | 45 | 100 | 6.56
48 | 46 | 100 | 6.6147
48 | 47 | 100 | 6.6693
48 | 48 | 100 | 6.724
48 | 49 | 100 | 6.7787
48 | 50 | 100 | 6.8333
48 | 51 | 100 | 6.888
48 | 52 | 100 | 6.9427
48 | 53 | 100 | 6.9973
48 | 54 | 100 | 7.052
48 | 55 | 100 | 7.1067
48 | 56 | 100 | 7.1613
48 | 57 | 100 | 7.216
48 | 58 | 100 | 7.2707
48 | 59 | 100 | 7.3253
48 | 60 | 100 | 7.38
48 | 61 | 100 | 7.4347
48 | 62 | 100 | 7.4893
48 | 63 | 100 | 7.544
48 | 64 | 100 | 7.5987
48 | 65 | 100 | 7.6533
48 | 66 | 100 | 7.708
48 | 67 | 100 | 7.7627
48 | 68 | 100 | 7.8173
48 | 69 | 100 | 7.872
48 | 70 | 100 | 7.9267
48 | 71 | 100 | 7.9813
48 | 72 | 100 | 8.036
48 | 73 | 100 | 8.0907
48 | 74 | 100 | 8.1453
48 | 75 | 100 | 8.2
48 | 76 | 100 | 8.2392
48 | 77 | 100 | 8.2784
48 | 78 | 100 | 8.3176
48 | 79 | 100 | 8.3568
48 | 80 | 100 | 8.396
48 | 81 | 100 | 8.4352
48 | 82 | 100 | 8.4744
48 | 83 | 100 | 8.5136
48 | 84 | 100 | 8.5528
48 | 85 | 100 | 8.592
48 | 86 | 100 | 8.6312
48 | 87 | 100 | 8.6704
48 | 88 | 100 | 8.7096
48 | 89 | 100 | 8.7488
48 | 90 | 100 | 8.788
48 | 91 | 100 | 8.8272
48 | 92 | 100 | 8.8664
48 | 93 | 100 | 8.9056
48 | 94 | 100 | 8.9448
48 | 95 | 100 | 8.984
48 | 96 | 100 | 9.0232
48 | 97 | 100 | 9.0624
48 | 98 | 100 | 9.1016
48 | 99 | 100 | 9.1408
48 | 100 | 100 | 9.18
48 | 101 | 100 | 9.2
48 | 102 | 100 | 9.22
48 | 103 | 100 | 9.24
48 | 104 | 100 | 9.26
48 | 105 | 100 | 9.28
48 | 106 | 100 | 9.3
48 | 107 | 100 | 9.32
48 | 108 | 100 | 9.34
48 | 109 | 100 | 9.36
48 | 110 | 100 | 9.38
48 | 111 | 100 | 9.4
48 | 112 | 100 | 9.42
48 | 113 | 100 | 9.44
48 | 114 | 100 | 9.46
48 | 115 | 100 | 9.48
48 | 116 | 100 | 9.5
48 | 117 | 100 | 9.52
48 | 118 | 100 | 9.54
48 | 119 | 100 | 9.56
48 | 120 | 100 | 9.58
48 | 121 | 100 | 9.6
48 | 122 | 100 | 9.62
48 | 123 | 100 | 9.64
48 | 124 | 100 | 9.66
48 | 125 | 100 | 9.68
48 | 126 | 100 | 9.7144
48 | 127 | 100 | 9.7488
48 | 128 | 100 | 9.7832
48 | 129 | 100 | 9.8176
48 | 130 | 100 | 9.852
48 | 131 | 100 | 9.8864
48 | 132 | 100 | 9.9208
48 | 133 | 100 | 9.9552
48 | 134 | 100 | 9.9896
48 | 135 | 100 | 10.024
48 | 136 | 100 | 10.0584
48 | 137 | 100 | 10.0928
48 | 138 | 100 | 10.1272
48 | 139 | 100 | 10.1616
48 | 140 | 100 | 10.196
48 | 141 | 100 | 10.2304
48 | 142 | 100 | 10.2648
48 | 143 | 100 | 10.2992
48 | 144 | 100 | 10.3336
48 | 145 | 100 | 10.368
48 | 146 | 100 | 10.4024
48 | 147 | 100 | 10.4368
48 | 148 | 100 | 10.4712
48 | 149 | 100 | 10.5056
48 | 150 | 100 | 10.54
49 | 45 | 100 | 6.58
49 | 46 | 100 | 6.634
49 | 47 | 100 | 6.688
49 | 48 | 100 | 6.742
49 | 49 | 100 | 6.796
49 | 50 | 100 | 6.85
49 | 51 | 100 | 6.904
49 | 52 | 100 | 6.958
49 | 53 | 100 | 7.012
49 | 54 | 100 | 7.066
49 | 55 | 100 | 7.12
49 | 56 | 100 | 7.174
49 | 57 | 100 | 7.228
49 | 58 | 100 | 7.282
49 | 59 | 100 | 7.336
49 | 60 | 100 | 7.39
49 | 61 | 100 | 7.444
49 | 62 | 100 | 7.498
49 | 63 | 100 | 7.552
49 | 64 | 100 | 7.606
49 | 65 | 100 | 7.66
49 | 66 | 100 | 7.714
49 | 67 | 100 | 7.768
49 | 68 | 100 | 7.822
49 | 69 | 100 | 7.876
49 | 70 | 100 | 7.93
49 | 71 | 100 | 7.984
49 | 72 | 100 | 8.038
49 | 73 | 100 | 8.092
49 | 74 | 100 | 8.146
49 | 75 | 100 | 8.2
49 | 76 | 100 | 8.2416
49 | 77 | 100 | 8.2832
49 | 78 | 100 | 8.3248
49 | 79 | 100 | 8.3664
49 | 80 | 100 | 8.408
49 | 81 | 100 | 8.4496
49 | 82 | 100 | 8.4912
49 | 83 | 100 | 8.5328
49 | 84 | 100 | 8.5744
49 | 85 | 100 | 8.616
49 | 86 | 100 | 8.6576
49 | 87 | 100 | 8.6992
49 | 88 | 100 | 8.7408
49 | 89 | 100 | 8.7824
49 | 90 | 100 | 8.824
49 | 91 | 100 | 8.8656
49 | 92 | 100 | 8.9072
49 | 93 | 100 | 8.9488
49 | 94 | 100 | 8.9904
49 | 95 | 100 | 9.032
49 | 96 | 100 | 9.0736
49 | 97 | 100 | 9.1152
49 | 98 | 100 | 9.1568
49 | 99 | 100 | 9.1984
49 | 100 | 100 | 9.24
49 | 101 | 100 | 9.2587
49 | 102 | 100 | 9.2773
49 | 103 | 100 | 9.296
49 | 104 | 100 | 9.3147
49 | 105 | 100 | 9.3333
49 | 106 | 100 | 9.352
49 | 107 | 100 | 9.3707
49 | 108 | 100 | 9.3893
49 | 109 | 100 | 9.408
49 | 110 | 100 | 9.4267
49 | 111 | 100 | 9.4453
49 | 112 | 100 | 9.464
49 | 113 | 100 | 9.4827
49 | 114 | 100 | 9.5013
49 | 115 | 100 | 9.52
49 | 116 | 100 | 9.5387
49 | 117 | 100 | 9.5573
49 | 118 | 100 | 9.576
49 | 119 | 100 | 9.5947
49 | 120 | 100 | 9.6133
49 | 121 | 100 | 9.632
49 | 122 | 100 | 9.6507
49 | 123 | 100 | 9.6693
49 | 124 | 100 | 9.688
49 | 125 | 100 | 9.7067
49 | 126 | 100 | 9.7405
49 | 127 | 100 | 9.7744
49 | 128 | 100 | 9.8083
49 | 129 | 100 | 9.8421
49 | 130 | 100 | 9.876
49 | 131 | 100 | 9.9099
49 | 132 | 100 | 9.9437
49 | 133 | 100 | 9.9776
49 | 134 | 100 | 10.0115
49 | 135 | 100 | 10.0453
49 | 136 | 100 | 10.0792
49 | 137 | 100 | 10.1131
49 | 138 | 100 | 10.1469
49 | 139 | 100 | 10.1808
49 | 140 | 100 | 10.2147
49 | 141 | 100 | 10.2485
49 | 142 | 100 | 10.2824
49 | 143 | 100 | 10.3163
49 | 144 | 100 | 10.3501
49 | 145 | 100 | 10.384
49 | 146 | 100 | 10.4179
49 | 147 | 100 | 10.4517
49 | 148 | 100 | 10.4856
49 | 149 | 100 | 10.5195
49 | 150 | 100 | 10.5533
50 | 45 | 100 | 6.6
50 | 46 | 100 | 6.6533
50 | 47 | 100 | 6.7067
50 | 48 | 100 | 6.76
50 | 49 | 100 | 6.8133
50 | 50 | 100 | 6.8667
50 | 51 | 100 | 6.92
50 | 52 | 100 | 6.9733
50 | 53 | 100 | 7.0267
50 | 54 | 100 | 7.08
50 | 55 | 100 | 7.1333
50 | 56 | 100 | 7.1867
50 | 57 | 100 | 7.24
50 | 58 | 100 | 7.2933
50 | 59 | 100 | 7.3467
50 | 60 | 100 | 7.4
50 | 61 | 100 | 7.4533
50 | 62 | 100 | 7.5067
50 | 63 | 100 | 7.56
50 | 64 | 100 | 7.6133
50 | 65 | 100 | 7.6667
50 | 66 | 100 | 7.72
50 | 67 | 100 | 7.7733
50 | 68 | 100 | 7.8267
50 | 69 | 100 | 7.88
50 | 70 | 100 | 7.9333
50 | 71 | 100 | 7.9867
50 | 72 | 100 | 8.04
50 | 73 | 100 | 8.0933
50 | 74 | 100 | 8.1467
50 | 75 | 100 | 8.2
50 | 76 | 100 | 8.244
50 | 77 | 100 | 8.288
50 | 78 | 100 | 8.332
50 | 79 | 100 | 8.376
50 | 80 | 100 | 8.42
50 | 81 | 100 | 8.464
50 | 82 | 100 | 8.508
50 | 83 | 100 | 8.552
50 | 84 | 100 | 8.596
50 | 85 | 100 | 8.64
50 | 86 | 100 | 8.684
50 | 87 | 100 | 8.728
50 | 88 | 100 | 8.772
50 | 89 | 100 | 8.816
50 | 90 | 100 | 8.86
50 | 91 | 100 | 8.904
50 | 92 | 100 | 8.948
50 | 93 | 100 | 8.992
50 | 94 | 100 | 9.036
50 | 95 | 100 | 9.08
50 | 96 | 100 | 9.124
50 | 97 | 100 | 9.168
50 | 98 | 100 | 9.212
50 | 99 | 100 | 9.256
50 | 100 | 100 | 9.3
50 | 101 | 100 | 9.3173
50 | 102 | 100 | 9.3347
50 | 103 | 100 | 9.352
50 | 104 | 100 | 9.3693
50 | 105 | 100 | 9.3867
50 | 106 | 100 | 9.404
50 | 107 | 100 | 9.4213
50 | 108 | 100 | 9.4387
50 | 109 | 100 | 9.456
50 | 110 | 100 | 9.4733
50 | 111 | 100 | 9.4907
50 | 112 | 100 | 9.508
50 | 113 | 100 | 9.5253
50 | 114 | 100 | 9.5427
50 | 115 | 100 | 9.56
50 | 116 | 100 | 9.5773
50 | 117 | 100 | 9.5947
50 | 118 | 100 | 9.612
50 | 119 | 100 | 9.6293
50 | 120 | 100 | 9.6467
50 | 121 | 100 | 9.664
50 | 122 | 100 | 9.6813
50 | 123 | 100 | 9.6987
50 | 124 | 100 | 9.716
50 | 125 | 100 | 9.7333
50 | 126 | 100 | 9.7667
50 | 127 | 100 | 9.8
50 | 128 | 100 | 9.8333
50 | 129 | 100 | 9.8667
50 | 130 | 100 | 9.9
50 | 131 | 100 | 9.9333
50 | 132 | 100 | 9.9667
50 | 133 | 100 | 10
50 | 134 | 100 | 10.0333
50 | 135 | 100 | 10.0667
50 | 136 | 100 | 10.1
50 | 137 | 100 | 10.1333
50 | 138 | 100 | 10.1667
50 | 139 | 100 | 10.2
50 | 140 | 100 | 10.2333
50 | 141 | 100 | 10.2667
50 | 142 | 100 | 10.3
50 | 143 | 100 | 10.3333
50 | 144 | 100 | 10.3667
50 | 145 | 100 | 10.4
50 | 146 | 100 | 10.4333
50 | 147 | 100 | 10.4667
50 | 148 | 100 | 10.5
50 | 149 | 100 | 10.5333
50 | 150 | 100 | 10.5667
51 | 45 | 100 | 6.62
51 | 46 | 100 | 6.6727
51 | 47 | 100 | 6.7253
51 | 48 | 100 | 6.778
51 | 49 | 100 | 6.8307
51 | 50 | 100 | 6.8833
51 | 51 | 100 | 6.936
51 | 52 | 100 | 6.9887
51 | 53 | 100 | 7.0413
51 | 54 | 100 | 7.094
51 | 55 | 100 | 7.1467
51 | 56 | 100 | 7.1993
51 | 57 | 100 | 7.252
51 | 58 | 100 | 7.3047
51 | 59 | 100 | 7.3573
51 | 60 | 100 | 7.41
51 | 61 | 100 | 7.4627
51 | 62 | 100 | 7.5153
51 | 63 | 100 | 7.568
51 | 64 | 100 | 7.6207
51 | 65 | 100 | 7.6733
51 | 66 | 100 | 7.726
51 | 67 | 100 | 7.7787
51 | 68 | 100 | 7.8313
51 | 69 | 100 | 7.884
51 | 70 | 100 | 7.9367
51 | 71 | 100 | 7.9893
51 | 72 | 100 | 8.042
51 | 73 | 100 | 8.0947
51 | 74 | 100 | 8.1473
51 | 75 | 100 | 8.2
51 | 76 | 100 | 8.2464
51 | 77 | 100 | 8.2928
51 | 78 | 100 | 8.3392
51 | 79 | 100 | 8.3856
51 | 80 | 100 | 8.432
51 | 81 | 100 | 8.4784
51 | 82 | 100 | 8.5248
51 | 83 | 100 | 8.5712
51 | 84 | 100 | 8.6176
51 | 85 | 100 | 8.664
51 | 86 | 100 | 8.7104
51 | 87 | 100 | 8.7568
51 | 88 | 100 | 8.8032
51 | 89 | 100 | 8.8496
51 | 90 | 100 | 8.896
51 | 91 | 100 | 8.9424
51 | 92 | 100 | 8.9888
51 | 93 | 100 | 9.0352
51 | 94 | 100 | 9.0816
51 | 95 | 100 | 9.128
51 | 96 | 100 | 9.1744
51 | 97 | 100 | 9.2208
51 | 98 | 100 | 9.2672
51 | 99 | 100 | 9.3136
51 | 100 | 100 | 9.36
51 | 101 | 100 | 9.376
51 | 102 | 100 | 9.392
51 | 103 | 100 | 9.408
51 | 104 | 100 | 9.424
51 | 105 | 100 | 9.44
51 | 106 | 100 | 9.456
51 | 107 | 100 | 9.472
51 | 108 | 100 | 9.488
51 | 109 | 100 | 9.504
51 | 110 | 100 | 9.52
51 | 111 | 100 | 9.536
51 | 112 | 100 | 9.552
51 | 113 | 100 | 9.568
51 | 114 | 100 | 9.584
51 | 115 | 100 | 9.6
51 | 116 | 100 | 9.616
51 | 117 | 100 | 9.632
51 | 118 | 100 | 9.648
51 | 119 | 100 | 9.664
51 | 120 | 100 | 9.68
51 | 121 | 100 | 9.696
51 | 122 | 100 | 9.712
51 | 123 | 100 | 9.728
51 | 124 | 100 | 9.744
51 | 125 | 100 | 9.76
51 | 126 | 100 | 9.7928
51 | 127 | 100 | 9.8256
51 | 128 | 100 | 9.8584
51 | 129 | 100 | 9.8912
51 | 130 | 100 | 9.924
51 | 131 | 100 | 9.9568
51 | 132 | 100 | 9.9896
51 | 133 | 100 | 10.0224
51 | 134 | 100 | 10.0552
51 | 135 | 100 | 10.088
51 | 136 | 100 | 10.1208
51 | 137 | 100 | 10.1536
51 | 138 | 100 | 10.1864
51 | 139 | 100 | 10.2192
51 | 140 | 100 | 10.252
51 | 141 | 100 | 10.2848
51 | 142 | 100 | 10.3176
51 | 143 | 100 | 10.3504
51 | 144 | 100 | 10.3832
51 | 145 | 100 | 10.416
51 | 146 | 100 | 10.4488
51 | 147 | 100 | 10.4816
51 | 148 | 100 | 10.5144
51 | 149 | 100 | 10.5472
51 | 150 | 100 | 10.58
52 | 45 | 100 | 6.64
52 | 46 | 100 | 6.692
52 | 47 | 100 | 6.744
52 | 48 | 100 | 6.796
52 | 49 | 100 | 6.848
52 | 50 | 100 | 6.9
52 | 51 | 100 | 6.952
52 | 52 | 100 | 7.004
52 | 53 | 100 | 7.056
52 | 54 | 100 | 7.108
52 | 55 | 100 | 7.16
52 | 56 | 100 | 7.212
52 | 57 | 100 | 7.264
52 | 58 | 100 | 7.316
52 | 59 | 100 | 7.368
52 | 60 | 100 | 7.42
52 | 61 | 100 | 7.472
52 | 62 | 100 | 7.524
52 | 63 | 100 | 7.576
52 | 64 | 100 | 7.628
52 | 65 | 100 | 7.68
52 | 66 | 100 | 7.732
52 | 67 | 100 | 7.784
52 | 68 | 100 | 7.836
52 | 69 | 100 | 7.888
52 | 70 | 100 | 7.94
52 | 71 | 100 | 7.992
52 | 72 | 100 | 8.044
52 | 73 | 100 | 8.096
52 | 74 | 100 | 8.148
52 | 75 | 100 | 8.2
52 | 76 | 100 | 8.2488
52 | 77 | 100 | 8.2976
52 | 78 | 100 | 8.3464
52 | 79 | 100 | 8.3952
52 | 80 | 100 | 8.444
52 | 81 | 100 | 8.4928
52 | 82 | 100 | 8.5416
52 | 83 | 100 | 8.5904
52 | 84 | 100 | 8.6392
52 | 85 | 100 | 8.688
52 | 86 | 100 | 8.7368
52 | 87 | 100 | 8.7856
52 | 88 | 100 | 8.8344
52 | 89 | 100 | 8.8832
52 | 90 | 100 | 8.932
52 | 91 | 100 | 8.9808
52 | 92 | 100 | 9.0296
52 | 93 | 100 | 9.0784
52 | 94 | 100 | 9.1272
52 | 95 | 100 | 9.176
52 | 96 | 100 | 9.2248
52 | 97 | 100 | 9.2736
52 | 98 | 100 | 9.3224
52 | 99 | 100 | 9.3712
52 | 100 | 100 | 9.42
52 | 101 | 100 | 9.4347
52 | 102 | 100 | 9.4493
52 | 103 | 100 | 9.464
52 | 104 | 100 | 9.4787
52 | 105 | 100 | 9.4933
52 | 106 | 100 | 9.508
52 | 107 | 100 | 9.5227
52 | 108 | 100 | 9.5373
52 | 109 | 100 | 9.552
52 | 110 | 100 | 9.5667
52 | 111 | 100 | 9.5813
52 | 112 | 100 | 9.596
52 | 113 | 100 | 9.6107
52 | 114 | 100 | 9.6253
52 | 115 | 100 | 9.64
52 | 116 | 100 | 9.6547
52 | 117 | 100 | 9.6693
52 | 118 | 100 | 9.684
52 | 119 | 100 | 9.6987
52 | 120 | 100 | 9.7133
52 | 121 | 100 | 9.728
52 | 122 | 100 | 9.7427
52 | 123 | 100 | 9.7573
52 | 124 | 100 | 9.772
52 | 125 | 100 | 9.7867
52 | 126 | 100 | 9.8189
52 | 127 | 100 | 9.8512
52 | 128 | 100 | 9.8835
52 | 129 | 100 | 9.9157
52 | 130 | 100 | 9.948
52 | 131 | 100 | 9.9803
52 | 132 | 100 | 10.0125
52 | 133 | 100 | 10.0448
52 | 134 | 100 | 10.0771
52 | 135 | 100 | 10.1093
52 | 136 | 100 | 10.1416
52 | 137 | 100 | 10.1739
52 | 138 | 100 | 10.2061
52 | 139 | 100 | 10.2384
52 | 140 | 100 | 10.2707
52 | 141 | 100 | 10.3029
52 | 142 | 100 | 10.3352
52 | 143 | 100 | 10.3675
52 | 144 | 100 | 10.3997
52 | 145 | 100 | 10.432
52 | 146 | 100 | 10.4643
52 | 147 | 100 | 10.4965
52 | 148 | 100 | 10.5288
52 | 149 | 100 | 10.5611
52 | 150 | 100 | 10.5933
53 | 45 | 100 | 6.66
53 | 46 | 100 | 6.7113
53 | 47 | 100 | 6.7627
53 | 48 | 100 | 6.814
53 | 49 | 100 | 6.8653
53 | 50 | 100 | 6.9167
53 | 51 | 100 | 6.968
53 | 52 | 100 | 7.0193
53 | 53 | 100 | 7.0707
53 | 54 | 100 | 7.122
53 | 55 | 100 | 7.1733
53 | 56 | 100 | 7.2247
53 | 57 | 100 | 7.276
53 | 58 | 100 | 7.3273
53 | 59 | 100 | 7.3787
53 | 60 | 100 | 7.43
53 | 61 | 100 | 7.4813
53 | 62 | 100 | 7.5327
53 | 63 | 100 | 7.584
53 | 64 | 100 | 7.6353
53 | 65 | 100 | 7.6867
53 | 66 | 100 | 7.738
53 | 67 | 100 | 7.7893
53 | 68 | 100 | 7.8407
53 | 69 | 100 | 7.892
53 | 70 | 100 | 7.9433
53 | 71 | 100 | 7.9947
53 | 72 | 100 | 8.046
53 | 73 | 100 | 8.0973
53 | 74 | 100 | 8.1487
53 | 75 | 100 | 8.2
53 | 76 | 100 | 8.2512
53 | 77 | 100 | 8.3024
53 | 78 | 100 | 8.3536
53 | 79 | 100 | 8.4048
53 | 80 | 100 | 8.456
53 | 81 | 100 | 8.5072
53 | 82 | 100 | 8.5584
53 | 83 | 100 | 8.6096
53 | 84 | 100 | 8.6608
53 | 85 | 100 | 8.712
53 | 86 | 100 | 8.7632
53 | 87 | 100 | 8.8144
53 | 88 | 100 | 8.8656
53 | 89 | 100 | 8.9168
53 | 90 | 100 | 8.968
53 | 91 | 100 | 9.0192
53 | 92 | 100 | 9.0704
53 | 93 | 100 | 9.1216
53 | 94 | 100 | 9.1728
53 | 95 | 100 | 9.224
53 | 96 | 100 | 9.2752
53 | 97 | 100 | 9.3264
53 | 98 | 100 | 9.3776
53 | 99 | 100 | 9.4288
53 | 100 | 100 | 9.48
53 | 101 | 100 | 9.4933
53 | 102 | 100 | 9.5067
53 | 103 | 100 | 9.52
53 | 104 | 100 | 9.5333
53 | 105 | 100 | 9.5467
53 | 106 | 100 | 9.56
53 | 107 | 100 | 9.5733
53 | 108 | 100 | 9.5867
53 | 109 | 100 | 9.6
53 | 110 | 100 | 9.6133
53 | 111 | 100 | 9.6267
53 | 112 | 100 | 9.64
53 | 113 | 100 | 9.6533
53 | 114 | 100 | 9.6667
53 | 115 | 100 | 9.68
53 | 116 | 100 | 9.6933
53 | 117 | 100 | 9.7067
53 | 118 | 100 | 9.72
53 | 119 | 100 | 9.7333
53 | 120 | 100 | 9.7467
53 | 121 | 100 | 9.76
53 | 122 | 100 | 9.7733
53 | 123 | 100 | 9.7867
53 | 124 | 100 | 9.8
53 | 125 | 100 | 9.8133
53 | 126 | 100 | 9.8451
53 | 127 | 100 | 9.8768
53 | 128 | 100 | 9.9085
53 | 129 | 100 | 9.9403
53 | 130 | 100 | 9.972
53 | 131 | 100 | 10.0037
53 | 132 | 100 | 10.0355
53 | 133 | 100 | 10.0672
53 | 134 | 100 | 10.0989
53 | 135 | 100 | 10.1307
53 | 136 | 100 | 10.1624
53 | 137 | 100 | 10.1941
53 | 138 | 100 | 10.2259
53 | 139 | 100 | 10.2576
53 | 140 | 100 | 10.2893
53 | 141 | 100 | 10.3211
53 | 142 | 100 | 10.3528
53 | 143 | 100 | 10.3845
53 | 144 | 100 | 10.4163
53 | 145 | 100 | 10.448
53 | 146 | 100 | 10.4797
53 | 147 | 100 | 10.5115
53 | 148 | 100 | 10.5432
53 | 149 | 100 | 10.5749
53 | 150 | 100 | 10.6067
54 | 45 | 100 | 6.68
54 | 46 | 100 | 6.7307
54 | 47 | 100 | 6.7813
54 | 48 | 100 | 6.832
54 | 49 | 100 | 6.8827
54 | 50 | 100 | 6.9333
54 | 51 | 100 | 6.984
54 | 52 | 100 | 7.0347
54 | 53 | 100 | 7.0853
54 | 54 | 100 | 7.136
54 | 55 | 100 | 7.1867
54 | 56 | 100 | 7.2373
54 | 57 | 100 | 7.288
54 | 58 | 100 | 7.3387
54 | 59 | 100 | 7.3893
54 | 60 | 100 | 7.44
54 | 61 | 100 | 7.4907
54 | 62 | 100 | 7.5413
54 | 63 | 100 | 7.592
54 | 64 | 100 | 7.6427
54 | 65 | 100 | 7.6933
54 | 66 | 100 | 7.744
54 | 67 | 100 | 7.7947
54 | 68 | 100 | 7.8453
54 | 69 | 100 | 7.896
54 | 70 | 100 | 7.9467
54 | 71 | 100 | 7.9973
54 | 72 | 100 | 8.048
54 | 73 | 100 | 8.0987
54 | 74 | 100 | 8.1493
54 | 75 | 100 | 8.2
54 | 76 | 100 | 8.2536
54 | 77 | 100 | 8.3072
54 | 78 | 100 | 8.3608
54 | 79 | 100 | 8.4144
54 | 80 | 100 | 8.468
54 | 81 | 100 | 8.5216
54 | 82 | 100 | 8.5752
54 | 83 | 100 | 8.6288
54 | 84 | 100 | 8.6824
54 | 85 | 100 | 8.736
54 | 86 | 100 | 8.7896
54 | 87 | 100 | 8.8432
54 | 88 | 100 | 8.8968
54 | 89 | 100 | 8.9504
54 | 90 | 100 | 9.004
54 | 91 | 100 | 9.0576
54 | 92 | 100 | 9.1112
54 | 93 | 100 | 9.1648
54 | 94 | 100 | 9.2184
54 | 95 | 100 | 9.272
54 | 96 | 100 | 9.3256
54 | 97 | 100 | 9.3792
54 | 98 | 100 | 9.4328
54 | 99 | 100 | 9.4864
54 | 100 | 100 | 9.54
54 | 101 | 100 | 9.552
54 | 102 | 100 | 9.564
54 | 103 | 100 | 9.576
54 | 104 | 100 | 9.588
54 | 105 | 100 | 9.6
54 | 106 | 100 | 9.612
54 | 107 | 100 | 9.624
54 | 108 | 100 | 9.636
54 | 109 | 100 | 9.648
54 | 110 | 100 | 9.66
54 | 111 | 100 | 9.672
54 | 112 | 100 | 9.684
54 | 113 | 100 | 9.696
54 | 114 | 100 | 9.708
54 | 115 | 100 | 9.72
54 | 116 | 100 | 9.732
54 | 117 | 100 | 9.744
54 | 118 | 100 | 9.756
54 | 119 | 100 | 9.768
54 | 120 | 100 | 9.78
54 | 121 | 100 | 9.792
54 | 122 | 100 | 9.804
54 | 123 | 100 | 9.816
54 | 124 | 100 | 9.828
54 | 125 | 100 | 9.84
54 | 126 | 100 | 9.8712
54 | 127 | 100 | 9.9024
54 | 128 | 100 | 9.9336
54 | 129 | 100 | 9.9648
54 | 130 | 100 | 9.996
54 | 131 | 100 | 10.0272
54 | 132 | 100 | 10.0584
54 | 133 | 100 | 10.0896
54 | 134 | 100 | 10.1208
54 | 135 | 100 | 10.152
54 | 136 | 100 | 10.1832
54 | 137 | 100 | 10.2144
54 | 138 | 100 | 10.2456
54 | 139 | 100 | 10.2768
54 | 140 | 100 | 10.308
54 | 141 | 100 | 10.3392
54 | 142 | 100 | 10.3704
54 | 143 | 100 | 10.4016
54 | 144 | 100 | 10.4328
54 | 145 | 100 | 10.464
54 | 146 | 100 | 10.4952
54 | 147 | 100 | 10.5264
54 | 148 | 100 | 10.5576
54 | 149 | 100 | 10.5888
54 | 150 | 100 | 10.62
55 | 45 | 100 | 6.7
55 | 46 | 100 | 6.75
55 | 47 | 100 | 6.8
55 | 48 | 100 | 6.85
55 | 49 | 100 | 6.9
55 | 50 | 100 | 6.95
55 | 51 | 100 | 7
55 | 52 | 100 | 7.05
55 | 53 | 100 | 7.1
55 | 54 | 100 | 7.15
55 | 55 | 100 | 7.2
55 | 56 | 100 | 7.25
55 | 57 | 100 | 7.3
55 | 58 | 100 | 7.35
55 | 59 | 100 | 7.4
55 | 60 | 100 | 7.45
55 | 61 | 100 | 7.5
55 | 62 | 100 | 7.55
55 | 63 | 100 | 7.6
55 | 64 | 100 | 7.65
55 | 65 | 100 | 7.7
55 | 66 | 100 | 7.75
55 | 67 | 100 | 7.8
55 | 68 | 100 | 7.85
55 | 69 | 100 | 7.9
55 | 70 | 100 | 7.95
55 | 71 | 100 | 8
55 | 72 | 100 | 8.05
55 | 73 | 100 | 8.1
55 | 74 | 100 | 8.15
55 | 75 | 100 | 8.2
55 | 76 | 100 | 8.256
55 | 77 | 100 | 8.312
55 | 78 | 100 | 8.368
55 | 79 | 100 | 8.424
55 | 80 | 100 | 8.48
55 | 81 | 100 | 8.536
55 | 82 | 100 | 8.592
55 | 83 | 100 | 8.648
55 | 84 | 100 | 8.704
55 | 85 | 100 | 8.76
55 | 86 | 100 | 8.816
55 | 87 | 100 | 8.872
55 | 88 | 100 | 8.928
55 | 89 | 100 | 8.984
55 | 90 | 100 | 9.04
55 | 91 | 100 | 9.096
55 | 92 | 100 | 9.152
55 | 93 | 100 | 9.208
55 | 94 | 100 | 9.264
55 | 95 | 100 | 9.32
55 | 96 | 100 | 9.376
55 | 97 | 100 | 9.432
55 | 98 | 100 | 9.488
55 | 99 | 100 | 9.544
55 | 100 | 100 | 9.6
55 | 101 | 100 | 9.6107
55 | 102 | 100 | 9.6213
55 | 103 | 100 | 9.632
55 | 104 | 100 | 9.6427
55 | 105 | 100 | 9.6533
55 | 106 | 100 | 9.664
55 | 107 | 100 | 9.6747
55 | 108 | 100 | 9.6853
55 | 109 | 100 | 9.696
55 | 110 | 100 | 9.7067
55 | 111 | 100 | 9.7173
55 | 112 | 100 | 9.728
55 | 113 | 100 | 9.7387
55 | 114 | 100 | 9.7493
55 | 115 | 100 | 9.76
55 | 116 | 100 | 9.7707
55 | 117 | 100 | 9.7813
55 | 118 | 100 | 9.792
55 | 119 | 100 | 9.8027
55 | 120 | 100 | 9.8133
55 | 121 | 100 | 9.824
55 | 122 | 100 | 9.8347
55 | 123 | 100 | 9.8453
55 | 124 | 100 | 9.856
55 | 125 | 100 | 9.8667
55 | 126 | 100 | 9.8973
55 | 127 | 100 | 9.928
55 | 128 | 100 | 9.9587
55 | 129 | 100 | 9.9893
55 | 130 | 100 | 10.02
55 | 131 | 100 | 10.0507
55 | 132 | 100 | 10.0813
55 | 133 | 100 | 10.112
55 | 134 | 100 | 10.1427
55 | 135 | 100 | 10.1733
55 | 136 | 100 | 10.204
55 | 137 | 100 | 10.2347
55 | 138 | 100 | 10.2653
55 | 139 | 100 | 10.296
55 | 140 | 100 | 10.3267
55 | 141 | 100 | 10.3573
55 | 142 | 100 | 10.388
55 | 143 | 100 | 10.4187
55 | 144 | 100 | 10.4493
55 | 145 | 100 | 10.48
55 | 146 | 100 | 10.5107
55 | 147 | 100 | 10.5413
55 | 148 | 100 | 10.572
55 | 149 | 100 | 10.6027
55 | 150 | 100 | 10.6333
56 | 45 | 100 | 6.72
56 | 46 | 100 | 6.7693
56 | 47 | 100 | 6.8187
56 | 48 | 100 | 6.868
56 | 49 | 100 | 6.9173
56 | 50 | 100 | 6.9667
56 | 51 | 100 | 7.016
56 | 52 | 100 | 7.0653
56 | 53 | 100 | 7.1147
56 | 54 | 100 | 7.164
56 | 55 | 100 | 7.2133
56 | 56 | 100 | 7.2627
56 | 57 | 100 | 7.312
56 | 58 | 100 | 7.3613
56 | 59 | 100 | 7.4107
56 | 60 | 100 | 7.46
56 | 61 | 100 | 7.5093
56 | 62 | 100 | 7.5587
56 | 63 | 100 | 7.608
56 | 64 | 100 | 7.6573
56 | 65 | 100 | 7.7067
56 | 66 | 100 | 7.756
56 | 67 | 100 | 7.8053
56 | 68 | 100 | 7.8547
56 | 69 | 100 | 7.904
56 | 70 | 100 | 7.9533
56 | 71 | 100 | 8.0027
56 | 72 | 100 | 8.052
56 | 73 | 100 | 8.1013
56 | 74 | 100 | 8.1507
56 | 75 | 100 | 8.2
56 | 76 | 100 | 8.2584
56 | 77 | 100 | 8.3168
56 | 78 | 100 | 8.3752
56 | 79 | 100 | 8.4336
56 | 80 | 100 | 8.492
56 | 81 | 100 | 8.5504
56 | 82 | 100 | 8.6088
56 | 83 | 100 | 8.6672
56 | 84 | 100 | 8.7256
56 | 85 | 100 | 8.784
56 | 86 | 100 | 8.8424
56 | 87 | 100 | 8.9008
56 | 88 | 100 | 8.9592
56 | 89 | 100 | 9.0176
56 | 90 | 100 | 9.076
56 | 91 | 100 | 9.1344
56 | 92 | 100 | 9.1928
56 | 93 | 100 | 9.2512
56 | 94 | 100 | 9.3096
56 | 95 | 100 | 9.368
56 | 96 | 100 | 9.4264
56 | 97 | 100 | 9.4848
56 | 98 | 100 | 9.5432
56 | 99 | 100 | 9.6016
56 | 100 | 100 | 9.66
56 | 101 | 100 | 9.6693
56 | 102 | 100 | 9.6787
56 | 103 | 100 | 9.688
56 | 104 | 100 | 9.6973
56 | 105 | 100 | 9.7067
56 | 106 | 100 | 9.716
56 | 107 | 100 | 9.7253
56 | 108 | 100 | 9.7347
56 | 109 | 100 | 9.744
56 | 110 | 100 | 9.7533
56 | 111 | 100 | 9.7627
56 | 112 | 100 | 9.772
56 | 113 | 100 | 9.7813
56 | 114 | 100 | 9.7907
56 | 115 | 100 | 9.8
56 | 116 | 100 | 9.8093
56 | 117 | 100 | 9.8187
56 | 118 | 100 | 9.828
56 | 119 | 100 | 9.8373
56 | 120 | 100 | 9.8467
56 | 121 | 100 | 9.856
56 | 122 | 100 | 9.8653
56 | 123 | 100 | 9.8747
56 | 124 | 100 | 9.884
56 | 125 | 100 | 9.8933
56 | 126 | 100 | 9.9235
56 | 127 | 100 | 9.9536
56 | 128 | 100 | 9.9837
56 | 129 | 100 | 10.0139
56 | 130 | 100 | 10.044
56 | 131 | 100 | 10.0741
56 | 132 | 100 | 10.1043
56 | 133 | 100 | 10.1344
56 | 134 | 100 | 10.1645
56 | 135 | 100 | 10.1947
56 | 136 | 100 | 10.2248
56 | 137 | 100 | 10.2549
56 | 138 | 100 | 10.2851
56 | 139 | 100 | 10.3152
56 | 140 | 100 | 10.3453
56 | 141 | 100 | 10.3755
56 | 142 | 100 | 10.4056
56 | 143 | 100 | 10.4357
56 | 144 | 100 | 10.4659
56 | 145 | 100 | 10.496
56 | 146 | 100 | 10.5261
56 | 147 | 100 | 10.5563
56 | 148 | 100 | 10.5864
56 | 149 | 100 | 10.6165
56 | 150 | 100 | 10.6467
57 | 45 | 100 | 6.74
57 | 46 | 100 | 6.7887
57 | 47 | 100 | 6.8373
57 | 48 | 100 | 6.886
57 | 49 | 100 | 6.9347
57 | 50 | 100 | 6.9833
57 | 51 | 100 | 7.032
57 | 52 | 100 | 7.0807
57 | 53 | 100 | 7.1293
57 | 54 | 100 | 7.178
57 | 55 | 100 | 7.2267
57 | 56 | 100 | 7.2753
57 | 57 | 100 | 7.324
57 | 58 | 100 | 7.3727
57 | 59 | 100 | 7.4213
57 | 60 | 100 | 7.47
57 | 61 | 100 | 7.5187
57 | 62 | 100 | 7.5673
57 | 63 | 100 | 7.616
57 | 64 | 100 | 7.6647
57 | 65 | 100 | 7.7133
57 | 66 | 100 | 7.762
57 | 67 | 100 | 7.8107
57 | 68 | 100 | 7.8593
57 | 69 | 100 | 7.908
57 | 70 | 100 | 7.9567
57 | 71 | 100 | 8.0053
57 | 72 | 100 | 8.054
57 | 73 | 100 | 8.1027
57 | 74 | 100 | 8.1513
57 | 75 | 100 | 8.2
57 | 76 | 100 | 8.2608
57 | 77 | 100 | 8.3216
57 | 78 | 100 | 8.3824
57 | 79 | 100 | 8.4432
57 | 80 | 100 | 8.504
57 | 81 | 100 | 8.5648
57 | 82 | 100 | 8.6256
57 | 83 | 100 | 8.6864
57 | 84 | 100 | 8.7472
57 | 85 | 100 | 8.808
57 | 86 | 100 | 8.8688
57 | 87 | 100 | 8.9296
57 | 88 | 100 | 8.9904
57 | 89 | 100 | 9.0512
57 | 90 | 100 | 9.112
57 | 91 | 100 | 9.1728
57 | 92 | 100 | 9.2336
57 | 93 | 100 | 9.2944
57 | 94 | 100 | 9.3552
57 | 95 | 100 | 9.416
57 | 96 | 100 | 9.4768
57 | 97 | 100 | 9.5376
57 | 98 | 100 | 9.5984
57 | 99 | 100 | 9.6592
57 | 100 | 100 | 9.72
57 | 101 | 100 | 9.728
57 | 102 | 100 | 9.736
57 | 103 | 100 | 9.744
57 | 104 | 100 | 9.752
57 | 105 | 100 | 9.76
57 | 106 | 100 | 9.768
57 | 107 | 100 | 9.776
57 | 108 | 100 | 9.784
57 | 109 | 100 | 9.792
57 | 110 | 100 | 9.8
57 | 111 | 100 | 9.808
57 | 112 | 100 | 9.816
57 | 113 | 100 | 9.824
57 | 114 | 100 | 9.832
57 | 115 | 100 | 9.84
57 | 116 | 100 | 9.848
57 | 117 | 100 | 9.856
57 | 118 | 100 | 9.864
57 | 119 | 100 | 9.872
57 | 120 | 100 | 9.88
57 | 121 | 100 | 9.888
57 | 122 | 100 | 9.896
57 | 123 | 100 | 9.904
57 | 124 | 100 | 9.912
57 | 125 | 100 | 9.92
57 | 126 | 100 | 9.9496
57 | 127 | 100 | 9.9792
57 | 128 | 100 | 10.0088
57 | 129 | 100 | 10.0384
57 | 130 | 100 | 10.068
57 | 131 | 100 | 10.0976
57 | 132 | 100 | 10.1272
57 | 133 | 100 | 10.1568
57 | 134 | 100 | 10.1864
57 | 135 | 100 | 10.216
57 | 136 | 100 | 10.2456
57 | 137 | 100 | 10.2752
57 | 138 | 100 | 10.3048
57 | 139 | 100 | 10.3344
57 | 140 | 100 | 10.364
57 | 141 | 100 | 10.3936
57 | 142 | 100 | 10.4232
57 | 143 | 100 | 10.4528
57 | 144 | 100 | 10.4824
57 | 145 | 100 | 10.512
57 | 146 | 100 | 10.5416
57 | 147 | 100 | 10.5712
57 | 148 | 100 | 10.6008
57 | 149 | 100 | 10.6304
57 | 150 | 100 | 10.66
58 | 45 | 100 | 6.76
58 | 46 | 100 | 6.808
58 | 47 | 100 | 6.856
58 | 48 | 100 | 6.904
58 | 49 | 100 | 6.952
58 | 50 | 100 | 7
58 | 51 | 100 | 7.048
58 | 52 | 100 | 7.096
58 | 53 | 100 | 7.144
58 | 54 | 100 | 7.192
58 | 55 | 100 | 7.24
58 | 56 | 100 | 7.288
58 | 57 | 100 | 7.336
58 | 58 | 100 | 7.384
58 | 59 | 100 | 7.432
58 | 60 | 100 | 7.48
58 | 61 | 100 | 7.528
58 | 62 | 100 | 7.576
58 | 63 | 100 | 7.624
58 | 64 | 100 | 7.672
58 | 65 | 100 | 7.72
58 | 66 | 100 | 7.768
58 | 67 | 100 | 7.816
58 | 68 | 100 | 7.864
58 | 69 | 100 | 7.912
58 | 70 | 100 | 7.96
58 | 71 | 100 | 8.008
58 | 72 | 100 | 8.056
58 | 73 | 100 | 8.104
58 | 74 | 100 | 8.152
58 | 75 | 100 | 8.2
58 | 76 | 100 | 8.2632
58 | 77 | 100 | 8.3264
58 | 78 | 100 | 8.3896
58 | 79 | 100 | 8.4528
58 | 80 | 100 | 8.516
58 | 81 | 100 | 8.5792
58 | 82 | 100 | 8.6424
58 | 83 | 100 | 8.7056
58 | 84 | 100 | 8.7688
58 | 85 | 100 | 8.832
58 | 86 | 100 | 8.8952
58 | 87 | 100 | 8.9584
58 | 88 | 100 | 9.0216
58 | 89 | 100 | 9.0848
58 | 90 | 100 | 9.148
58 | 91 | 100 | 9.2112
58 | 92 | 100 | 9.2744
58 | 93 | 100 | 9.3376
58 | 94 | 100 | 9.4008
58 | 95 | 100 | 9.464
58 | 96 | 100 | 9.5272
58 | 97 | 100 | 9.5904
58 | 98 | 100 | 9.6536
58 | 99 | 100 | 9.7168
58 | 100 | 100 | 9.78
58 | 101 | 100 | 9.7867
58 | 102 | 100 | 9.7933
58 | 103 | 100 | 9.8
58 | 104 | 100 | 9.8067
58 | 105 | 100 | 9.8133
58 | 106 | 100 | 9.82
58 | 107 | 100 | 9.8267
58 | 108 | 100 | 9.8333
58 | 109 | 100 | 9.84
58 | 110 | 100 | 9.8467
58 | 111 | 100 | 9.8533
58 | 112 | 100 | 9.86
58 | 113 | 100 | 9.8667
58 | 114 | 100 | 9.8733
58 | 115 | 100 | 9.88
58 | 116 | 100 | 9.8867
58 | 117 | 100 | 9.8933
58 | 118 | 100 | 9.9
58 | 119 | 100 | 9.9067
58 | 120 | 100 | 9.9133
58 | 121 | 100 | 9.92
58 | 122 | 100 | 9.9267
58 | 123 | 100 | 9.9333
58 | 124 | 100 | 9.94
58 | 125 | 100 | 9.9467
58 | 126 | 100 | 9.9757
58 | 127 | 100 | 10.0048
58 | 128 | 100 | 10.0339
58 | 129 | 100 | 10.0629
58 | 130 | 100 | 10.092
58 | 131 | 100 | 10.1211
58 | 132 | 100 | 10.1501
58 | 133 | 100 | 10.1792
58 | 134 | 100 | 10.2083
58 | 135 | 100 | 10.2373
58 | 136 | 100 | 10.2664
58 | 137 | 100 | 10.2955
58 | 138 | 100 | 10.3245
58 | 139 | 100 | 10.3536
58 | 140 | 100 | 10.3827
58 | 141 | 100 | 10.4117
58 | 142 | 100 | 10.4408
58 | 143 | 100 | 10.4699
58 | 144 | 100 | 10.4989
58 | 145 | 100 | 10.528
58 | 146 | 100 | 10.5571
58 | 147 | 100 | 10.5861
58 | 148 | 100 | 10.6152
58 | 149 | 100 | 10.6443
58 | 150 | 100 | 10.6733
59 | 45 | 100 | 6.78
59 | 46 | 100 | 6.8273
59 | 47 | 100 | 6.8747
59 | 48 | 100 | 6.922
59 | 49 | 100 | 6.9693
59 | 50 | 100 | 7.0167
59 | 51 | 100 | 7.064
59 | 52 | 100 | 7.1113
59 | 53 | 100 | 7.1587
59 | 54 | 100 | 7.206
59 | 55 | 100 | 7.2533
59 | 56 | 100 | 7.3007
59 | 57 | 100 | 7.348
59 | 58 | 100 | 7.3953
59 | 59 | 100 | 7.4427
59 | 60 | 100 | 7.49
59 | 61 | 100 | 7.5373
59 | 62 | 100 | 7.5847
59 | 63 | 100 | 7.632
59 | 64 | 100 | 7.6793
59 | 65 | 100 | 7.7267
59 | 66 | 100 | 7.774
59 | 67 | 100 | 7.8213
59 | 68 | 100 | 7.8687
59 | 69 | 100 | 7.916
59 | 70 | 100 | 7.9633
59 | 71 | 100 | 8.0107
59 | 72 | 100 | 8.058
59 | 73 | 100 | 8.1053
59 | 74 | 100 | 8.1527
59 | 75 | 100 | 8.2
59 | 76 | 100 | 8.2656
59 | 77 | 100 | 8.3312
59 | 78 | 100 | 8.3968
59 | 79 | 100 | 8.4624
59 | 80 | 100 | 8.528
59 | 81 | 100 | 8.5936
59 | 82 | 100 | 8.6592
59 | 83 | 100 | 8.7248
59 | 84 | 100 | 8.7904
59 | 85 | 100 | 8.856
59 | 86 | 100 | 8.9216
59 | 87 | 100 | 8.9872
59 | 88 | 100 | 9.0528
59 | 89 | 100 | 9.1184
59 | 90 | 100 | 9.184
59 | 91 | 100 | 9.2496
59 | 92 | 100 | 9.3152
59 | 93 | 100 | 9.3808
59 | 94 | 100 | 9.4464
59 | 95 | 100 | 9.512
59 | 96 | 100 | 9.5776
59 | 97 | 100 | 9.6432
59 | 98 | 100 | 9.7088
59 | 99 | 100 | 9.7744
59 | 100 | 100 | 9.84
59 | 101 | 100 | 9.8453
59 | 102 | 100 | 9.8507
59 | 103 | 100 | 9.856
59 | 104 | 100 | 9.8613
59 | 105 | 100 | 9.8667
59 | 106 | 100 | 9.872
59 | 107 | 100 | 9.8773
59 | 108 | 100 | 9.8827
59 | 109 | 100 | 9.888
59 | 110 | 100 | 9.8933
59 | 111 | 100 | 9.8987
59 | 112 | 100 | 9.904
59 | 113 | 100 | 9.9093
59 | 114 | 100 | 9.9147
59 | 115 | 100 | 9.92
59 | 116 | 100 | 9.9253
59 | 117 | 100 | 9.9307
59 | 118 | 100 | 9.936
59 | 119 | 100 | 9.9413
59 | 120 | 100 | 9.9467
59 | 121 | 100 | 9.952
59 | 122 | 100 | 9.9573
59 | 123 | 100 | 9.9627
59 | 124 | 100 | 9.968
59 | 125 | 100 | 9.9733
59 | 126 | 100 | 10.0019
59 | 127 | 100 | 10.0304
59 | 128 | 100 | 10.0589
59 | 129 | 100 | 10.0875
59 | 130 | 100 | 10.116
59 | 131 | 100 | 10.1445
59 | 132 | 100 | 10.1731
59 | 133 | 100 | 10.2016
59 | 134 | 100 | 10.2301
59 | 135 | 100 | 10.2587
59 | 136 | 100 | 10.2872
59 | 137 | 100 | 10.3157
59 | 138 | 100 | 10.3443
59 | 139 | 100 | 10.3728
59 | 140 | 100 | 10.4013
59 | 141 | 100 | 10.4299
59 | 142 | 100 | 10.4584
59 | 143 | 100 | 10.4869
59 | 144 | 100 | 10.5155
59 | 145 | 100 | 10.544
59 | 146 | 100 | 10.5725
59 | 147 | 100 | 10.6011
59 | 148 | 100 | 10.6296
59 | 149 | 100 | 10.6581
59 | 150 | 100 | 10.6867
60 | 45 | 100 | 6.8
60 | 46 | 100 | 6.8467
60 | 47 | 100 | 6.8933
60 | 48 | 100 | 6.94
60 | 49 | 100 | 6.9867
60 | 50 | 100 | 7.0333
60 | 51 | 100 | 7.08
60 | 52 | 100 | 7.1267
60 | 53 | 100 | 7.1733
60 | 54 | 100 | 7.22
60 | 55 | 100 | 7.2667
60 | 56 | 100 | 7.3133
60 | 57 | 100 | 7.36
60 | 58 | 100 | 7.4067
60 | 59 | 100 | 7.4533
60 | 60 | 100 | 7.5
60 | 61 | 100 | 7.5467
60 | 62 | 100 | 7.5933
60 | 63 | 100 | 7.64
60 | 64 | 100 | 7.6867
60 | 65 | 100 | 7.7333
60 | 66 | 100 | 7.78
60 | 67 | 100 | 7.8267
60 | 68 | 100 | 7.8733
60 | 69 | 100 | 7.92
60 | 70 | 100 | 7.9667
60 | 71 | 100 | 8.0133
60 | 72 | 100 | 8.06
60 | 73 | 100 | 8.1067
60 | 74 | 100 | 8.1533
60 | 75 | 100 | 8.2
60 | 76 | 100 | 8.268
60 | 77 | 100 | 8.336
60 | 78 | 100 | 8.404
60 | 79 | 100 | 8.472
60 | 80 | 100 | 8.54
60 | 81 | 100 | 8.608
60 | 82 | 100 | 8.676
60 | 83 | 100 | 8.744
60 | 84 | 100 | 8.812
60 | 85 | 100 | 8.88
60 | 86 | 100 | 8.948
60 | 87 | 100 | 9.016
60 | 88 | 100 | 9.084
60 | 89 | 100 | 9.152
60 | 90 | 100 | 9.22
60 | 91 | 100 | 9.288
60 | 92 | 100 | 9.356
60 | 93 | 100 | 9.424
60 | 94 | 100 | 9.492
60 | 95 | 100 | 9.56
60 | 96 | 100 | 9.628
60 | 97 | 100 | 9.696
60 | 98 | 100 | 9.764
60 | 99 | 100 | 9.832
60 | 100 | 100 | 9.9
60 | 101 | 100 | 9.904
60 | 102 | 100 | 9.908
60 | 103 | 100 | 9.912
60 | 104 | 100 | 9.916
60 | 105 | 100 | 9.92
60 | 106 | 100 | 9.924
60 | 107 | 100 | 9.928
60 | 108 | 100 | 9.932
60 | 109 | 100 | 9.936
60 | 110 | 100 | 9.94
60 | 111 | 100 | 9.944
60 | 112 | 100 | 9.948
60 | 113 | 100 | 9.952
60 | 114 | 100 | 9.956
60 | 115 | 100 | 9.96
60 | 116 | 100 | 9.964
60 | 117 | 100 | 9.968
60 | 118 | 100 | 9.972
60 | 119 | 100 | 9.976
60 | 120 | 100 | 9.98
60 | 121 | 100 | 9.984
60 | 122 | 100 | 9.988
60 | 123 | 100 | 9.992
60 | 124 | 100 | 9.996
60 | 125 | 100 | 10
60 | 126 | 100 | 10.028
60 | 127 | 100 | 10.056
60 | 128 | 100 | 10.084
60 | 129 | 100 | 10.112
60 | 130 | 100 | 10.14
60 | 131 | 100 | 10.168
60 | 132 | 100 | 10.196
60 | 133 | 100 | 10.224
60 | 134 | 100 | 10.252
60 | 135 | 100 | 10.28
60 | 136 | 100 | 10.308
60 | 137 | 100 | 10.336
60 | 138 | 100 | 10.364
60 | 139 | 100 | 10.392
60 | 140 | 100 | 10.42
60 | 141 | 100 | 10.448
60 | 142 | 100 | 10.476
60 | 143 | 100 | 10.504
60 | 144 | 100 | 10.532
60 | 145 | 100 | 10.56
60 | 146 | 100 | 10.588
60 | 147 | 100 | 10.616
60 | 148 | 100 | 10.644
60 | 149 | 100 | 10.672
60 | 150 | 100 | 10.7
61 | 45 | 100 | 6.8067
61 | 46 | 100 | 6.8533
61 | 47 | 100 | 6.9
61 | 48 | 100 | 6.9467
61 | 49 | 100 | 6.9933
61 | 50 | 100 | 7.04
61 | 51 | 100 | 7.0867
61 | 52 | 100 | 7.1333
61 | 53 | 100 | 7.18
61 | 54 | 100 | 7.2267
61 | 55 | 100 | 7.2733
61 | 56 | 100 | 7.32
61 | 57 | 100 | 7.3667
61 | 58 | 100 | 7.4133
61 | 59 | 100 | 7.46
61 | 60 | 100 | 7.5067
61 | 61 | 100 | 7.5533
61 | 62 | 100 | 7.6
61 | 63 | 100 | 7.6467
61 | 64 | 100 | 7.6933
61 | 65 | 100 | 7.74
61 | 66 | 100 | 7.7867
61 | 67 | 100 | 7.8333
61 | 68 | 100 | 7.88
61 | 69 | 100 | 7.9267
61 | 70 | 100 | 7.9733
61 | 71 | 100 | 8.02
61 | 72 | 100 | 8.0667
61 | 73 | 100 | 8.1133
61 | 74 | 100 | 8.16
61 | 75 | 100 | 8.2067
61 | 76 | 100 | 8.2749
61 | 77 | 100 | 8.3432
61 | 78 | 100 | 8.4115
61 | 79 | 100 | 8.4797
61 | 80 | 100 | 8.548
61 | 81 | 100 | 8.6163
61 | 82 | 100 | 8.6845
61 | 83 | 100 | 8.7528
61 | 84 | 100 | 8.8211
61 | 85 | 100 | 8.8893
61 | 86 | 100 | 8.9576
61 | 87 | 100 | 9.0259
61 | 88 | 100 | 9.0941
61 | 89 | 100 | 9.1624
61 | 90 | 100 | 9.2307
61 | 91 | 100 | 9.2989
61 | 92 | 100 | 9.3672
61 | 93 | 100 | 9.4355
61 | 94 | 100 | 9.5037
61 | 95 | 100 | 9.572
61 | 96 | 100 | 9.6403
61 | 97 | 100 | 9.7085
61 | 98 | 100 | 9.7768
61 | 99 | 100 | 9.8451
61 | 100 | 100 | 9.9133
61 | 101 | 100 | 9.9176
61 | 102 | 100 | 9.9219
61 | 103 | 100 | 9.9261
61 | 104 | 100 | 9.9304
61 | 105 | 100 | 9.9347
61 | 106 | 100 | 9.9389
61 | 107 | 100 | 9.9432
61 | 108 | 100 | 9.9475
61 | 109 | 100 | 9.9517
61 | 110 | 100 | 9.956
61 | 111 | 100 | 9.9603
61 | 112 | 100 | 9.9645
61 | 113 | 100 | 9.9688
61 | 114 | 100 | 9.9731
61 | 115 | 100 | 9.9773
61 | 116 | 100 | 9.9816
61 | 117 | 100 | 9.9859
61 | 118 | 100 | 9.9901
61 | 119 | 100 | 9.9944
61 | 120 | 100 | 9.9987
61 | 121 | 100 | 10.0029
61 | 122 | 100 | 10.0072
61 | 123 | 100 | 10.0115
61 | 124 | 100 | 10.0157
61 | 125 | 100 | 10.02
61 | 126 | 100 | 10.0477
61 | 127 | 100 | 10.0755
61 | 128 | 100 | 10.1032
61 | 129 | 100 | 10.1309
61 | 130 | 100 | 10.1587
61 | 131 | 100 | 10.1864
61 | 132 | 100 | 10.2141
61 | 133 | 100 | 10.2419
61 | 134 | 100 | 10.2696
61 | 135 | 100 | 10.2973
61 | 136 | 100 | 10.3251
61 | 137 | 100 | 10.3528
61 | 138 | 100 | 10.3805
61 | 139 | 100 | 10.4083
61 | 140 | 100 | 10.436
61 | 141 | 100 | 10.4637
61 | 142 | 100 | 10.4915
61 | 143 | 100 | 10.5192
61 | 144 | 100 | 10.5469
61 | 145 | 100 | 10.5747
61 | 146 | 100 | 10.6024
61 | 147 | 100 | 10.6301
61 | 148 | 100 | 10.6579
61 | 149 | 100 | 10.6856
61 | 150 | 100 | 10.7133
62 | 45 | 100 | 6.8133
62 | 46 | 100 | 6.86
62 | 47 | 100 | 6.9067
62 | 48 | 100 | 6.9533
62 | 49 | 100 | 7
62 | 50 | 100 | 7.0467
62 | 51 | 100 | 7.0933
62 | 52 | 100 | 7.14
62 | 53 | 100 | 7.1867
62 | 54 | 100 | 7.2333
62 | 55 | 100 | 7.28
62 | 56 | 100 | 7.3267
62 | 57 | 100 | 7.3733
62 | 58 | 100 | 7.42
62 | 59 | 100 | 7.4667
62 | 60 | 100 | 7.5133
62 | 61 | 100 | 7.56
62 | 62 | 100 | 7.6067
62 | 63 | 100 | 7.6533
62 | 64 | 100 | 7.7
62 | 65 | 100 | 7.7467
62 | 66 | 100 | 7.7933
62 | 67 | 100 | 7.84
62 | 68 | 100 | 7.8867
62 | 69 | 100 | 7.9333
62 | 70 | 100 | 7.98
62 | 71 | 100 | 8.0267
62 | 72 | 100 | 8.0733
62 | 73 | 100 | 8.12
62 | 74 | 100 | 8.1667
62 | 75 | 100 | 8.2133
62 | 76 | 100 | 8.2819
62 | 77 | 100 | 8.3504
62 | 78 | 100 | 8.4189
62 | 79 | 100 | 8.4875
62 | 80 | 100 | 8.556
62 | 81 | 100 | 8.6245
62 | 82 | 100 | 8.6931
62 | 83 | 100 | 8.7616
62 | 84 | 100 | 8.8301
62 | 85 | 100 | 8.8987
62 | 86 | 100 | 8.9672
62 | 87 | 100 | 9.0357
62 | 88 | 100 | 9.1043
62 | 89 | 100 | 9.1728
62 | 90 | 100 | 9.2413
62 | 91 | 100 | 9.3099
62 | 92 | 100 | 9.3784
62 | 93 | 100 | 9.4469
62 | 94 | 100 | 9.5155
62 | 95 | 100 | 9.584
62 | 96 | 100 | 9.6525
62 | 97 | 100 | 9.7211
62 | 98 | 100 | 9.7896
62 | 99 | 100 | 9.8581
62 | 100 | 100 | 9.9267
62 | 101 | 100 | 9.9312
62 | 102 | 100 | 9.9357
62 | 103 | 100 | 9.9403
62 | 104 | 100 | 9.9448
62 | 105 | 100 | 9.9493
62 | 106 | 100 | 9.9539
62 | 107 | 100 | 9.9584
62 | 108 | 100 | 9.9629
62 | 109 | 100 | 9.9675
62 | 110 | 100 | 9.972
62 | 111 | 100 | 9.9765
62 | 112 | 100 | 9.9811
62 | 113 | 100 | 9.9856
62 | 114 | 100 | 9.9901
62 | 115 | 100 | 9.9947
62 | 116 | 100 | 9.9992
62 | 117 | 100 | 10.0037
62 | 118 | 100 | 10.0083
62 | 119 | 100 | 10.0128
62 | 120 | 100 | 10.0173
62 | 121 | 100 | 10.0219
62 | 122 | 100 | 10.0264
62 | 123 | 100 | 10.0309
62 | 124 | 100 | 10.0355
62 | 125 | 100 | 10.04
62 | 126 | 100 | 10.0675
62 | 127 | 100 | 10.0949
62 | 128 | 100 | 10.1224
62 | 129 | 100 | 10.1499
62 | 130 | 100 | 10.1773
62 | 131 | 100 | 10.2048
62 | 132 | 100 | 10.2323
62 | 133 | 100 | 10.2597
62 | 134 | 100 | 10.2872
62 | 135 | 100 | 10.3147
62 | 136 | 100 | 10.3421
62 | 137 | 100 | 10.3696
62 | 138 | 100 | 10.3971
62 | 139 | 100 | 10.4245
62 | 140 | 100 | 10.452
62 | 141 | 100 | 10.4795
62 | 142 | 100 | 10.5069
62 | 143 | 100 | 10.5344
62 | 144 | 100 | 10.5619
62 | 145 | 100 | 10.5893
62 | 146 | 100 | 10.6168
62 | 147 | 100 | 10.6443
62 | 148 | 100 | 10.6717
62 | 149 | 100 | 10.6992
62 | 150 | 100 | 10.7267
63 | 45 | 100 | 6.82
63 | 46 | 100 | 6.8667
63 | 47 | 100 | 6.9133
63 | 48 | 100 | 6.96
63 | 49 | 100 | 7.0067
63 | 50 | 100 | 7.0533
63 | 51 | 100 | 7.1
63 | 52 | 100 | 7.1467
63 | 53 | 100 | 7.1933
63 | 54 | 100 | 7.24
63 | 55 | 100 | 7.2867
63 | 56 | 100 | 7.3333
63 | 57 | 100 | 7.38
63 | 58 | 100 | 7.4267
63 | 59 | 100 | 7.4733
63 | 60 | 100 | 7.52
63 | 61 | 100 | 7.5667
63 | 62 | 100 | 7.6133
63 | 63 | 100 | 7.66
63 | 64 | 100 | 7.7067
63 | 65 | 100 | 7.7533
63 | 66 | 100 | 7.8
63 | 67 | 100 | 7.8467
63 | 68 | 100 | 7.8933
63 | 69 | 100 | 7.94
63 | 70 | 100 | 7.9867
63 | 71 | 100 | 8.0333
63 | 72 | 100 | 8.08
63 | 73 | 100 | 8.1267
63 | 74 | 100 | 8.1733
63 | 75 | 100 | 8.22
63 | 76 | 100 | 8.2888
63 | 77 | 100 | 8.3576
63 | 78 | 100 | 8.4264
63 | 79 | 100 | 8.4952
63 | 80 | 100 | 8.564
63 | 81 | 100 | 8.6328
63 | 82 | 100 | 8.7016
63 | 83 | 100 | 8.7704
63 | 84 | 100 | 8.8392
63 | 85 | 100 | 8.908
63 | 86 | 100 | 8.9768
63 | 87 | 100 | 9.0456
63 | 88 | 100 | 9.1144
63 | 89 | 100 | 9.1832
63 | 90 | 100 | 9.252
63 | 91 | 100 | 9.3208
63 | 92 | 100 | 9.3896
63 | 93 | 100 | 9.4584
63 | 94 | 100 | 9.5272
63 | 95 | 100 | 9.596
63 | 96 | 100 | 9.6648
63 | 97 | 100 | 9.7336
63 | 98 | 100 | 9.8024
63 | 99 | 100 | 9.8712
63 | 100 | 100 | 9.94
63 | 101 | 100 | 9.9448
63 | 102 | 100 | 9.9496
63 | 103 | 100 | 9.9544
63 | 104 | 100 | 9.9592
63 | 105 | 100 | 9.964
63 | 106 | 100 | 9.9688
63 | 107 | 100 | 9.9736
63 | 108 | 100 | 9.9784
63 | 109 | 100 | 9.9832
63 | 110 | 100 | 9.988
63 | 111 | 100 | 9.9928
63 | 112 | 100 | 9.9976
63 | 113 | 100 | 10.0024
63 | 114 | 100 | 10.0072
63 | 115 | 100 | 10.012
63 | 116 | 100 | 10.0168
63 | 117 | 100 | 10.0216
63 | 118 | 100 | 10.0264
63 | 119 | 100 | 10.0312
63 | 120 | 100 | 10.036
63 | 121 | 100 | 10.0408
63 | 122 | 100 | 10.0456
63 | 123 | 100 | 10.0504
63 | 124 | 100 | 10.0552
63 | 125 | 100 | 10.06
63 | 126 | 100 | 10.0872
63 | 127 | 100 | 10.1144
63 | 128 | 100 | 10.1416
63 | 129 | 100 | 10.1688
63 | 130 | 100 | 10.196
63 | 131 | 100 | 10.2232
63 | 132 | 100 | 10.2504
63 | 133 | 100 | 10.2776
63 | 134 | 100 | 10.3048
63 | 135 | 100 | 10.332
63 | 136 | 100 | 10.3592
63 | 137 | 100 | 10.3864
63 | 138 | 100 | 10.4136
63 | 139 | 100 | 10.4408
63 | 140 | 100 | 10.468
63 | 141 | 100 | 10.4952
63 | 142 | 100 | 10.5224
63 | 143 | 100 | 10.5496
63 | 144 | 100 | 10.5768
63 | 145 | 100 | 10.604
63 | 146 | 100 | 10.6312
63 | 147 | 100 | 10.6584
63 | 148 | 100 | 10.6856
63 | 149 | 100 | 10.7128
63 | 150 | 100 | 10.74
64 | 45 | 100 | 6.8267
64 | 46 | 100 | 6.8733
64 | 47 | 100 | 6.92
64 | 48 | 100 | 6.9667
64 | 49 | 100 | 7.0133
64 | 50 | 100 | 7.06
64 | 51 | 100 | 7.1067
64 | 52 | 100 | 7.1533
64 | 53 | 100 | 7.2
64 | 54 | 100 | 7.2467
64 | 55 | 100 | 7.2933
64 | 56 | 100 | 7.34
64 | 57 | 100 | 7.3867
64 | 58 | 100 | 7.4333
64 | 59 | 100 | 7.48
64 | 60 | 100 | 7.5267
64 | 61 | 100 | 7.5733
64 | 62 | 100 | 7.62
64 | 63 | 100 | 7.6667
64 | 64 | 100 | 7.7133
64 | 65 | 100 | 7.76
64 | 66 | 100 | 7.8067
64 | 67 | 100 | 7.8533
64 | 68 | 100 | 7.9
64 | 69 | 100 | 7.9467
64 | 70 | 100 | 7.9933
64 | 71 | 100 | 8.04
64 | 72 | 100 | 8.0867
64 | 73 | 100 | 8.1333
64 | 74 | 100 | 8.18
64 | 75 | 100 | 8.2267
64 | 76 | 100 | 8.2957
64 | 77 | 100 | 8.3648
64 | 78 | 100 | 8.4339
64 | 79 | 100 | 8.5029
64 | 80 | 100 | 8.572
64 | 81 | 100 | 8.6411
64 | 82 | 100 | 8.7101
64 | 83 | 100 | 8.7792
64 | 84 | 100 | 8.8483
64 | 85 | 100 | 8.9173
64 | 86 | 100 | 8.9864
64 | 87 | 100 | 9.0555
64 | 88 | 100 | 9.1245
64 | 89 | 100 | 9.1936
64 | 90 | 100 | 9.2627
64 | 91 | 100 | 9.3317
64 | 92 | 100 | 9.4008
64 | 93 | 100 | 9.4699
64 | 94 | 100 | 9.5389
64 | 95 | 100 | 9.608
64 | 96 | 100 | 9.6771
64 | 97 | 100 | 9.7461
64 | 98 | 100 | 9.8152
64 | 99 | 100 | 9.8843
64 | 100 | 100 | 9.9533
64 | 101 | 100 | 9.9584
64 | 102 | 100 | 9.9635
64 | 103 | 100 | 9.9685
64 | 104 | 100 | 9.9736
64 | 105 | 100 | 9.9787
64 | 106 | 100 | 9.9837
64 | 107 | 100 | 9.9888
64 | 108 | 100 | 9.9939
64 | 109 | 100 | 9.9989
64 | 110 | 100 | 10.004
64 | 111 | 100 | 10.0091
64 | 112 | 100 | 10.0141
64 | 113 | 100 | 10.0192
64 | 114 | 100 | 10.0243
64 | 115 | 100 | 10.0293
64 | 116 | 100 | 10.0344
64 | 117 | 100 | 10.0395
64 | 118 | 100 | 10.0445
64 | 119 | 100 | 10.0496
64 | 120 | 100 | 10.0547
64 | 121 | 100 | 10.0597
64 | 122 | 100 | 10.0648
64 | 123 | 100 | 10.0699
64 | 124 | 100 | 10.0749
64 | 125 | 100 | 10.08
64 | 126 | 100 | 10.1069
64 | 127 | 100 | 10.1339
64 | 128 | 100 | 10.1608
64 | 129 | 100 | 10.1877
64 | 130 | 100 | 10.2147
64 | 131 | 100 | 10.2416
64 | 132 | 100 | 10.2685
64 | 133 | 100 | 10.2955
64 | 134 | 100 | 10.3224
64 | 135 | 100 | 10.3493
64 | 136 | 100 | 10.3763
64 | 137 | 100 | 10.4032
64 | 138 | 100 | 10.4301
64 | 139 | 100 | 10.4571
64 | 140 | 100 | 10.484
64 | 141 | 100 | 10.5109
64 | 142 | 100 | 10.5379
64 | 143 | 100 | 10.5648
64 | 144 | 100 | 10.5917
64 | 145 | 100 | 10.6187
64 | 146 | 100 | 10.6456
64 | 147 | 100 | 10.6725
64 | 148 | 100 | 10.6995
64 | 149 | 100 | 10.7264
64 | 150 | 100 | 10.7533
65 | 45 | 100 | 6.8333
65 | 46 | 100 | 6.88
65 | 47 | 100 | 6.9267
65 | 48 | 100 | 6.9733
65 | 49 | 100 | 7.02
65 | 50 | 100 | 7.0667
65 | 51 | 100 | 7.1133
65 | 52 | 100 | 7.16
65 | 53 | 100 | 7.2067
65 | 54 | 100 | 7.2533
65 | 55 | 100 | 7.3
65 | 56 | 100 | 7.3467
65 | 57 | 100 | 7.3933
65 | 58 | 100 | 7.44
65 | 59 | 100 | 7.4867
65 | 60 | 100 | 7.5333
65 | 61 | 100 | 7.58
65 | 62 | 100 | 7.6267
65 | 63 | 100 | 7.6733
65 | 64 | 100 | 7.72
65 | 65 | 100 | 7.7667
65 | 66 | 100 | 7.8133
65 | 67 | 100 | 7.86
65 | 68 | 100 | 7.9067
65 | 69 | 100 | 7.9533
65 | 70 | 100 | 8
65 | 71 | 100 | 8.0467
65 | 72 | 100 | 8.0933
65 | 73 | 100 | 8.14
65 | 74 | 100 | 8.1867
65 | 75 | 100 | 8.2333
65 | 76 | 100 | 8.3027
65 | 77 | 100 | 8.372
65 | 78 | 100 | 8.4413
65 | 79 | 100 | 8.5107
65 | 80 | 100 | 8.58
65 | 81 | 100 | 8.6493
65 | 82 | 100 | 8.7187
65 | 83 | 100 | 8.788
65 | 84 | 100 | 8.8573
65 | 85 | 100 | 8.9267
65 | 86 | 100 | 8.996
65 | 87 | 100 | 9.0653
65 | 88 | 100 | 9.1347
65 | 89 | 100 | 9.204
65 | 90 | 100 | 9.2733
65 | 91 | 100 | 9.3427
65 | 92 | 100 | 9.412
65 | 93 | 100 | 9.4813
65 | 94 | 100 | 9.5507
65 | 95 | 100 | 9.62
65 | 96 | 100 | 9.6893
65 | 97 | 100 | 9.7587
65 | 98 | 100 | 9.828
65 | 99 | 100 | 9.8973
65 | 100 | 100 | 9.9667
65 | 101 | 100 | 9.972
65 | 102 | 100 | 9.9773
65 | 103 | 100 | 9.9827
65 | 104 | 100 | 9.988
65 | 105 | 100 | 9.9933
65 | 106 | 100 | 9.9987
65 | 107 | 100 | 10.004
65 | 108 | 100 | 10.0093
65 | 109 | 100 | 10.0147
65 | 110 | 100 | 10.02
65 | 111 | 100 | 10.0253
65 | 112 | 100 | 10.0307
65 | 113 | 100 | 10.036
65 | 114 | 100 | 10.0413
65 | 115 | 100 | 10.0467
65 | 116 | 100 | 10.052
65 | 117 | 100 | 10.0573
65 | 118 | 100 | 10.0627
65 | 119 | 100 | 10.068
65 | 120 | 100 | 10.0733
65 | 121 | 100 | 10.0787
65 | 122 | 100 | 10.084
65 | 123 | 100 | 10.0893
65 | 124 | 100 | 10.0947
65 | 125 | 100 | 10.1
65 | 126 | 100 | 10.1267
65 | 127 | 100 | 10.1533
65 | 128 | 100 | 10.18
65 | 129 | 100 | 10.2067
65 | 130 | 100 | 10.2333
65 | 131 | 100 | 10.26
65 | 132 | 100 | 10.2867
65 | 133 | 100 | 10.3133
65 | 134 | 100 | 10.34
65 | 135 | 100 | 10.3667
65 | 136 | 100 | 10.3933
65 | 137 | 100 | 10.42
65 | 138 | 100 | 10.4467
65 | 139 | 100 | 10.4733
65 | 140 | 100 | 10.5
65 | 141 | 100 | 10.5267
65 | 142 | 100 | 10.5533
65 | 143 | 100 | 10.58
65 | 144 | 100 | 10.6067
65 | 145 | 100 | 10.6333
65 | 146 | 100 | 10.66
65 | 147 | 100 | 10.6867
65 | 148 | 100 | 10.7133
65 | 149 | 100 | 10.74
65 | 150 | 100 | 10.7667
66 | 45 | 100 | 6.84
66 | 46 | 100 | 6.8867
66 | 47 | 100 | 6.9333
66 | 48 | 100 | 6.98
66 | 49 | 100 | 7.0267
66 | 50 | 100 | 7.0733
66 | 51 | 100 | 7.12
66 | 52 | 100 | 7.1667
66 | 53 | 100 | 7.2133
66 | 54 | 100 | 7.26
66 | 55 | 100 | 7.3067
66 | 56 | 100 | 7.3533
66 | 57 | 100 | 7.4
66 | 58 | 100 | 7.4467
66 | 59 | 100 | 7.4933
66 | 60 | 100 | 7.54
66 | 61 | 100 | 7.5867
66 | 62 | 100 | 7.6333
66 | 63 | 100 | 7.68
66 | 64 | 100 | 7.7267
66 | 65 | 100 | 7.7733
66 | 66 | 100 | 7.82
66 | 67 | 100 | 7.8667
66 | 68 | 100 | 7.9133
66 | 69 | 100 | 7.96
66 | 70 | 100 | 8.0067
66 | 71 | 100 | 8.0533
66 | 72 | 100 | 8.1
66 | 73 | 100 | 8.1467
66 | 74 | 100 | 8.1933
66 | 75 | 100 | 8.24
66 | 76 | 100 | 8.3096
66 | 77 | 100 | 8.3792
66 | 78 | 100 | 8.4488
66 | 79 | 100 | 8.5184
66 | 80 | 100 | 8.588
66 | 81 | 100 | 8.6576
66 | 82 | 100 | 8.7272
66 | 83 | 100 | 8.7968
66 | 84 | 100 | 8.8664
66 | 85 | 100 | 8.936
66 | 86 | 100 | 9.0056
66 | 87 | 100 | 9.0752
66 | 88 | 100 | 9.1448
66 | 89 | 100 | 9.2144
66 | 90 | 100 | 9.284
66 | 91 | 100 | 9.3536
66 | 92 | 100 | 9.4232
66 | 93 | 100 | 9.4928
66 | 94 | 100 | 9.5624
66 | 95 | 100 | 9.632
66 | 96 | 100 | 9.7016
66 | 97 | 100 | 9.7712
66 | 98 | 100 | 9.8408
66 | 99 | 100 | 9.9104
66 | 100 | 100 | 9.98
66 | 101 | 100 | 9.9856
66 | 102 | 100 | 9.9912
66 | 103 | 100 | 9.9968
66 | 104 | 100 | 10.0024
66 | 105 | 100 | 10.008
66 | 106 | 100 | 10.0136
66 | 107 | 100 | 10.0192
66 | 108 | 100 | 10.0248
66 | 109 | 100 | 10.0304
66 | 110 | 100 | 10.036
66 | 111 | 100 | 10.0416
66 | 112 | 100 | 10.0472
66 | 113 | 100 | 10.0528
66 | 114 | 100 | 10.0584
66 | 115 | 100 | 10.064
66 | 116 | 100 | 10.0696
66 | 117 | 100 | 10.0752
66 | 118 | 100 | 10.0808
66 | 119 | 100 | 10.0864
66 | 120 | 100 | 10.092
66 | 121 | 100 | 10.0976
66 | 122 | 100 | 10.1032
66 | 123 | 100 | 10.1088
66 | 124 | 100 | 10.1144
66 | 125 | 100 | 10.12
66 | 126 | 100 | 10.1464
66 | 127 | 100 | 10.1728
66 | 128 | 100 | 10.1992
66 | 129 | 100 | 10.2256
66 | 130 | 100 | 10.252
66 | 131 | 100 | 10.2784
66 | 132 | 100 | 10.3048
66 | 133 | 100 | 10.3312
66 | 134 | 100 | 10.3576
66 | 135 | 100 | 10.384
66 | 136 | 100 | 10.4104
66 | 137 | 100 | 10.4368
66 | 138 | 100 | 10.4632
66 | 139 | 100 | 10.4896
66 | 140 | 100 | 10.516
66 | 141 | 100 | 10.5424
66 | 142 | 100 | 10.5688
66 | 143 | 100 | 10.5952
66 | 144 | 100 | 10.6216
66 | 145 | 100 | 10.648
66 | 146 | 100 | 10.6744
66 | 147 | 100 | 10.7008
66 | 148 | 100 | 10.7272
66 | 149 | 100 | 10.7536
66 | 150 | 100 | 10.78
67 | 45 | 100 | 6.8467
67 | 46 | 100 | 6.8933
67 | 47 | 100 | 6.94
67 | 48 | 100 | 6.9867
67 | 49 | 100 | 7.0333
67 | 50 | 100 | 7.08
67 | 51 | 100 | 7.1267
67 | 52 | 100 | 7.1733
67 | 53 | 100 | 7.22
67 | 54 | 100 | 7.2667
67 | 55 | 100 | 7.3133
67 | 56 | 100 | 7.36
67 | 57 | 100 | 7.4067
67 | 58 | 100 | 7.4533
67 | 59 | 100 | 7.5
67 | 60 | 100 | 7.5467
67 | 61 | 100 | 7.5933
67 | 62 | 100 | 7.64
67 | 63 | 100 | 7.6867
67 | 64 | 100 | 7.7333
67 | 65 | 100 | 7.78
67 | 66 | 100 | 7.8267
67 | 67 | 100 | 7.8733
67 | 68 | 100 | 7.92
67 | 69 | 100 | 7.9667
67 | 70 | 100 | 8.0133
67 | 71 | 100 | 8.06
67 | 72 | 100 | 8.1067
67 | 73 | 100 | 8.1533
67 | 74 | 100 | 8.2
67 | 75 | 100 | 8.2467
67 | 76 | 100 | 8.3165
67 | 77 | 100 | 8.3864
67 | 78 | 100 | 8.4563
67 | 79 | 100 | 8.5261
67 | 80 | 100 | 8.596
67 | 81 | 100 | 8.6659
67 | 82 | 100 | 8.7357
67 | 83 | 100 | 8.8056
67 | 84 | 100 | 8.8755
67 | 85 | 100 | 8.9453
67 | 86 | 100 | 9.0152
67 | 87 | 100 | 9.0851
67 | 88 | 100 | 9.1549
67 | 89 | 100 | 9.2248
67 | 90 | 100 | 9.2947
67 | 91 | 100 | 9.3645
67 | 92 | 100 | 9.4344
67 | 93 | 100 | 9.5043
67 | 94 | 100 | 9.5741
67 | 95 | 100 | 9.644
67 | 96 | 100 | 9.7139
67 | 97 | 100 | 9.7837
67 | 98 | 100 | 9.8536
67 | 99 | 100 | 9.9235
67 | 100 | 100 | 9.9933
67 | 101 | 100 | 9.9992
67 | 102 | 100 | 10.0051
67 | 103 | 100 | 10.0109
67 | 104 | 100 | 10.0168
67 | 105 | 100 | 10.0227
67 | 106 | 100 | 10.0285
67 | 107 | 100 | 10.0344
67 | 108 | 100 | 10.0403
67 | 109 | 100 | 10.0461
67 | 110 | 100 | 10.052
67 | 111 | 100 | 10.0579
67 | 112 | 100 | 10.0637
67 | 113 | 100 | 10.0696
67 | 114 | 100 | 10.0755
67 | 115 | 100 | 10.0813
67 | 116 | 100 | 10.0872
67 | 117 | 100 | 10.0931
67 | 118 | 100 | 10.0989
67 | 119 | 100 | 10.1048
67 | 120 | 100 | 10.1107
67 | 121 | 100 | 10.1165
67 | 122 | 100 | 10.1224
67 | 123 | 100 | 10.1283
67 | 124 | 100 | 10.1341
67 | 125 | 100 | 10.14
67 | 126 | 100 | 10.1661
67 | 127 | 100 | 10.1923
67 | 128 | 100 | 10.2184
67 | 129 | 100 | 10.2445
67 | 130 | 100 | 10.2707
67 | 131 | 100 | 10.2968
67 | 132 | 100 | 10.3229
67 | 133 | 100 | 10.3491
67 | 134 | 100 | 10.3752
67 | 135 | 100 | 10.4013
67 | 136 | 100 | 10.4275
67 | 137 | 100 | 10.4536
67 | 138 | 100 | 10.4797
67 | 139 | 100 | 10.5059
67 | 140 | 100 | 10.532
67 | 141 | 100 | 10.5581
67 | 142 | 100 | 10.5843
67 | 143 | 100 | 10.6104
67 | 144 | 100 | 10.6365
67 | 145 | 100 | 10.6627
67 | 146 | 100 | 10.6888
67 | 147 | 100 | 10.7149
67 | 148 | 100 | 10.7411
67 | 149 | 100 | 10.7672
67 | 150 | 100 | 10.7933
68 | 45 | 100 | 6.8533
68 | 46 | 100 | 6.9
68 | 47 | 100 | 6.9467
68 | 48 | 100 | 6.9933
68 | 49 | 100 | 7.04
68 | 50 | 100 | 7.0867
68 | 51 | 100 | 7.1333
68 | 52 | 100 | 7.18
68 | 53 | 100 | 7.2267
68 | 54 | 100 | 7.2733
68 | 55 | 100 | 7.32
68 | 56 | 100 | 7.3667
68 | 57 | 100 | 7.4133
68 | 58 | 100 | 7.46
68 | 59 | 100 | 7.5067
68 | 60 | 100 | 7.5533
68 | 61 | 100 | 7.6
68 | 62 | 100 | 7.6467
68 | 63 | 100 | 7.6933
68 | 64 | 100 | 7.74
68 | 65 | 100 | 7.7867
68 | 66 | 100 | 7.8333
68 | 67 | 100 | 7.88
68 | 68 | 100 | 7.9267
68 | 69 | 100 | 7.9733
68 | 70 | 100 | 8.02
68 | 71 | 100 | 8.0667
68 | 72 | 100 | 8.1133
68 | 73 | 100 | 8.16
68 | 74 | 100 | 8.2067
68 | 75 | 100 | 8.2533
68 | 76 | 100 | 8.3235
68 | 77 | 100 | 8.3936
68 | 78 | 100 | 8.4637
68 | 79 | 100 | 8.5339
68 | 80 | 100 | 8.604
68 | 81 | 100 | 8.6741
68 | 82 | 100 | 8.7443
68 | 83 | 100 | 8.8144
68 | 84 | 100 | 8.8845
68 | 85 | 100 | 8.9547
68 | 86 | 100 | 9.0248
68 | 87 | 100 | 9.0949
68 | 88 | 100 | 9.1651
68 | 89 | 100 | 9.2352
68 | 90 | 100 | 9.3053
68 | 91 | 100 | 9.3755
68 | 92 | 100 | 9.4456
68 | 93 | 100 | 9.5157
68 | 94 | 100 | 9.5859
68 | 95 | 100 | 9.656
68 | 96 | 100 | 9.7261
68 | 97 | 100 | 9.7963
68 | 98 | 100 | 9.8664
68 | 99 | 100 | 9.9365
68 | 100 | 100 | 10.0067
68 | 101 | 100 | 10.0128
68 | 102 | 100 | 10.0189
68 | 103 | 100 | 10.0251
68 | 104 | 100 | 10.0312
68 | 105 | 100 | 10.0373
68 | 106 | 100 | 10.0435
68 | 107 | 100 | 10.0496
68 | 108 | 100 | 10.0557
68 | 109 | 100 | 10.0619
68 | 110 | 100 | 10.068
68 | 111 | 100 | 10.0741
68 | 112 | 100 | 10.0803
68 | 113 | 100 | 10.0864
68 | 114 | 100 | 10.0925
68 | 115 | 100 | 10.0987
68 | 116 | 100 | 10.1048
68 | 117 | 100 | 10.1109
68 | 118 | 100 | 10.1171
68 | 119 | 100 | 10.1232
68 | 120 | 100 | 10.1293
68 | 121 | 100 | 10.1355
68 | 122 | 100 | 10.1416
68 | 123 | 100 | 10.1477
68 | 124 | 100 | 10.1539
68 | 125 | 100 | 10.16
68 | 126 | 100 | 10.1859
68 | 127 | 100 | 10.2117
68 | 128 | 100 | 10.2376
68 | 129 | 100 | 10.2635
68 | 130 | 100 | 10.2893
68 | 131 | 100 | 10.3152
68 | 132 | 100 | 10.3411
68 | 133 | 100 | 10.3669
68 | 134 | 100 | 10.3928
68 | 135 | 100 | 10.4187
68 | 136 | 100 | 10.4445
68 | 137 | 100 | 10.4704
68 | 138 | 100 | 10.4963
68 | 139 | 100 | 10.5221
68 | 140 | 100 | 10.548
68 | 141 | 100 | 10.5739
68 | 142 | 100 | 10.5997
68 | 143 | 100 | 10.6256
68 | 144 | 100 | 10.6515
68 | 145 | 100 | 10.6773
68 | 146 | 100 | 10.7032
68 | 147 | 100 | 10.7291
68 | 148 | 100 | 10.7549
68 | 149 | 100 | 10.7808
68 | 150 | 100 | 10.8067
69 | 45 | 100 | 6.86
69 | 46 | 100 | 6.9067
69 | 47 | 100 | 6.9533
69 | 48 | 100 | 7
69 | 49 | 100 | 7.0467
69 | 50 | 100 | 7.0933
69 | 51 | 100 | 7.14
69 | 52 | 100 | 7.1867
69 | 53 | 100 | 7.2333
69 | 54 | 100 | 7.28
69 | 55 | 100 | 7.3267
69 | 56 | 100 | 7.3733
69 | 57 | 100 | 7.42
69 | 58 | 100 | 7.4667
69 | 59 | 100 | 7.5133
69 | 60 | 100 | 7.56
69 | 61 | 100 | 7.6067
69 | 62 | 100 | 7.6533
69 | 63 | 100 | 7.7
69 | 64 | 100 | 7.7467
69 | 65 | 100 | 7.7933
69 | 66 | 100 | 7.84
69 | 67 | 100 | 7.8867
69 | 68 | 100 | 7.9333
69 | 69 | 100 | 7.98
69 | 70 | 100 | 8.0267
69 | 71 | 100 | 8.0733
69 | 72 | 100 | 8.12
69 | 73 | 100 | 8.1667
69 | 74 | 100 | 8.2133
69 | 75 | 100 | 8.26
69 | 76 | 100 | 8.3304
69 | 77 | 100 | 8.4008
69 | 78 | 100 | 8.4712
69 | 79 | 100 | 8.5416
69 | 80 | 100 | 8.612
69 | 81 | 100 | 8.6824
69 | 82 | 100 | 8.7528
69 | 83 | 100 | 8.8232
69 | 84 | 100 | 8.8936
69 | 85 | 100 | 8.964
69 | 86 | 100 | 9.0344
69 | 87 | 100 | 9.1048
69 | 88 | 100 | 9.1752
69 | 89 | 100 | 9.2456
69 | 90 | 100 | 9.316
69 | 91 | 100 | 9.3864
69 | 92 | 100 | 9.4568
69 | 93 | 100 | 9.5272
69 | 94 | 100 | 9.5976
69 | 95 | 100 | 9.668
69 | 96 | 100 | 9.7384
69 | 97 | 100 | 9.8088
69 | 98 | 100 | 9.8792
69 | 99 | 100 | 9.9496
69 | 100 | 100 | 10.02
69 | 101 | 100 | 10.0264
69 | 102 | 100 | 10.0328
69 | 103 | 100 | 10.0392
69 | 104 | 100 | 10.0456
69 | 105 | 100 | 10.052
69 | 106 | 100 | 10.0584
69 | 107 | 100 | 10.0648
69 | 108 | 100 | 10.0712
69 | 109 | 100 | 10.0776
69 | 110 | 100 | 10.084
69 | 111 | 100 | 10.0904
69 | 112 | 100 | 10.0968
69 | 113 | 100 | 10.1032
69 | 114 | 100 | 10.1096
69 | 115 | 100 | 10.116
69 | 116 | 100 | 10.1224
69 | 117 | 100 | 10.1288
69 | 118 | 100 | 10.1352
69 | 119 | 100 | 10.1416
69 | 120 | 100 | 10.148
69 | 121 | 100 | 10.1544
69 | 122 | 100 | 10.1608
69 | 123 | 100 | 10.1672
69 | 124 | 100 | 10.1736
69 | 125 | 100 | 10.18
69 | 126 | 100 | 10.2056
69 | 127 | 100 | 10.2312
69 | 128 | 100 | 10.2568
69 | 129 | 100 | 10.2824
69 | 130 | 100 | 10.308
69 | 131 | 100 | 10.3336
69 | 132 | 100 | 10.3592
69 | 133 | 100 | 10.3848
69 | 134 | 100 | 10.4104
69 | 135 | 100 | 10.436
69 | 136 | 100 | 10.4616
69 | 137 | 100 | 10.4872
69 | 138 | 100 | 10.5128
69 | 139 | 100 | 10.5384
69 | 140 | 100 | 10.564
69 | 141 | 100 | 10.5896
69 | 142 | 100 | 10.6152
69 | 143 | 100 | 10.6408
69 | 144 | 100 | 10.6664
69 | 145 | 100 | 10.692
69 | 146 | 100 | 10.7176
69 | 147 | 100 | 10.7432
69 | 148 | 100 | 10.7688
69 | 149 | 100 | 10.7944
69 | 150 | 100 | 10.82
70 | 45 | 100 | 6.8667
70 | 46 | 100 | 6.9133
70 | 47 | 100 | 6.96
70 | 48 | 100 | 7.0067
70 | 49 | 100 | 7.0533
70 | 50 | 100 | 7.1
70 | 51 | 100 | 7.1467
70 | 52 | 100 | 7.1933
70 | 53 | 100 | 7.24
70 | 54 | 100 | 7.2867
70 | 55 | 100 | 7.3333
70 | 56 | 100 | 7.38
70 | 57 | 100 | 7.4267
70 | 58 | 100 | 7.4733
70 | 59 | 100 | 7.52
70 | 60 | 100 | 7.5667
70 | 61 | 100 | 7.6133
70 | 62 | 100 | 7.66
70 | 63 | 100 | 7.7067
70 | 64 | 100 | 7.7533
70 | 65 | 100 | 7.8
70 | 66 | 100 | 7.8467
70 | 67 | 100 | 7.8933
70 | 68 | 100 | 7.94
70 | 69 | 100 | 7.9867
70 | 70 | 100 | 8.0333
70 | 71 | 100 | 8.08
70 | 72 | 100 | 8.1267
70 | 73 | 100 | 8.1733
70 | 74 | 100 | 8.22
70 | 75 | 100 | 8.2667
70 | 76 | 100 | 8.3373
70 | 77 | 100 | 8.408
70 | 78 | 100 | 8.4787
70 | 79 | 100 | 8.5493
70 | 80 | 100 | 8.62
70 | 81 | 100 | 8.6907
70 | 82 | 100 | 8.7613
70 | 83 | 100 | 8.832
70 | 84 | 100 | 8.9027
70 | 85 | 100 | 8.9733
70 | 86 | 100 | 9.044
70 | 87 | 100 | 9.1147
70 | 88 | 100 | 9.1853
70 | 89 | 100 | 9.256
70 | 90 | 100 | 9.3267
70 | 91 | 100 | 9.3973
70 | 92 | 100 | 9.468
70 | 93 | 100 | 9.5387
70 | 94 | 100 | 9.6093
70 | 95 | 100 | 9.68
70 | 96 | 100 | 9.7507
70 | 97 | 100 | 9.8213
70 | 98 | 100 | 9.892
70 | 99 | 100 | 9.9627
70 | 100 | 100 | 10.0333
70 | 101 | 100 | 10.04
70 | 102 | 100 | 10.0467
70 | 103 | 100 | 10.0533
70 | 104 | 100 | 10.06
70 | 105 | 100 | 10.0667
70 | 106 | 100 | 10.0733
70 | 107 | 100 | 10.08
70 | 108 | 100 | 10.0867
70 | 109 | 100 | 10.0933
70 | 110 | 100 | 10.1
70 | 111 | 100 | 10.1067
70 | 112 | 100 | 10.1133
70 | 113 | 100 | 10.12
70 | 114 | 100 | 10.1267
70 | 115 | 100 | 10.1333
70 | 116 | 100 | 10.14
70 | 117 | 100 | 10.1467
70 | 118 | 100 | 10.1533
70 | 119 | 100 | 10.16
70 | 120 | 100 | 10.1667
70 | 121 | 100 | 10.1733
70 | 122 | 100 | 10.18
70 | 123 | 100 | 10.1867
70 | 124 | 100 | 10.1933
70 | 125 | 100 | 10.2
70 | 126 | 100 | 10.2253
70 | 127 | 100 | 10.2507
70 | 128 | 100 | 10.276
70 | 129 | 100 | 10.3013
70 | 130 | 100 | 10.3267
70 | 131 | 100 | 10.352
70 | 132 | 100 | 10.3773
70 | 133 | 100 | 10.4027
70 | 134 | 100 | 10.428
70 | 135 | 100 | 10.4533
70 | 136 | 100 | 10.4787
70 | 137 | 100 | 10.504
70 | 138 | 100 | 10.5293
70 | 139 | 100 | 10.5547
70 | 140 | 100 | 10.58
70 | 141 | 100 | 10.6053
70 | 142 | 100 | 10.6307
70 | 143 | 100 | 10.656
70 | 144 | 100 | 10.6813
70 | 145 | 100 | 10.7067
70 | 146 | 100 | 10.732
70 | 147 | 100 | 10.7573
70 | 148 | 100 | 10.7827
70 | 149 | 100 | 10.808
70 | 150 | 100 | 10.8333
71 | 45 | 100 | 6.8733
71 | 46 | 100 | 6.92
71 | 47 | 100 | 6.9667
71 | 48 | 100 | 7.0133
71 | 49 | 100 | 7.06
71 | 50 | 100 | 7.1067
71 | 51 | 100 | 7.1533
71 | 52 | 100 | 7.2
71 | 53 | 100 | 7.2467
71 | 54 | 100 | 7.2933
71 | 55 | 100 | 7.34
71 | 56 | 100 | 7.3867
71 | 57 | 100 | 7.4333
71 | 58 | 100 | 7.48
71 | 59 | 100 | 7.5267
71 | 60 | 100 | 7.5733
71 | 61 | 100 | 7.62
71 | 62 | 100 | 7.6667
71 | 63 | 100 | 7.7133
71 | 64 | 100 | 7.76
71 | 65 | 100 | 7.8067
71 | 66 | 100 | 7.8533
71 | 67 | 100 | 7.9
71 | 68 | 100 | 7.9467
71 | 69 | 100 | 7.9933
71 | 70 | 100 | 8.04
71 | 71 | 100 | 8.0867
71 | 72 | 100 | 8.1333
71 | 73 | 100 | 8.18
71 | 74 | 100 | 8.2267
71 | 75 | 100 | 8.2733
71 | 76 | 100 | 8.3443
71 | 77 | 100 | 8.4152
71 | 78 | 100 | 8.4861
71 | 79 | 100 | 8.5571
71 | 80 | 100 | 8.628
71 | 81 | 100 | 8.6989
71 | 82 | 100 | 8.7699
71 | 83 | 100 | 8.8408
71 | 84 | 100 | 8.9117
71 | 85 | 100 | 8.9827
71 | 86 | 100 | 9.0536
71 | 87 | 100 | 9.1245
71 | 88 | 100 | 9.1955
71 | 89 | 100 | 9.2664
71 | 90 | 100 | 9.3373
71 | 91 | 100 | 9.4083
71 | 92 | 100 | 9.4792
71 | 93 | 100 | 9.5501
71 | 94 | 100 | 9.6211
71 | 95 | 100 | 9.692
71 | 96 | 100 | 9.7629
71 | 97 | 100 | 9.8339
71 | 98 | 100 | 9.9048
71 | 99 | 100 | 9.9757
71 | 100 | 100 | 10.0467
71 | 101 | 100 | 10.0536
71 | 102 | 100 | 10.0605
71 | 103 | 100 | 10.0675
71 | 104 | 100 | 10.0744
71 | 105 | 100 | 10.0813
71 | 106 | 100 | 10.0883
71 | 107 | 100 | 10.0952
71 | 108 | 100 | 10.1021
71 | 109 | 100 | 10.1091
71 | 110 | 100 | 10.116
71 | 111 | 100 | 10.1229
71 | 112 | 100 | 10.1299
71 | 113 | 100 | 10.1368
71 | 114 | 100 | 10.1437
71 | 115 | 100 | 10.1507
71 | 116 | 100 | 10.1576
71 | 117 | 100 | 10.1645
71 | 118 | 100 | 10.1715
71 | 119 | 100 | 10.1784
71 | 120 | 100 | 10.1853
71 | 121 | 100 | 10.1923
71 | 122 | 100 | 10.1992
71 | 123 | 100 | 10.2061
71 | 124 | 100 | 10.2131
71 | 125 | 100 | 10.22
71 | 126 | 100 | 10.2451
71 | 127 | 100 | 10.2701
71 | 128 | 100 | 10.2952
71 | 129 | 100 | 10.3203
71 | 130 | 100 | 10.3453
71 | 131 | 100 | 10.3704
71 | 132 | 100 | 10.3955
71 | 133 | 100 | 10.4205
71 | 134 | 100 | 10.4456
71 | 135 | 100 | 10.4707
71 | 136 | 100 | 10.4957
71 | 137 | 100 | 10.5208
71 | 138 | 100 | 10.5459
71 | 139 | 100 | 10.5709
71 | 140 | 100 | 10.596
71 | 141 | 100 | 10.6211
71 | 142 | 100 | 10.6461
71 | 143 | 100 | 10.6712
71 | 144 | 100 | 10.6963
71 | 145 | 100 | 10.7213
71 | 146 | 100 | 10.7464
71 | 147 | 100 | 10.7715
71 | 148 | 100 | 10.7965
71 | 149 | 100 | 10.8216
71 | 150 | 100 | 10.8467
72 | 45 | 100 | 6.88
72 | 46 | 100 | 6.9267
72 | 47 | 100 | 6.9733
72 | 48 | 100 | 7.02
72 | 49 | 100 | 7.0667
72 | 50 | 100 | 7.1133
72 | 51 | 100 | 7.16
72 | 52 | 100 | 7.2067
72 | 53 | 100 | 7.2533
72 | 54 | 100 | 7.3
72 | 55 | 100 | 7.3467
72 | 56 | 100 | 7.3933
72 | 57 | 100 | 7.44
72 | 58 | 100 | 7.4867
72 | 59 | 100 | 7.5333
72 | 60 | 100 | 7.58
72 | 61 | 100 | 7.6267
72 | 62 | 100 | 7.6733
72 | 63 | 100 | 7.72
72 | 64 | 100 | 7.7667
72 | 65 | 100 | 7.8133
72 | 66 | 100 | 7.86
72 | 67 | 100 | 7.9067
72 | 68 | 100 | 7.9533
72 | 69 | 100 | 8
72 | 70 | 100 | 8.0467
72 | 71 | 100 | 8.0933
72 | 72 | 100 | 8.14
72 | 73 | 100 | 8.1867
72 | 74 | 100 | 8.2333
72 | 75 | 100 | 8.28
72 | 76 | 100 | 8.3512
72 | 77 | 100 | 8.4224
72 | 78 | 100 | 8.4936
72 | 79 | 100 | 8.5648
72 | 80 | 100 | 8.636
72 | 81 | 100 | 8.7072
72 | 82 | 100 | 8.7784
72 | 83 | 100 | 8.8496
72 | 84 | 100 | 8.9208
72 | 85 | 100 | 8.992
72 | 86 | 100 | 9.0632
72 | 87 | 100 | 9.1344
72 | 88 | 100 | 9.2056
72 | 89 | 100 | 9.2768
72 | 90 | 100 | 9.348
72 | 91 | 100 | 9.4192
72 | 92 | 100 | 9.4904
72 | 93 | 100 | 9.5616
72 | 94 | 100 | 9.6328
72 | 95 | 100 | 9.704
72 | 96 | 100 | 9.7752
72 | 97 | 100 | 9.8464
72 | 98 | 100 | 9.9176
72 | 99 | 100 | 9.9888
72 | 100 | 100 | 10.06
72 | 101 | 100 | 10.0672
72 | 102 | 100 | 10.0744
72 | 103 | 100 | 10.0816
72 | 104 | 100 | 10.0888
72 | 105 | 100 | 10.096
72 | 106 | 100 | 10.1032
72 | 107 | 100 | 10.1104
72 | 108 | 100 | 10.1176
72 | 109 | 100 | 10.1248
72 | 110 | 100 | 10.132
72 | 111 | 100 | 10.1392
72 | 112 | 100 | 10.1464
72 | 113 | 100 | 10.1536
72 | 114 | 100 | 10.1608
72 | 115 | 100 | 10.168
72 | 116 | 100 | 10.1752
72 | 117 | 100 | 10.1824
72 | 118 | 100 | 10.1896
72 | 119 | 100 | 10.1968
72 | 120 | 100 | 10.204
72 | 121 | 100 | 10.2112
72 | 122 | 100 | 10.2184
72 | 123 | 100 | 10.2256
72 | 124 | 100 | 10.2328
72 | 125 | 100 | 10.24
72 | 126 | 100 | 10.2648
72 | 127 | 100 | 10.2896
72 | 128 | 100 | 10.3144
72 | 129 | 100 | 10.3392
72 | 130 | 100 | 10.364
72 | 131 | 100 | 10.3888
72 | 132 | 100 | 10.4136
72 | 133 | 100 | 10.4384
72 | 134 | 100 | 10.4632
72 | 135 | 100 | 10.488
72 | 136 | 100 | 10.5128
72 | 137 | 100 | 10.5376
72 | 138 | 100 | 10.5624
72 | 139 | 100 | 10.5872
72 | 140 | 100 | 10.612
72 | 141 | 100 | 10.6368
72 | 142 | 100 | 10.6616
72 | 143 | 100 | 10.6864
72 | 144 | 100 | 10.7112
72 | 145 | 100 | 10.736
72 | 146 | 100 | 10.7608
72 | 147 | 100 | 10.7856
72 | 148 | 100 | 10.8104
72 | 149 | 100 | 10.8352
72 | 150 | 100 | 10.86
73 | 45 | 100 | 6.8867
73 | 46 | 100 | 6.9333
73 | 47 | 100 | 6.98
73 | 48 | 100 | 7.0267
73 | 49 | 100 | 7.0733
73 | 50 | 100 | 7.12
73 | 51 | 100 | 7.1667
73 | 52 | 100 | 7.2133
73 | 53 | 100 | 7.26
73 | 54 | 100 | 7.3067
73 | 55 | 100 | 7.3533
73 | 56 | 100 | 7.4
73 | 57 | 100 | 7.4467
73 | 58 | 100 | 7.4933
73 | 59 | 100 | 7.54
73 | 60 | 100 | 7.5867
73 | 61 | 100 | 7.6333
73 | 62 | 100 | 7.68
73 | 63 | 100 | 7.7267
73 | 64 | 100 | 7.7733
73 | 65 | 100 | 7.82
73 | 66 | 100 | 7.8667
73 | 67 | 100 | 7.9133
73 | 68 | 100 | 7.96
73 | 69 | 100 | 8.0067
73 | 70 | 100 | 8.0533
73 | 71 | 100 | 8.1
73 | 72 | 100 | 8.1467
73 | 73 | 100 | 8.1933
73 | 74 | 100 | 8.24
73 | 75 | 100 | 8.2867
73 | 76 | 100 | 8.3581
73 | 77 | 100 | 8.4296
73 | 78 | 100 | 8.5011
73 | 79 | 100 | 8.5725
73 | 80 | 100 | 8.644
73 | 81 | 100 | 8.7155
73 | 82 | 100 | 8.7869
73 | 83 | 100 | 8.8584
73 | 84 | 100 | 8.9299
73 | 85 | 100 | 9.0013
73 | 86 | 100 | 9.0728
73 | 87 | 100 | 9.1443
73 | 88 | 100 | 9.2157
73 | 89 | 100 | 9.2872
73 | 90 | 100 | 9.3587
73 | 91 | 100 | 9.4301
73 | 92 | 100 | 9.5016
73 | 93 | 100 | 9.5731
73 | 94 | 100 | 9.6445
73 | 95 | 100 | 9.716
73 | 96 | 100 | 9.7875
73 | 97 | 100 | 9.8589
73 | 98 | 100 | 9.9304
73 | 99 | 100 | 10.0019
73 | 100 | 100 | 10.0733
73 | 101 | 100 | 10.0808
73 | 102 | 100 | 10.0883
73 | 103 | 100 | 10.0957
73 | 104 | 100 | 10.1032
73 | 105 | 100 | 10.1107
73 | 106 | 100 | 10.1181
73 | 107 | 100 | 10.1256
73 | 108 | 100 | 10.1331
73 | 109 | 100 | 10.1405
73 | 110 | 100 | 10.148
73 | 111 | 100 | 10.1555
73 | 112 | 100 | 10.1629
73 | 113 | 100 | 10.1704
73 | 114 | 100 | 10.1779
73 | 115 | 100 | 10.1853
73 | 116 | 100 | 10.1928
73 | 117 | 100 | 10.2003
73 | 118 | 100 | 10.2077
73 | 119 | 100 | 10.2152
73 | 120 | 100 | 10.2227
73 | 121 | 100 | 10.2301
73 | 122 | 100 | 10.2376
73 | 123 | 100 | 10.2451
73 | 124 | 100 | 10.2525
73 | 125 | 100 | 10.26
73 | 126 | 100 | 10.2845
73 | 127 | 100 | 10.3091
73 | 128 | 100 | 10.3336
73 | 129 | 100 | 10.3581
73 | 130 | 100 | 10.3827
73 | 131 | 100 | 10.4072
73 | 132 | 100 | 10.4317
73 | 133 | 100 | 10.4563
73 | 134 | 100 | 10.4808
73 | 135 | 100 | 10.5053
73 | 136 | 100 | 10.5299
73 | 137 | 100 | 10.5544
73 | 138 | 100 | 10.5789
73 | 139 | 100 | 10.6035
73 | 140 | 100 | 10.628
73 | 141 | 100 | 10.6525
73 | 142 | 100 | 10.6771
73 | 143 | 100 | 10.7016
73 | 144 | 100 | 10.7261
73 | 145 | 100 | 10.7507
73 | 146 | 100 | 10.7752
73 | 147 | 100 | 10.7997
73 | 148 | 100 | 10.8243
73 | 149 | 100 | 10.8488
73 | 150 | 100 | 10.8733
74 | 45 | 100 | 6.8933
74 | 46 | 100 | 6.94
74 | 47 | 100 | 6.9867
74 | 48 | 100 | 7.0333
74 | 49 | 100 | 7.08
74 | 50 | 100 | 7.1267
74 | 51 | 100 | 7.1733
74 | 52 | 100 | 7.22
74 | 53 | 100 | 7.2667
74 | 54 | 100 | 7.3133
74 | 55 | 100 | 7.36
74 | 56 | 100 | 7.4067
74 | 57 | 100 | 7.4533
74 | 58 | 100 | 7.5
74 | 59 | 100 | 7.5467
74 | 60 | 100 | 7.5933
74 | 61 | 100 | 7.64
74 | 62 | 100 | 7.6867
74 | 63 | 100 | 7.7333
74 | 64 | 100 | 7.78
74 | 65 | 100 | 7.8267
74 | 66 | 100 | 7.8733
74 | 67 | 100 | 7.92
74 | 68 | 100 | 7.9667
74 | 69 | 100 | 8.0133
74 | 70 | 100 | 8.06
74 | 71 | 100 | 8.1067
74 | 72 | 100 | 8.1533
74 | 73 | 100 | 8.2
74 | 74 | 100 | 8.2467
74 | 75 | 100 | 8.2933
74 | 76 | 100 | 8.3651
74 | 77 | 100 | 8.4368
74 | 78 | 100 | 8.5085
74 | 79 | 100 | 8.5803
74 | 80 | 100 | 8.652
74 | 81 | 100 | 8.7237
74 | 82 | 100 | 8.7955
74 | 83 | 100 | 8.8672
74 | 84 | 100 | 8.9389
74 | 85 | 100 | 9.0107
74 | 86 | 100 | 9.0824
74 | 87 | 100 | 9.1541
74 | 88 | 100 | 9.2259
74 | 89 | 100 | 9.2976
74 | 90 | 100 | 9.3693
74 | 91 | 100 | 9.4411
74 | 92 | 100 | 9.5128
74 | 93 | 100 | 9.5845
74 | 94 | 100 | 9.6563
74 | 95 | 100 | 9.728
74 | 96 | 100 | 9.7997
74 | 97 | 100 | 9.8715
74 | 98 | 100 | 9.9432
74 | 99 | 100 | 10.0149
74 | 100 | 100 | 10.0867
74 | 101 | 100 | 10.0944
74 | 102 | 100 | 10.1021
74 | 103 | 100 | 10.1099
74 | 104 | 100 | 10.1176
74 | 105 | 100 | 10.1253
74 | 106 | 100 | 10.1331
74 | 107 | 100 | 10.1408
74 | 108 | 100 | 10.1485
74 | 109 | 100 | 10.1563
74 | 110 | 100 | 10.164
74 | 111 | 100 | 10.1717
74 | 112 | 100 | 10.1795
74 | 113 | 100 | 10.1872
74 | 114 | 100 | 10.1949
74 | 115 | 100 | 10.2027
74 | 116 | 100 | 10.2104
74 | 117 | 100 | 10.2181
74 | 118 | 100 | 10.2259
74 | 119 | 100 | 10.2336
74 | 120 | 100 | 10.2413
74 | 121 | 100 | 10.2491
74 | 122 | 100 | 10.2568
74 | 123 | 100 | 10.2645
74 | 124 | 100 | 10.2723
74 | 125 | 100 | 10.28
74 | 126 | 100 | 10.3043
74 | 127 | 100 | 10.3285
74 | 128 | 100 | 10.3528
74 | 129 | 100 | 10.3771
74 | 130 | 100 | 10.4013
74 | 131 | 100 | 10.4256
74 | 132 | 100 | 10.4499
74 | 133 | 100 | 10.4741
74 | 134 | 100 | 10.4984
74 | 135 | 100 | 10.5227
74 | 136 | 100 | 10.5469
74 | 137 | 100 | 10.5712
74 | 138 | 100 | 10.5955
74 | 139 | 100 | 10.6197
74 | 140 | 100 | 10.644
74 | 141 | 100 | 10.6683
74 | 142 | 100 | 10.6925
74 | 143 | 100 | 10.7168
74 | 144 | 100 | 10.7411
74 | 145 | 100 | 10.7653
74 | 146 | 100 | 10.7896
74 | 147 | 100 | 10.8139
74 | 148 | 100 | 10.8381
74 | 149 | 100 | 10.8624
74 | 150 | 100 | 10.8867
75 | 45 | 100 | 6.9
75 | 46 | 100 | 6.9467
75 | 47 | 100 | 6.9933
75 | 48 | 100 | 7.04
75 | 49 | 100 | 7.0867
75 | 50 | 100 | 7.1333
75 | 51 | 100 | 7.18
75 | 52 | 100 | 7.2267
75 | 53 | 100 | 7.2733
75 | 54 | 100 | 7.32
75 | 55 | 100 | 7.3667
75 | 56 | 100 | 7.4133
75 | 57 | 100 | 7.46
75 | 58 | 100 | 7.5067
75 | 59 | 100 | 7.5533
75 | 60 | 100 | 7.6
75 | 61 | 100 | 7.6467
75 | 62 | 100 | 7.6933
75 | 63 | 100 | 7.74
75 | 64 | 100 | 7.7867
75 | 65 | 100 | 7.8333
75 | 66 | 100 | 7.88
75 | 67 | 100 | 7.9267
75 | 68 | 100 | 7.9733
75 | 69 | 100 | 8.02
75 | 70 | 100 | 8.0667
75 | 71 | 100 | 8.1133
75 | 72 | 100 | 8.16
75 | 73 | 100 | 8.2067
75 | 74 | 100 | 8.2533
75 | 75 | 100 | 8.3
75 | 76 | 100 | 8.372
75 | 77 | 100 | 8.444
75 | 78 | 100 | 8.516
75 | 79 | 100 | 8.588
75 | 80 | 100 | 8.66
75 | 81 | 100 | 8.732
75 | 82 | 100 | 8.804
75 | 83 | 100 | 8.876
75 | 84 | 100 | 8.948
75 | 85 | 100 | 9.02
75 | 86 | 100 | 9.092
75 | 87 | 100 | 9.164
75 | 88 | 100 | 9.236
75 | 89 | 100 | 9.308
75 | 90 | 100 | 9.38
75 | 91 | 100 | 9.452
75 | 92 | 100 | 9.524
75 | 93 | 100 | 9.596
75 | 94 | 100 | 9.668
75 | 95 | 100 | 9.74
75 | 96 | 100 | 9.812
75 | 97 | 100 | 9.884
75 | 98 | 100 | 9.956
75 | 99 | 100 | 10.028
75 | 100 | 100 | 10.1
75 | 101 | 100 | 10.108
75 | 102 | 100 | 10.116
75 | 103 | 100 | 10.124
75 | 104 | 100 | 10.132
75 | 105 | 100 | 10.14
75 | 106 | 100 | 10.148
75 | 107 | 100 | 10.156
75 | 108 | 100 | 10.164
75 | 109 | 100 | 10.172
75 | 110 | 100 | 10.18
75 | 111 | 100 | 10.188
75 | 112 | 100 | 10.196
75 | 113 | 100 | 10.204
75 | 114 | 100 | 10.212
75 | 115 | 100 | 10.22
75 | 116 | 100 | 10.228
75 | 117 | 100 | 10.236
75 | 118 | 100 | 10.244
75 | 119 | 100 | 10.252
75 | 120 | 100 | 10.26
75 | 121 | 100 | 10.268
75 | 122 | 100 | 10.276
75 | 123 | 100 | 10.284
75 | 124 | 100 | 10.292
75 | 125 | 100 | 10.3
75 | 126 | 100 | 10.324
75 | 127 | 100 | 10.348
75 | 128 | 100 | 10.372
75 | 129 | 100 | 10.396
75 | 130 | 100 | 10.42
75 | 131 | 100 | 10.444
75 | 132 | 100 | 10.468
75 | 133 | 100 | 10.492
75 | 134 | 100 | 10.516
75 | 135 | 100 | 10.54
75 | 136 | 100 | 10.564
75 | 137 | 100 | 10.588
75 | 138 | 100 | 10.612
75 | 139 | 100 | 10.636
75 | 140 | 100 | 10.66
75 | 141 | 100 | 10.684
75 | 142 | 100 | 10.708
75 | 143 | 100 | 10.732
75 | 144 | 100 | 10.756
75 | 145 | 100 | 10.78
75 | 146 | 100 | 10.804
75 | 147 | 100 | 10.828
75 | 148 | 100 | 10.852
75 | 149 | 100 | 10.876
75 | 150 | 100 | 10.9
30 | 45 | 135 | 4.6
30 | 46 | 135 | 4.67
30 | 47 | 135 | 4.74
30 | 48 | 135 | 4.81
30 | 49 | 135 | 4.88
30 | 50 | 135 | 4.95
30 | 51 | 135 | 5.02
30 | 52 | 135 | 5.09
30 | 53 | 135 | 5.16
30 | 54 | 135 | 5.23
30 | 55 | 135 | 5.3
30 | 56 | 135 | 5.37
30 | 57 | 135 | 5.44
30 | 58 | 135 | 5.51
30 | 59 | 135 | 5.58
30 | 60 | 135 | 5.65
30 | 61 | 135 | 5.72
30 | 62 | 135 | 5.79
30 | 63 | 135 | 5.86
30 | 64 | 135 | 5.93
30 | 65 | 135 | 6
30 | 66 | 135 | 6.07
30 | 67 | 135 | 6.14
30 | 68 | 135 | 6.21
30 | 69 | 135 | 6.28
30 | 70 | 135 | 6.35
30 | 71 | 135 | 6.42
30 | 72 | 135 | 6.49
30 | 73 | 135 | 6.56
30 | 74 | 135 | 6.63
30 | 75 | 135 | 6.7
30 | 76 | 135 | 6.72
30 | 77 | 135 | 6.74
30 | 78 | 135 | 6.76
30 | 79 | 135 | 6.78
30 | 80 | 135 | 6.8
30 | 81 | 135 | 6.82
30 | 82 | 135 | 6.84
30 | 83 | 135 | 6.86
30 | 84 | 135 | 6.88
30 | 85 | 135 | 6.9
30 | 86 | 135 | 6.92
30 | 87 | 135 | 6.94
30 | 88 | 135 | 6.96
30 | 89 | 135 | 6.98
30 | 90 | 135 | 7
30 | 91 | 135 | 7.02
30 | 92 | 135 | 7.04
30 | 93 | 135 | 7.06
30 | 94 | 135 | 7.08
30 | 95 | 135 | 7.1
30 | 96 | 135 | 7.12
30 | 97 | 135 | 7.14
30 | 98 | 135 | 7.16
30 | 99 | 135 | 7.18
30 | 100 | 135 | 7.2
30 | 101 | 135 | 7.244
30 | 102 | 135 | 7.288
30 | 103 | 135 | 7.332
30 | 104 | 135 | 7.376
30 | 105 | 135 | 7.42
30 | 106 | 135 | 7.464
30 | 107 | 135 | 7.508
30 | 108 | 135 | 7.552
30 | 109 | 135 | 7.596
30 | 110 | 135 | 7.64
30 | 111 | 135 | 7.684
30 | 112 | 135 | 7.728
30 | 113 | 135 | 7.772
30 | 114 | 135 | 7.816
30 | 115 | 135 | 7.86
30 | 116 | 135 | 7.904
30 | 117 | 135 | 7.948
30 | 118 | 135 | 7.992
30 | 119 | 135 | 8.036
30 | 120 | 135 | 8.08
30 | 121 | 135 | 8.124
30 | 122 | 135 | 8.168
30 | 123 | 135 | 8.212
30 | 124 | 135 | 8.256
30 | 125 | 135 | 8.3
30 | 126 | 135 | 8.348
30 | 127 | 135 | 8.396
30 | 128 | 135 | 8.444
30 | 129 | 135 | 8.492
30 | 130 | 135 | 8.54
30 | 131 | 135 | 8.588
30 | 132 | 135 | 8.636
30 | 133 | 135 | 8.684
30 | 134 | 135 | 8.732
30 | 135 | 135 | 8.78
30 | 136 | 135 | 8.828
30 | 137 | 135 | 8.876
30 | 138 | 135 | 8.924
30 | 139 | 135 | 8.972
30 | 140 | 135 | 9.02
30 | 141 | 135 | 9.068
30 | 142 | 135 | 9.116
30 | 143 | 135 | 9.164
30 | 144 | 135 | 9.212
30 | 145 | 135 | 9.26
30 | 146 | 135 | 9.308
30 | 147 | 135 | 9.356
30 | 148 | 135 | 9.404
30 | 149 | 135 | 9.452
30 | 150 | 135 | 9.5
31 | 45 | 135 | 4.6133
31 | 46 | 135 | 4.6836
31 | 47 | 135 | 4.7538
31 | 48 | 135 | 4.824
31 | 49 | 135 | 4.8942
31 | 50 | 135 | 4.9644
31 | 51 | 135 | 5.0347
31 | 52 | 135 | 5.1049
31 | 53 | 135 | 5.1751
31 | 54 | 135 | 5.2453
31 | 55 | 135 | 5.3156
31 | 56 | 135 | 5.3858
31 | 57 | 135 | 5.456
31 | 58 | 135 | 5.5262
31 | 59 | 135 | 5.5964
31 | 60 | 135 | 5.6667
31 | 61 | 135 | 5.7369
31 | 62 | 135 | 5.8071
31 | 63 | 135 | 5.8773
31 | 64 | 135 | 5.9476
31 | 65 | 135 | 6.0178
31 | 66 | 135 | 6.088
31 | 67 | 135 | 6.1582
31 | 68 | 135 | 6.2284
31 | 69 | 135 | 6.2987
31 | 70 | 135 | 6.3689
31 | 71 | 135 | 6.4391
31 | 72 | 135 | 6.5093
31 | 73 | 135 | 6.5796
31 | 74 | 135 | 6.6498
31 | 75 | 135 | 6.72
31 | 76 | 135 | 6.7403
31 | 77 | 135 | 6.7605
31 | 78 | 135 | 6.7808
31 | 79 | 135 | 6.8011
31 | 80 | 135 | 6.8213
31 | 81 | 135 | 6.8416
31 | 82 | 135 | 6.8619
31 | 83 | 135 | 6.8821
31 | 84 | 135 | 6.9024
31 | 85 | 135 | 6.9227
31 | 86 | 135 | 6.9429
31 | 87 | 135 | 6.9632
31 | 88 | 135 | 6.9835
31 | 89 | 135 | 7.0037
31 | 90 | 135 | 7.024
31 | 91 | 135 | 7.0443
31 | 92 | 135 | 7.0645
31 | 93 | 135 | 7.0848
31 | 94 | 135 | 7.1051
31 | 95 | 135 | 7.1253
31 | 96 | 135 | 7.1456
31 | 97 | 135 | 7.1659
31 | 98 | 135 | 7.1861
31 | 99 | 135 | 7.2064
31 | 100 | 135 | 7.2267
31 | 101 | 135 | 7.2701
31 | 102 | 135 | 7.3136
31 | 103 | 135 | 7.3571
31 | 104 | 135 | 7.4005
31 | 105 | 135 | 7.444
31 | 106 | 135 | 7.4875
31 | 107 | 135 | 7.5309
31 | 108 | 135 | 7.5744
31 | 109 | 135 | 7.6179
31 | 110 | 135 | 7.6613
31 | 111 | 135 | 7.7048
31 | 112 | 135 | 7.7483
31 | 113 | 135 | 7.7917
31 | 114 | 135 | 7.8352
31 | 115 | 135 | 7.8787
31 | 116 | 135 | 7.9221
31 | 117 | 135 | 7.9656
31 | 118 | 135 | 8.0091
31 | 119 | 135 | 8.0525
31 | 120 | 135 | 8.096
31 | 121 | 135 | 8.1395
31 | 122 | 135 | 8.1829
31 | 123 | 135 | 8.2264
31 | 124 | 135 | 8.2699
31 | 125 | 135 | 8.3133
31 | 126 | 135 | 8.3613
31 | 127 | 135 | 8.4093
31 | 128 | 135 | 8.4573
31 | 129 | 135 | 8.5053
31 | 130 | 135 | 8.5533
31 | 131 | 135 | 8.6013
31 | 132 | 135 | 8.6493
31 | 133 | 135 | 8.6973
31 | 134 | 135 | 8.7453
31 | 135 | 135 | 8.7933
31 | 136 | 135 | 8.8413
31 | 137 | 135 | 8.8893
31 | 138 | 135 | 8.9373
31 | 139 | 135 | 8.9853
31 | 140 | 135 | 9.0333
31 | 141 | 135 | 9.0813
31 | 142 | 135 | 9.1293
31 | 143 | 135 | 9.1773
31 | 144 | 135 | 9.2253
31 | 145 | 135 | 9.2733
31 | 146 | 135 | 9.3213
31 | 147 | 135 | 9.3693
31 | 148 | 135 | 9.4173
31 | 149 | 135 | 9.4653
31 | 150 | 135 | 9.5133
32 | 45 | 135 | 4.6267
32 | 46 | 135 | 4.6971
32 | 47 | 135 | 4.7676
32 | 48 | 135 | 4.838
32 | 49 | 135 | 4.9084
32 | 50 | 135 | 4.9789
32 | 51 | 135 | 5.0493
32 | 52 | 135 | 5.1198
32 | 53 | 135 | 5.1902
32 | 54 | 135 | 5.2607
32 | 55 | 135 | 5.3311
32 | 56 | 135 | 5.4016
32 | 57 | 135 | 5.472
32 | 58 | 135 | 5.5424
32 | 59 | 135 | 5.6129
32 | 60 | 135 | 5.6833
32 | 61 | 135 | 5.7538
32 | 62 | 135 | 5.8242
32 | 63 | 135 | 5.8947
32 | 64 | 135 | 5.9651
32 | 65 | 135 | 6.0356
32 | 66 | 135 | 6.106
32 | 67 | 135 | 6.1764
32 | 68 | 135 | 6.2469
32 | 69 | 135 | 6.3173
32 | 70 | 135 | 6.3878
32 | 71 | 135 | 6.4582
32 | 72 | 135 | 6.5287
32 | 73 | 135 | 6.5991
32 | 74 | 135 | 6.6696
32 | 75 | 135 | 6.74
32 | 76 | 135 | 6.7605
32 | 77 | 135 | 6.7811
32 | 78 | 135 | 6.8016
32 | 79 | 135 | 6.8221
32 | 80 | 135 | 6.8427
32 | 81 | 135 | 6.8632
32 | 82 | 135 | 6.8837
32 | 83 | 135 | 6.9043
32 | 84 | 135 | 6.9248
32 | 85 | 135 | 6.9453
32 | 86 | 135 | 6.9659
32 | 87 | 135 | 6.9864
32 | 88 | 135 | 7.0069
32 | 89 | 135 | 7.0275
32 | 90 | 135 | 7.048
32 | 91 | 135 | 7.0685
32 | 92 | 135 | 7.0891
32 | 93 | 135 | 7.1096
32 | 94 | 135 | 7.1301
32 | 95 | 135 | 7.1507
32 | 96 | 135 | 7.1712
32 | 97 | 135 | 7.1917
32 | 98 | 135 | 7.2123
32 | 99 | 135 | 7.2328
32 | 100 | 135 | 7.2533
32 | 101 | 135 | 7.2963
32 | 102 | 135 | 7.3392
32 | 103 | 135 | 7.3821
32 | 104 | 135 | 7.4251
32 | 105 | 135 | 7.468
32 | 106 | 135 | 7.5109
32 | 107 | 135 | 7.5539
32 | 108 | 135 | 7.5968
32 | 109 | 135 | 7.6397
32 | 110 | 135 | 7.6827
32 | 111 | 135 | 7.7256
32 | 112 | 135 | 7.7685
32 | 113 | 135 | 7.8115
32 | 114 | 135 | 7.8544
32 | 115 | 135 | 7.8973
32 | 116 | 135 | 7.9403
32 | 117 | 135 | 7.9832
32 | 118 | 135 | 8.0261
32 | 119 | 135 | 8.0691
32 | 120 | 135 | 8.112
32 | 121 | 135 | 8.1549
32 | 122 | 135 | 8.1979
32 | 123 | 135 | 8.2408
32 | 124 | 135 | 8.2837
32 | 125 | 135 | 8.3267
32 | 126 | 135 | 8.3747
32 | 127 | 135 | 8.4227
32 | 128 | 135 | 8.4707
32 | 129 | 135 | 8.5187
32 | 130 | 135 | 8.5667
32 | 131 | 135 | 8.6147
32 | 132 | 135 | 8.6627
32 | 133 | 135 | 8.7107
32 | 134 | 135 | 8.7587
32 | 135 | 135 | 8.8067
32 | 136 | 135 | 8.8547
32 | 137 | 135 | 8.9027
32 | 138 | 135 | 8.9507
32 | 139 | 135 | 8.9987
32 | 140 | 135 | 9.0467
32 | 141 | 135 | 9.0947
32 | 142 | 135 | 9.1427
32 | 143 | 135 | 9.1907
32 | 144 | 135 | 9.2387
32 | 145 | 135 | 9.2867
32 | 146 | 135 | 9.3347
32 | 147 | 135 | 9.3827
32 | 148 | 135 | 9.4307
32 | 149 | 135 | 9.4787
32 | 150 | 135 | 9.5267
33 | 45 | 135 | 4.64
33 | 46 | 135 | 4.7107
33 | 47 | 135 | 4.7813
33 | 48 | 135 | 4.852
33 | 49 | 135 | 4.9227
33 | 50 | 135 | 4.9933
33 | 51 | 135 | 5.064
33 | 52 | 135 | 5.1347
33 | 53 | 135 | 5.2053
33 | 54 | 135 | 5.276
33 | 55 | 135 | 5.3467
33 | 56 | 135 | 5.4173
33 | 57 | 135 | 5.488
33 | 58 | 135 | 5.5587
33 | 59 | 135 | 5.6293
33 | 60 | 135 | 5.7
33 | 61 | 135 | 5.7707
33 | 62 | 135 | 5.8413
33 | 63 | 135 | 5.912
33 | 64 | 135 | 5.9827
33 | 65 | 135 | 6.0533
33 | 66 | 135 | 6.124
33 | 67 | 135 | 6.1947
33 | 68 | 135 | 6.2653
33 | 69 | 135 | 6.336
33 | 70 | 135 | 6.4067
33 | 71 | 135 | 6.4773
33 | 72 | 135 | 6.548
33 | 73 | 135 | 6.6187
33 | 74 | 135 | 6.6893
33 | 75 | 135 | 6.76
33 | 76 | 135 | 6.7808
33 | 77 | 135 | 6.8016
33 | 78 | 135 | 6.8224
33 | 79 | 135 | 6.8432
33 | 80 | 135 | 6.864
33 | 81 | 135 | 6.8848
33 | 82 | 135 | 6.9056
33 | 83 | 135 | 6.9264
33 | 84 | 135 | 6.9472
33 | 85 | 135 | 6.968
33 | 86 | 135 | 6.9888
33 | 87 | 135 | 7.0096
33 | 88 | 135 | 7.0304
33 | 89 | 135 | 7.0512
33 | 90 | 135 | 7.072
33 | 91 | 135 | 7.0928
33 | 92 | 135 | 7.1136
33 | 93 | 135 | 7.1344
33 | 94 | 135 | 7.1552
33 | 95 | 135 | 7.176
33 | 96 | 135 | 7.1968
33 | 97 | 135 | 7.2176
33 | 98 | 135 | 7.2384
33 | 99 | 135 | 7.2592
33 | 100 | 135 | 7.28
33 | 101 | 135 | 7.3224
33 | 102 | 135 | 7.3648
33 | 103 | 135 | 7.4072
33 | 104 | 135 | 7.4496
33 | 105 | 135 | 7.492
33 | 106 | 135 | 7.5344
33 | 107 | 135 | 7.5768
33 | 108 | 135 | 7.6192
33 | 109 | 135 | 7.6616
33 | 110 | 135 | 7.704
33 | 111 | 135 | 7.7464
33 | 112 | 135 | 7.7888
33 | 113 | 135 | 7.8312
33 | 114 | 135 | 7.8736
33 | 115 | 135 | 7.916
33 | 116 | 135 | 7.9584
33 | 117 | 135 | 8.0008
33 | 118 | 135 | 8.0432
33 | 119 | 135 | 8.0856
33 | 120 | 135 | 8.128
33 | 121 | 135 | 8.1704
33 | 122 | 135 | 8.2128
33 | 123 | 135 | 8.2552
33 | 124 | 135 | 8.2976
33 | 125 | 135 | 8.34
33 | 126 | 135 | 8.388
33 | 127 | 135 | 8.436
33 | 128 | 135 | 8.484
33 | 129 | 135 | 8.532
33 | 130 | 135 | 8.58
33 | 131 | 135 | 8.628
33 | 132 | 135 | 8.676
33 | 133 | 135 | 8.724
33 | 134 | 135 | 8.772
33 | 135 | 135 | 8.82
33 | 136 | 135 | 8.868
33 | 137 | 135 | 8.916
33 | 138 | 135 | 8.964
33 | 139 | 135 | 9.012
33 | 140 | 135 | 9.06
33 | 141 | 135 | 9.108
33 | 142 | 135 | 9.156
33 | 143 | 135 | 9.204
33 | 144 | 135 | 9.252
33 | 145 | 135 | 9.3
33 | 146 | 135 | 9.348
33 | 147 | 135 | 9.396
33 | 148 | 135 | 9.444
33 | 149 | 135 | 9.492
33 | 150 | 135 | 9.54
34 | 45 | 135 | 4.6533
34 | 46 | 135 | 4.7242
34 | 47 | 135 | 4.7951
34 | 48 | 135 | 4.866
34 | 49 | 135 | 4.9369
34 | 50 | 135 | 5.0078
34 | 51 | 135 | 5.0787
34 | 52 | 135 | 5.1496
34 | 53 | 135 | 5.2204
34 | 54 | 135 | 5.2913
34 | 55 | 135 | 5.3622
34 | 56 | 135 | 5.4331
34 | 57 | 135 | 5.504
34 | 58 | 135 | 5.5749
34 | 59 | 135 | 5.6458
34 | 60 | 135 | 5.7167
34 | 61 | 135 | 5.7876
34 | 62 | 135 | 5.8584
34 | 63 | 135 | 5.9293
34 | 64 | 135 | 6.0002
34 | 65 | 135 | 6.0711
34 | 66 | 135 | 6.142
34 | 67 | 135 | 6.2129
34 | 68 | 135 | 6.2838
34 | 69 | 135 | 6.3547
34 | 70 | 135 | 6.4256
34 | 71 | 135 | 6.4964
34 | 72 | 135 | 6.5673
34 | 73 | 135 | 6.6382
34 | 74 | 135 | 6.7091
34 | 75 | 135 | 6.78
34 | 76 | 135 | 6.8011
34 | 77 | 135 | 6.8221
34 | 78 | 135 | 6.8432
34 | 79 | 135 | 6.8643
34 | 80 | 135 | 6.8853
34 | 81 | 135 | 6.9064
34 | 82 | 135 | 6.9275
34 | 83 | 135 | 6.9485
34 | 84 | 135 | 6.9696
34 | 85 | 135 | 6.9907
34 | 86 | 135 | 7.0117
34 | 87 | 135 | 7.0328
34 | 88 | 135 | 7.0539
34 | 89 | 135 | 7.0749
34 | 90 | 135 | 7.096
34 | 91 | 135 | 7.1171
34 | 92 | 135 | 7.1381
34 | 93 | 135 | 7.1592
34 | 94 | 135 | 7.1803
34 | 95 | 135 | 7.2013
34 | 96 | 135 | 7.2224
34 | 97 | 135 | 7.2435
34 | 98 | 135 | 7.2645
34 | 99 | 135 | 7.2856
34 | 100 | 135 | 7.3067
34 | 101 | 135 | 7.3485
34 | 102 | 135 | 7.3904
34 | 103 | 135 | 7.4323
34 | 104 | 135 | 7.4741
34 | 105 | 135 | 7.516
34 | 106 | 135 | 7.5579
34 | 107 | 135 | 7.5997
34 | 108 | 135 | 7.6416
34 | 109 | 135 | 7.6835
34 | 110 | 135 | 7.7253
34 | 111 | 135 | 7.7672
34 | 112 | 135 | 7.8091
34 | 113 | 135 | 7.8509
34 | 114 | 135 | 7.8928
34 | 115 | 135 | 7.9347
34 | 116 | 135 | 7.9765
34 | 117 | 135 | 8.0184
34 | 118 | 135 | 8.0603
34 | 119 | 135 | 8.1021
34 | 120 | 135 | 8.144
34 | 121 | 135 | 8.1859
34 | 122 | 135 | 8.2277
34 | 123 | 135 | 8.2696
34 | 124 | 135 | 8.3115
34 | 125 | 135 | 8.3533
34 | 126 | 135 | 8.4013
34 | 127 | 135 | 8.4493
34 | 128 | 135 | 8.4973
34 | 129 | 135 | 8.5453
34 | 130 | 135 | 8.5933
34 | 131 | 135 | 8.6413
34 | 132 | 135 | 8.6893
34 | 133 | 135 | 8.7373
34 | 134 | 135 | 8.7853
34 | 135 | 135 | 8.8333
34 | 136 | 135 | 8.8813
34 | 137 | 135 | 8.9293
34 | 138 | 135 | 8.9773
34 | 139 | 135 | 9.0253
34 | 140 | 135 | 9.0733
34 | 141 | 135 | 9.1213
34 | 142 | 135 | 9.1693
34 | 143 | 135 | 9.2173
34 | 144 | 135 | 9.2653
34 | 145 | 135 | 9.3133
34 | 146 | 135 | 9.3613
34 | 147 | 135 | 9.4093
34 | 148 | 135 | 9.4573
34 | 149 | 135 | 9.5053
34 | 150 | 135 | 9.5533
35 | 45 | 135 | 4.6667
35 | 46 | 135 | 4.7378
35 | 47 | 135 | 4.8089
35 | 48 | 135 | 4.88
35 | 49 | 135 | 4.9511
35 | 50 | 135 | 5.0222
35 | 51 | 135 | 5.0933
35 | 52 | 135 | 5.1644
35 | 53 | 135 | 5.2356
35 | 54 | 135 | 5.3067
35 | 55 | 135 | 5.3778
35 | 56 | 135 | 5.4489
35 | 57 | 135 | 5.52
35 | 58 | 135 | 5.5911
35 | 59 | 135 | 5.6622
35 | 60 | 135 | 5.7333
35 | 61 | 135 | 5.8044
35 | 62 | 135 | 5.8756
35 | 63 | 135 | 5.9467
35 | 64 | 135 | 6.0178
35 | 65 | 135 | 6.0889
35 | 66 | 135 | 6.16
35 | 67 | 135 | 6.2311
35 | 68 | 135 | 6.3022
35 | 69 | 135 | 6.3733
35 | 70 | 135 | 6.4444
35 | 71 | 135 | 6.5156
35 | 72 | 135 | 6.5867
35 | 73 | 135 | 6.6578
35 | 74 | 135 | 6.7289
35 | 75 | 135 | 6.8
35 | 76 | 135 | 6.8213
35 | 77 | 135 | 6.8427
35 | 78 | 135 | 6.864
35 | 79 | 135 | 6.8853
35 | 80 | 135 | 6.9067
35 | 81 | 135 | 6.928
35 | 82 | 135 | 6.9493
35 | 83 | 135 | 6.9707
35 | 84 | 135 | 6.992
35 | 85 | 135 | 7.0133
35 | 86 | 135 | 7.0347
35 | 87 | 135 | 7.056
35 | 88 | 135 | 7.0773
35 | 89 | 135 | 7.0987
35 | 90 | 135 | 7.12
35 | 91 | 135 | 7.1413
35 | 92 | 135 | 7.1627
35 | 93 | 135 | 7.184
35 | 94 | 135 | 7.2053
35 | 95 | 135 | 7.2267
35 | 96 | 135 | 7.248
35 | 97 | 135 | 7.2693
35 | 98 | 135 | 7.2907
35 | 99 | 135 | 7.312
35 | 100 | 135 | 7.3333
35 | 101 | 135 | 7.3747
35 | 102 | 135 | 7.416
35 | 103 | 135 | 7.4573
35 | 104 | 135 | 7.4987
35 | 105 | 135 | 7.54
35 | 106 | 135 | 7.5813
35 | 107 | 135 | 7.6227
35 | 108 | 135 | 7.664
35 | 109 | 135 | 7.7053
35 | 110 | 135 | 7.7467
35 | 111 | 135 | 7.788
35 | 112 | 135 | 7.8293
35 | 113 | 135 | 7.8707
35 | 114 | 135 | 7.912
35 | 115 | 135 | 7.9533
35 | 116 | 135 | 7.9947
35 | 117 | 135 | 8.036
35 | 118 | 135 | 8.0773
35 | 119 | 135 | 8.1187
35 | 120 | 135 | 8.16
35 | 121 | 135 | 8.2013
35 | 122 | 135 | 8.2427
35 | 123 | 135 | 8.284
35 | 124 | 135 | 8.3253
35 | 125 | 135 | 8.3667
35 | 126 | 135 | 8.4147
35 | 127 | 135 | 8.4627
35 | 128 | 135 | 8.5107
35 | 129 | 135 | 8.5587
35 | 130 | 135 | 8.6067
35 | 131 | 135 | 8.6547
35 | 132 | 135 | 8.7027
35 | 133 | 135 | 8.7507
35 | 134 | 135 | 8.7987
35 | 135 | 135 | 8.8467
35 | 136 | 135 | 8.8947
35 | 137 | 135 | 8.9427
35 | 138 | 135 | 8.9907
35 | 139 | 135 | 9.0387
35 | 140 | 135 | 9.0867
35 | 141 | 135 | 9.1347
35 | 142 | 135 | 9.1827
35 | 143 | 135 | 9.2307
35 | 144 | 135 | 9.2787
35 | 145 | 135 | 9.3267
35 | 146 | 135 | 9.3747
35 | 147 | 135 | 9.4227
35 | 148 | 135 | 9.4707
35 | 149 | 135 | 9.5187
35 | 150 | 135 | 9.5667
36 | 45 | 135 | 4.68
36 | 46 | 135 | 4.7513
36 | 47 | 135 | 4.8227
36 | 48 | 135 | 4.894
36 | 49 | 135 | 4.9653
36 | 50 | 135 | 5.0367
36 | 51 | 135 | 5.108
36 | 52 | 135 | 5.1793
36 | 53 | 135 | 5.2507
36 | 54 | 135 | 5.322
36 | 55 | 135 | 5.3933
36 | 56 | 135 | 5.4647
36 | 57 | 135 | 5.536
36 | 58 | 135 | 5.6073
36 | 59 | 135 | 5.6787
36 | 60 | 135 | 5.75
36 | 61 | 135 | 5.8213
36 | 62 | 135 | 5.8927
36 | 63 | 135 | 5.964
36 | 64 | 135 | 6.0353
36 | 65 | 135 | 6.1067
36 | 66 | 135 | 6.178
36 | 67 | 135 | 6.2493
36 | 68 | 135 | 6.3207
36 | 69 | 135 | 6.392
36 | 70 | 135 | 6.4633
36 | 71 | 135 | 6.5347
36 | 72 | 135 | 6.606
36 | 73 | 135 | 6.6773
36 | 74 | 135 | 6.7487
36 | 75 | 135 | 6.82
36 | 76 | 135 | 6.8416
36 | 77 | 135 | 6.8632
36 | 78 | 135 | 6.8848
36 | 79 | 135 | 6.9064
36 | 80 | 135 | 6.928
36 | 81 | 135 | 6.9496
36 | 82 | 135 | 6.9712
36 | 83 | 135 | 6.9928
36 | 84 | 135 | 7.0144
36 | 85 | 135 | 7.036
36 | 86 | 135 | 7.0576
36 | 87 | 135 | 7.0792
36 | 88 | 135 | 7.1008
36 | 89 | 135 | 7.1224
36 | 90 | 135 | 7.144
36 | 91 | 135 | 7.1656
36 | 92 | 135 | 7.1872
36 | 93 | 135 | 7.2088
36 | 94 | 135 | 7.2304
36 | 95 | 135 | 7.252
36 | 96 | 135 | 7.2736
36 | 97 | 135 | 7.2952
36 | 98 | 135 | 7.3168
36 | 99 | 135 | 7.3384
36 | 100 | 135 | 7.36
36 | 101 | 135 | 7.4008
36 | 102 | 135 | 7.4416
36 | 103 | 135 | 7.4824
36 | 104 | 135 | 7.5232
36 | 105 | 135 | 7.564
36 | 106 | 135 | 7.6048
36 | 107 | 135 | 7.6456
36 | 108 | 135 | 7.6864
36 | 109 | 135 | 7.7272
36 | 110 | 135 | 7.768
36 | 111 | 135 | 7.8088
36 | 112 | 135 | 7.8496
36 | 113 | 135 | 7.8904
36 | 114 | 135 | 7.9312
36 | 115 | 135 | 7.972
36 | 116 | 135 | 8.0128
36 | 117 | 135 | 8.0536
36 | 118 | 135 | 8.0944
36 | 119 | 135 | 8.1352
36 | 120 | 135 | 8.176
36 | 121 | 135 | 8.2168
36 | 122 | 135 | 8.2576
36 | 123 | 135 | 8.2984
36 | 124 | 135 | 8.3392
36 | 125 | 135 | 8.38
36 | 126 | 135 | 8.428
36 | 127 | 135 | 8.476
36 | 128 | 135 | 8.524
36 | 129 | 135 | 8.572
36 | 130 | 135 | 8.62
36 | 131 | 135 | 8.668
36 | 132 | 135 | 8.716
36 | 133 | 135 | 8.764
36 | 134 | 135 | 8.812
36 | 135 | 135 | 8.86
36 | 136 | 135 | 8.908
36 | 137 | 135 | 8.956
36 | 138 | 135 | 9.004
36 | 139 | 135 | 9.052
36 | 140 | 135 | 9.1
36 | 141 | 135 | 9.148
36 | 142 | 135 | 9.196
36 | 143 | 135 | 9.244
36 | 144 | 135 | 9.292
36 | 145 | 135 | 9.34
36 | 146 | 135 | 9.388
36 | 147 | 135 | 9.436
36 | 148 | 135 | 9.484
36 | 149 | 135 | 9.532
36 | 150 | 135 | 9.58
37 | 45 | 135 | 4.6933
37 | 46 | 135 | 4.7649
37 | 47 | 135 | 4.8364
37 | 48 | 135 | 4.908
37 | 49 | 135 | 4.9796
37 | 50 | 135 | 5.0511
37 | 51 | 135 | 5.1227
37 | 52 | 135 | 5.1942
37 | 53 | 135 | 5.2658
37 | 54 | 135 | 5.3373
37 | 55 | 135 | 5.4089
37 | 56 | 135 | 5.4804
37 | 57 | 135 | 5.552
37 | 58 | 135 | 5.6236
37 | 59 | 135 | 5.6951
37 | 60 | 135 | 5.7667
37 | 61 | 135 | 5.8382
37 | 62 | 135 | 5.9098
37 | 63 | 135 | 5.9813
37 | 64 | 135 | 6.0529
37 | 65 | 135 | 6.1244
37 | 66 | 135 | 6.196
37 | 67 | 135 | 6.2676
37 | 68 | 135 | 6.3391
37 | 69 | 135 | 6.4107
37 | 70 | 135 | 6.4822
37 | 71 | 135 | 6.5538
37 | 72 | 135 | 6.6253
37 | 73 | 135 | 6.6969
37 | 74 | 135 | 6.7684
37 | 75 | 135 | 6.84
37 | 76 | 135 | 6.8619
37 | 77 | 135 | 6.8837
37 | 78 | 135 | 6.9056
37 | 79 | 135 | 6.9275
37 | 80 | 135 | 6.9493
37 | 81 | 135 | 6.9712
37 | 82 | 135 | 6.9931
37 | 83 | 135 | 7.0149
37 | 84 | 135 | 7.0368
37 | 85 | 135 | 7.0587
37 | 86 | 135 | 7.0805
37 | 87 | 135 | 7.1024
37 | 88 | 135 | 7.1243
37 | 89 | 135 | 7.1461
37 | 90 | 135 | 7.168
37 | 91 | 135 | 7.1899
37 | 92 | 135 | 7.2117
37 | 93 | 135 | 7.2336
37 | 94 | 135 | 7.2555
37 | 95 | 135 | 7.2773
37 | 96 | 135 | 7.2992
37 | 97 | 135 | 7.3211
37 | 98 | 135 | 7.3429
37 | 99 | 135 | 7.3648
37 | 100 | 135 | 7.3867
37 | 101 | 135 | 7.4269
37 | 102 | 135 | 7.4672
37 | 103 | 135 | 7.5075
37 | 104 | 135 | 7.5477
37 | 105 | 135 | 7.588
37 | 106 | 135 | 7.6283
37 | 107 | 135 | 7.6685
37 | 108 | 135 | 7.7088
37 | 109 | 135 | 7.7491
37 | 110 | 135 | 7.7893
37 | 111 | 135 | 7.8296
37 | 112 | 135 | 7.8699
37 | 113 | 135 | 7.9101
37 | 114 | 135 | 7.9504
37 | 115 | 135 | 7.9907
37 | 116 | 135 | 8.0309
37 | 117 | 135 | 8.0712
37 | 118 | 135 | 8.1115
37 | 119 | 135 | 8.1517
37 | 120 | 135 | 8.192
37 | 121 | 135 | 8.2323
37 | 122 | 135 | 8.2725
37 | 123 | 135 | 8.3128
37 | 124 | 135 | 8.3531
37 | 125 | 135 | 8.3933
37 | 126 | 135 | 8.4413
37 | 127 | 135 | 8.4893
37 | 128 | 135 | 8.5373
37 | 129 | 135 | 8.5853
37 | 130 | 135 | 8.6333
37 | 131 | 135 | 8.6813
37 | 132 | 135 | 8.7293
37 | 133 | 135 | 8.7773
37 | 134 | 135 | 8.8253
37 | 135 | 135 | 8.8733
37 | 136 | 135 | 8.9213
37 | 137 | 135 | 8.9693
37 | 138 | 135 | 9.0173
37 | 139 | 135 | 9.0653
37 | 140 | 135 | 9.1133
37 | 141 | 135 | 9.1613
37 | 142 | 135 | 9.2093
37 | 143 | 135 | 9.2573
37 | 144 | 135 | 9.3053
37 | 145 | 135 | 9.3533
37 | 146 | 135 | 9.4013
37 | 147 | 135 | 9.4493
37 | 148 | 135 | 9.4973
37 | 149 | 135 | 9.5453
37 | 150 | 135 | 9.5933
38 | 45 | 135 | 4.7067
38 | 46 | 135 | 4.7784
38 | 47 | 135 | 4.8502
38 | 48 | 135 | 4.922
38 | 49 | 135 | 4.9938
38 | 50 | 135 | 5.0656
38 | 51 | 135 | 5.1373
38 | 52 | 135 | 5.2091
38 | 53 | 135 | 5.2809
38 | 54 | 135 | 5.3527
38 | 55 | 135 | 5.4244
38 | 56 | 135 | 5.4962
38 | 57 | 135 | 5.568
38 | 58 | 135 | 5.6398
38 | 59 | 135 | 5.7116
38 | 60 | 135 | 5.7833
38 | 61 | 135 | 5.8551
38 | 62 | 135 | 5.9269
38 | 63 | 135 | 5.9987
38 | 64 | 135 | 6.0704
38 | 65 | 135 | 6.1422
38 | 66 | 135 | 6.214
38 | 67 | 135 | 6.2858
38 | 68 | 135 | 6.3576
38 | 69 | 135 | 6.4293
38 | 70 | 135 | 6.5011
38 | 71 | 135 | 6.5729
38 | 72 | 135 | 6.6447
38 | 73 | 135 | 6.7164
38 | 74 | 135 | 6.7882
38 | 75 | 135 | 6.86
38 | 76 | 135 | 6.8821
38 | 77 | 135 | 6.9043
38 | 78 | 135 | 6.9264
38 | 79 | 135 | 6.9485
38 | 80 | 135 | 6.9707
38 | 81 | 135 | 6.9928
38 | 82 | 135 | 7.0149
38 | 83 | 135 | 7.0371
38 | 84 | 135 | 7.0592
38 | 85 | 135 | 7.0813
38 | 86 | 135 | 7.1035
38 | 87 | 135 | 7.1256
38 | 88 | 135 | 7.1477
38 | 89 | 135 | 7.1699
38 | 90 | 135 | 7.192
38 | 91 | 135 | 7.2141
38 | 92 | 135 | 7.2363
38 | 93 | 135 | 7.2584
38 | 94 | 135 | 7.2805
38 | 95 | 135 | 7.3027
38 | 96 | 135 | 7.3248
38 | 97 | 135 | 7.3469
38 | 98 | 135 | 7.3691
38 | 99 | 135 | 7.3912
38 | 100 | 135 | 7.4133
38 | 101 | 135 | 7.4531
38 | 102 | 135 | 7.4928
38 | 103 | 135 | 7.5325
38 | 104 | 135 | 7.5723
38 | 105 | 135 | 7.612
38 | 106 | 135 | 7.6517
38 | 107 | 135 | 7.6915
38 | 108 | 135 | 7.7312
38 | 109 | 135 | 7.7709
38 | 110 | 135 | 7.8107
38 | 111 | 135 | 7.8504
38 | 112 | 135 | 7.8901
38 | 113 | 135 | 7.9299
38 | 114 | 135 | 7.9696
38 | 115 | 135 | 8.0093
38 | 116 | 135 | 8.0491
38 | 117 | 135 | 8.0888
38 | 118 | 135 | 8.1285
38 | 119 | 135 | 8.1683
38 | 120 | 135 | 8.208
38 | 121 | 135 | 8.2477
38 | 122 | 135 | 8.2875
38 | 123 | 135 | 8.3272
38 | 124 | 135 | 8.3669
38 | 125 | 135 | 8.4067
38 | 126 | 135 | 8.4547
38 | 127 | 135 | 8.5027
38 | 128 | 135 | 8.5507
38 | 129 | 135 | 8.5987
38 | 130 | 135 | 8.6467
38 | 131 | 135 | 8.6947
38 | 132 | 135 | 8.7427
38 | 133 | 135 | 8.7907
38 | 134 | 135 | 8.8387
38 | 135 | 135 | 8.8867
38 | 136 | 135 | 8.9347
38 | 137 | 135 | 8.9827
38 | 138 | 135 | 9.0307
38 | 139 | 135 | 9.0787
38 | 140 | 135 | 9.1267
38 | 141 | 135 | 9.1747
38 | 142 | 135 | 9.2227
38 | 143 | 135 | 9.2707
38 | 144 | 135 | 9.3187
38 | 145 | 135 | 9.3667
38 | 146 | 135 | 9.4147
38 | 147 | 135 | 9.4627
38 | 148 | 135 | 9.5107
38 | 149 | 135 | 9.5587
38 | 150 | 135 | 9.6067
39 | 45 | 135 | 4.72
39 | 46 | 135 | 4.792
39 | 47 | 135 | 4.864
39 | 48 | 135 | 4.936
39 | 49 | 135 | 5.008
39 | 50 | 135 | 5.08
39 | 51 | 135 | 5.152
39 | 52 | 135 | 5.224
39 | 53 | 135 | 5.296
39 | 54 | 135 | 5.368
39 | 55 | 135 | 5.44
39 | 56 | 135 | 5.512
39 | 57 | 135 | 5.584
39 | 58 | 135 | 5.656
39 | 59 | 135 | 5.728
39 | 60 | 135 | 5.8
39 | 61 | 135 | 5.872
39 | 62 | 135 | 5.944
39 | 63 | 135 | 6.016
39 | 64 | 135 | 6.088
39 | 65 | 135 | 6.16
39 | 66 | 135 | 6.232
39 | 67 | 135 | 6.304
39 | 68 | 135 | 6.376
39 | 69 | 135 | 6.448
39 | 70 | 135 | 6.52
39 | 71 | 135 | 6.592
39 | 72 | 135 | 6.664
39 | 73 | 135 | 6.736
39 | 74 | 135 | 6.808
39 | 75 | 135 | 6.88
39 | 76 | 135 | 6.9024
39 | 77 | 135 | 6.9248
39 | 78 | 135 | 6.9472
39 | 79 | 135 | 6.9696
39 | 80 | 135 | 6.992
39 | 81 | 135 | 7.0144
39 | 82 | 135 | 7.0368
39 | 83 | 135 | 7.0592
39 | 84 | 135 | 7.0816
39 | 85 | 135 | 7.104
39 | 86 | 135 | 7.1264
39 | 87 | 135 | 7.1488
39 | 88 | 135 | 7.1712
39 | 89 | 135 | 7.1936
39 | 90 | 135 | 7.216
39 | 91 | 135 | 7.2384
39 | 92 | 135 | 7.2608
39 | 93 | 135 | 7.2832
39 | 94 | 135 | 7.3056
39 | 95 | 135 | 7.328
39 | 96 | 135 | 7.3504
39 | 97 | 135 | 7.3728
39 | 98 | 135 | 7.3952
39 | 99 | 135 | 7.4176
39 | 100 | 135 | 7.44
39 | 101 | 135 | 7.4792
39 | 102 | 135 | 7.5184
39 | 103 | 135 | 7.5576
39 | 104 | 135 | 7.5968
39 | 105 | 135 | 7.636
39 | 106 | 135 | 7.6752
39 | 107 | 135 | 7.7144
39 | 108 | 135 | 7.7536
39 | 109 | 135 | 7.7928
39 | 110 | 135 | 7.832
39 | 111 | 135 | 7.8712
39 | 112 | 135 | 7.9104
39 | 113 | 135 | 7.9496
39 | 114 | 135 | 7.9888
39 | 115 | 135 | 8.028
39 | 116 | 135 | 8.0672
39 | 117 | 135 | 8.1064
39 | 118 | 135 | 8.1456
39 | 119 | 135 | 8.1848
39 | 120 | 135 | 8.224
39 | 121 | 135 | 8.2632
39 | 122 | 135 | 8.3024
39 | 123 | 135 | 8.3416
39 | 124 | 135 | 8.3808
39 | 125 | 135 | 8.42
39 | 126 | 135 | 8.468
39 | 127 | 135 | 8.516
39 | 128 | 135 | 8.564
39 | 129 | 135 | 8.612
39 | 130 | 135 | 8.66
39 | 131 | 135 | 8.708
39 | 132 | 135 | 8.756
39 | 133 | 135 | 8.804
39 | 134 | 135 | 8.852
39 | 135 | 135 | 8.9
39 | 136 | 135 | 8.948
39 | 137 | 135 | 8.996
39 | 138 | 135 | 9.044
39 | 139 | 135 | 9.092
39 | 140 | 135 | 9.14
39 | 141 | 135 | 9.188
39 | 142 | 135 | 9.236
39 | 143 | 135 | 9.284
39 | 144 | 135 | 9.332
39 | 145 | 135 | 9.38
39 | 146 | 135 | 9.428
39 | 147 | 135 | 9.476
39 | 148 | 135 | 9.524
39 | 149 | 135 | 9.572
39 | 150 | 135 | 9.62
40 | 45 | 135 | 4.7333
40 | 46 | 135 | 4.8056
40 | 47 | 135 | 4.8778
40 | 48 | 135 | 4.95
40 | 49 | 135 | 5.0222
40 | 50 | 135 | 5.0944
40 | 51 | 135 | 5.1667
40 | 52 | 135 | 5.2389
40 | 53 | 135 | 5.3111
40 | 54 | 135 | 5.3833
40 | 55 | 135 | 5.4556
40 | 56 | 135 | 5.5278
40 | 57 | 135 | 5.6
40 | 58 | 135 | 5.6722
40 | 59 | 135 | 5.7444
40 | 60 | 135 | 5.8167
40 | 61 | 135 | 5.8889
40 | 62 | 135 | 5.9611
40 | 63 | 135 | 6.0333
40 | 64 | 135 | 6.1056
40 | 65 | 135 | 6.1778
40 | 66 | 135 | 6.25
40 | 67 | 135 | 6.3222
40 | 68 | 135 | 6.3944
40 | 69 | 135 | 6.4667
40 | 70 | 135 | 6.5389
40 | 71 | 135 | 6.6111
40 | 72 | 135 | 6.6833
40 | 73 | 135 | 6.7556
40 | 74 | 135 | 6.8278
40 | 75 | 135 | 6.9
40 | 76 | 135 | 6.9227
40 | 77 | 135 | 6.9453
40 | 78 | 135 | 6.968
40 | 79 | 135 | 6.9907
40 | 80 | 135 | 7.0133
40 | 81 | 135 | 7.036
40 | 82 | 135 | 7.0587
40 | 83 | 135 | 7.0813
40 | 84 | 135 | 7.104
40 | 85 | 135 | 7.1267
40 | 86 | 135 | 7.1493
40 | 87 | 135 | 7.172
40 | 88 | 135 | 7.1947
40 | 89 | 135 | 7.2173
40 | 90 | 135 | 7.24
40 | 91 | 135 | 7.2627
40 | 92 | 135 | 7.2853
40 | 93 | 135 | 7.308
40 | 94 | 135 | 7.3307
40 | 95 | 135 | 7.3533
40 | 96 | 135 | 7.376
40 | 97 | 135 | 7.3987
40 | 98 | 135 | 7.4213
40 | 99 | 135 | 7.444
40 | 100 | 135 | 7.4667
40 | 101 | 135 | 7.5053
40 | 102 | 135 | 7.544
40 | 103 | 135 | 7.5827
40 | 104 | 135 | 7.6213
40 | 105 | 135 | 7.66
40 | 106 | 135 | 7.6987
40 | 107 | 135 | 7.7373
40 | 108 | 135 | 7.776
40 | 109 | 135 | 7.8147
40 | 110 | 135 | 7.8533
40 | 111 | 135 | 7.892
40 | 112 | 135 | 7.9307
40 | 113 | 135 | 7.9693
40 | 114 | 135 | 8.008
40 | 115 | 135 | 8.0467
40 | 116 | 135 | 8.0853
40 | 117 | 135 | 8.124
40 | 118 | 135 | 8.1627
40 | 119 | 135 | 8.2013
40 | 120 | 135 | 8.24
40 | 121 | 135 | 8.2787
40 | 122 | 135 | 8.3173
40 | 123 | 135 | 8.356
40 | 124 | 135 | 8.3947
40 | 125 | 135 | 8.4333
40 | 126 | 135 | 8.4813
40 | 127 | 135 | 8.5293
40 | 128 | 135 | 8.5773
40 | 129 | 135 | 8.6253
40 | 130 | 135 | 8.6733
40 | 131 | 135 | 8.7213
40 | 132 | 135 | 8.7693
40 | 133 | 135 | 8.8173
40 | 134 | 135 | 8.8653
40 | 135 | 135 | 8.9133
40 | 136 | 135 | 8.9613
40 | 137 | 135 | 9.0093
40 | 138 | 135 | 9.0573
40 | 139 | 135 | 9.1053
40 | 140 | 135 | 9.1533
40 | 141 | 135 | 9.2013
40 | 142 | 135 | 9.2493
40 | 143 | 135 | 9.2973
40 | 144 | 135 | 9.3453
40 | 145 | 135 | 9.3933
40 | 146 | 135 | 9.4413
40 | 147 | 135 | 9.4893
40 | 148 | 135 | 9.5373
40 | 149 | 135 | 9.5853
40 | 150 | 135 | 9.6333
41 | 45 | 135 | 4.7467
41 | 46 | 135 | 4.8191
41 | 47 | 135 | 4.8916
41 | 48 | 135 | 4.964
41 | 49 | 135 | 5.0364
41 | 50 | 135 | 5.1089
41 | 51 | 135 | 5.1813
41 | 52 | 135 | 5.2538
41 | 53 | 135 | 5.3262
41 | 54 | 135 | 5.3987
41 | 55 | 135 | 5.4711
41 | 56 | 135 | 5.5436
41 | 57 | 135 | 5.616
41 | 58 | 135 | 5.6884
41 | 59 | 135 | 5.7609
41 | 60 | 135 | 5.8333
41 | 61 | 135 | 5.9058
41 | 62 | 135 | 5.9782
41 | 63 | 135 | 6.0507
41 | 64 | 135 | 6.1231
41 | 65 | 135 | 6.1956
41 | 66 | 135 | 6.268
41 | 67 | 135 | 6.3404
41 | 68 | 135 | 6.4129
41 | 69 | 135 | 6.4853
41 | 70 | 135 | 6.5578
41 | 71 | 135 | 6.6302
41 | 72 | 135 | 6.7027
41 | 73 | 135 | 6.7751
41 | 74 | 135 | 6.8476
41 | 75 | 135 | 6.92
41 | 76 | 135 | 6.9429
41 | 77 | 135 | 6.9659
41 | 78 | 135 | 6.9888
41 | 79 | 135 | 7.0117
41 | 80 | 135 | 7.0347
41 | 81 | 135 | 7.0576
41 | 82 | 135 | 7.0805
41 | 83 | 135 | 7.1035
41 | 84 | 135 | 7.1264
41 | 85 | 135 | 7.1493
41 | 86 | 135 | 7.1723
41 | 87 | 135 | 7.1952
41 | 88 | 135 | 7.2181
41 | 89 | 135 | 7.2411
41 | 90 | 135 | 7.264
41 | 91 | 135 | 7.2869
41 | 92 | 135 | 7.3099
41 | 93 | 135 | 7.3328
41 | 94 | 135 | 7.3557
41 | 95 | 135 | 7.3787
41 | 96 | 135 | 7.4016
41 | 97 | 135 | 7.4245
41 | 98 | 135 | 7.4475
41 | 99 | 135 | 7.4704
41 | 100 | 135 | 7.4933
41 | 101 | 135 | 7.5315
41 | 102 | 135 | 7.5696
41 | 103 | 135 | 7.6077
41 | 104 | 135 | 7.6459
41 | 105 | 135 | 7.684
41 | 106 | 135 | 7.7221
41 | 107 | 135 | 7.7603
41 | 108 | 135 | 7.7984
41 | 109 | 135 | 7.8365
41 | 110 | 135 | 7.8747
41 | 111 | 135 | 7.9128
41 | 112 | 135 | 7.9509
41 | 113 | 135 | 7.9891
41 | 114 | 135 | 8.0272
41 | 115 | 135 | 8.0653
41 | 116 | 135 | 8.1035
41 | 117 | 135 | 8.1416
41 | 118 | 135 | 8.1797
41 | 119 | 135 | 8.2179
41 | 120 | 135 | 8.256
41 | 121 | 135 | 8.2941
41 | 122 | 135 | 8.3323
41 | 123 | 135 | 8.3704
41 | 124 | 135 | 8.4085
41 | 125 | 135 | 8.4467
41 | 126 | 135 | 8.4947
41 | 127 | 135 | 8.5427
41 | 128 | 135 | 8.5907
41 | 129 | 135 | 8.6387
41 | 130 | 135 | 8.6867
41 | 131 | 135 | 8.7347
41 | 132 | 135 | 8.7827
41 | 133 | 135 | 8.8307
41 | 134 | 135 | 8.8787
41 | 135 | 135 | 8.9267
41 | 136 | 135 | 8.9747
41 | 137 | 135 | 9.0227
41 | 138 | 135 | 9.0707
41 | 139 | 135 | 9.1187
41 | 140 | 135 | 9.1667
41 | 141 | 135 | 9.2147
41 | 142 | 135 | 9.2627
41 | 143 | 135 | 9.3107
41 | 144 | 135 | 9.3587
41 | 145 | 135 | 9.4067
41 | 146 | 135 | 9.4547
41 | 147 | 135 | 9.5027
41 | 148 | 135 | 9.5507
41 | 149 | 135 | 9.5987
41 | 150 | 135 | 9.6467
42 | 45 | 135 | 4.76
42 | 46 | 135 | 4.8327
42 | 47 | 135 | 4.9053
42 | 48 | 135 | 4.978
42 | 49 | 135 | 5.0507
42 | 50 | 135 | 5.1233
42 | 51 | 135 | 5.196
42 | 52 | 135 | 5.2687
42 | 53 | 135 | 5.3413
42 | 54 | 135 | 5.414
42 | 55 | 135 | 5.4867
42 | 56 | 135 | 5.5593
42 | 57 | 135 | 5.632
42 | 58 | 135 | 5.7047
42 | 59 | 135 | 5.7773
42 | 60 | 135 | 5.85
42 | 61 | 135 | 5.9227
42 | 62 | 135 | 5.9953
42 | 63 | 135 | 6.068
42 | 64 | 135 | 6.1407
42 | 65 | 135 | 6.2133
42 | 66 | 135 | 6.286
42 | 67 | 135 | 6.3587
42 | 68 | 135 | 6.4313
42 | 69 | 135 | 6.504
42 | 70 | 135 | 6.5767
42 | 71 | 135 | 6.6493
42 | 72 | 135 | 6.722
42 | 73 | 135 | 6.7947
42 | 74 | 135 | 6.8673
42 | 75 | 135 | 6.94
42 | 76 | 135 | 6.9632
42 | 77 | 135 | 6.9864
42 | 78 | 135 | 7.0096
42 | 79 | 135 | 7.0328
42 | 80 | 135 | 7.056
42 | 81 | 135 | 7.0792
42 | 82 | 135 | 7.1024
42 | 83 | 135 | 7.1256
42 | 84 | 135 | 7.1488
42 | 85 | 135 | 7.172
42 | 86 | 135 | 7.1952
42 | 87 | 135 | 7.2184
42 | 88 | 135 | 7.2416
42 | 89 | 135 | 7.2648
42 | 90 | 135 | 7.288
42 | 91 | 135 | 7.3112
42 | 92 | 135 | 7.3344
42 | 93 | 135 | 7.3576
42 | 94 | 135 | 7.3808
42 | 95 | 135 | 7.404
42 | 96 | 135 | 7.4272
42 | 97 | 135 | 7.4504
42 | 98 | 135 | 7.4736
42 | 99 | 135 | 7.4968
42 | 100 | 135 | 7.52
42 | 101 | 135 | 7.5576
42 | 102 | 135 | 7.5952
42 | 103 | 135 | 7.6328
42 | 104 | 135 | 7.6704
42 | 105 | 135 | 7.708
42 | 106 | 135 | 7.7456
42 | 107 | 135 | 7.7832
42 | 108 | 135 | 7.8208
42 | 109 | 135 | 7.8584
42 | 110 | 135 | 7.896
42 | 111 | 135 | 7.9336
42 | 112 | 135 | 7.9712
42 | 113 | 135 | 8.0088
42 | 114 | 135 | 8.0464
42 | 115 | 135 | 8.084
42 | 116 | 135 | 8.1216
42 | 117 | 135 | 8.1592
42 | 118 | 135 | 8.1968
42 | 119 | 135 | 8.2344
42 | 120 | 135 | 8.272
42 | 121 | 135 | 8.3096
42 | 122 | 135 | 8.3472
42 | 123 | 135 | 8.3848
42 | 124 | 135 | 8.4224
42 | 125 | 135 | 8.46
42 | 126 | 135 | 8.508
42 | 127 | 135 | 8.556
42 | 128 | 135 | 8.604
42 | 129 | 135 | 8.652
42 | 130 | 135 | 8.7
42 | 131 | 135 | 8.748
42 | 132 | 135 | 8.796
42 | 133 | 135 | 8.844
42 | 134 | 135 | 8.892
42 | 135 | 135 | 8.94
42 | 136 | 135 | 8.988
42 | 137 | 135 | 9.036
42 | 138 | 135 | 9.084
42 | 139 | 135 | 9.132
42 | 140 | 135 | 9.18
42 | 141 | 135 | 9.228
42 | 142 | 135 | 9.276
42 | 143 | 135 | 9.324
42 | 144 | 135 | 9.372
42 | 145 | 135 | 9.42
42 | 146 | 135 | 9.468
42 | 147 | 135 | 9.516
42 | 148 | 135 | 9.564
42 | 149 | 135 | 9.612
42 | 150 | 135 | 9.66
43 | 45 | 135 | 4.7733
43 | 46 | 135 | 4.8462
43 | 47 | 135 | 4.9191
43 | 48 | 135 | 4.992
43 | 49 | 135 | 5.0649
43 | 50 | 135 | 5.1378
43 | 51 | 135 | 5.2107
43 | 52 | 135 | 5.2836
43 | 53 | 135 | 5.3564
43 | 54 | 135 | 5.4293
43 | 55 | 135 | 5.5022
43 | 56 | 135 | 5.5751
43 | 57 | 135 | 5.648
43 | 58 | 135 | 5.7209
43 | 59 | 135 | 5.7938
43 | 60 | 135 | 5.8667
43 | 61 | 135 | 5.9396
43 | 62 | 135 | 6.0124
43 | 63 | 135 | 6.0853
43 | 64 | 135 | 6.1582
43 | 65 | 135 | 6.2311
43 | 66 | 135 | 6.304
43 | 67 | 135 | 6.3769
43 | 68 | 135 | 6.4498
43 | 69 | 135 | 6.5227
43 | 70 | 135 | 6.5956
43 | 71 | 135 | 6.6684
43 | 72 | 135 | 6.7413
43 | 73 | 135 | 6.8142
43 | 74 | 135 | 6.8871
43 | 75 | 135 | 6.96
43 | 76 | 135 | 6.9835
43 | 77 | 135 | 7.0069
43 | 78 | 135 | 7.0304
43 | 79 | 135 | 7.0539
43 | 80 | 135 | 7.0773
43 | 81 | 135 | 7.1008
43 | 82 | 135 | 7.1243
43 | 83 | 135 | 7.1477
43 | 84 | 135 | 7.1712
43 | 85 | 135 | 7.1947
43 | 86 | 135 | 7.2181
43 | 87 | 135 | 7.2416
43 | 88 | 135 | 7.2651
43 | 89 | 135 | 7.2885
43 | 90 | 135 | 7.312
43 | 91 | 135 | 7.3355
43 | 92 | 135 | 7.3589
43 | 93 | 135 | 7.3824
43 | 94 | 135 | 7.4059
43 | 95 | 135 | 7.4293
43 | 96 | 135 | 7.4528
43 | 97 | 135 | 7.4763
43 | 98 | 135 | 7.4997
43 | 99 | 135 | 7.5232
43 | 100 | 135 | 7.5467
43 | 101 | 135 | 7.5837
43 | 102 | 135 | 7.6208
43 | 103 | 135 | 7.6579
43 | 104 | 135 | 7.6949
43 | 105 | 135 | 7.732
43 | 106 | 135 | 7.7691
43 | 107 | 135 | 7.8061
43 | 108 | 135 | 7.8432
43 | 109 | 135 | 7.8803
43 | 110 | 135 | 7.9173
43 | 111 | 135 | 7.9544
43 | 112 | 135 | 7.9915
43 | 113 | 135 | 8.0285
43 | 114 | 135 | 8.0656
43 | 115 | 135 | 8.1027
43 | 116 | 135 | 8.1397
43 | 117 | 135 | 8.1768
43 | 118 | 135 | 8.2139
43 | 119 | 135 | 8.2509
43 | 120 | 135 | 8.288
43 | 121 | 135 | 8.3251
43 | 122 | 135 | 8.3621
43 | 123 | 135 | 8.3992
43 | 124 | 135 | 8.4363
43 | 125 | 135 | 8.4733
43 | 126 | 135 | 8.5213
43 | 127 | 135 | 8.5693
43 | 128 | 135 | 8.6173
43 | 129 | 135 | 8.6653
43 | 130 | 135 | 8.7133
43 | 131 | 135 | 8.7613
43 | 132 | 135 | 8.8093
43 | 133 | 135 | 8.8573
43 | 134 | 135 | 8.9053
43 | 135 | 135 | 8.9533
43 | 136 | 135 | 9.0013
43 | 137 | 135 | 9.0493
43 | 138 | 135 | 9.0973
43 | 139 | 135 | 9.1453
43 | 140 | 135 | 9.1933
43 | 141 | 135 | 9.2413
43 | 142 | 135 | 9.2893
43 | 143 | 135 | 9.3373
43 | 144 | 135 | 9.3853
43 | 145 | 135 | 9.4333
43 | 146 | 135 | 9.4813
43 | 147 | 135 | 9.5293
43 | 148 | 135 | 9.5773
43 | 149 | 135 | 9.6253
43 | 150 | 135 | 9.6733
44 | 45 | 135 | 4.7867
44 | 46 | 135 | 4.8598
44 | 47 | 135 | 4.9329
44 | 48 | 135 | 5.006
44 | 49 | 135 | 5.0791
44 | 50 | 135 | 5.1522
44 | 51 | 135 | 5.2253
44 | 52 | 135 | 5.2984
44 | 53 | 135 | 5.3716
44 | 54 | 135 | 5.4447
44 | 55 | 135 | 5.5178
44 | 56 | 135 | 5.5909
44 | 57 | 135 | 5.664
44 | 58 | 135 | 5.7371
44 | 59 | 135 | 5.8102
44 | 60 | 135 | 5.8833
44 | 61 | 135 | 5.9564
44 | 62 | 135 | 6.0296
44 | 63 | 135 | 6.1027
44 | 64 | 135 | 6.1758
44 | 65 | 135 | 6.2489
44 | 66 | 135 | 6.322
44 | 67 | 135 | 6.3951
44 | 68 | 135 | 6.4682
44 | 69 | 135 | 6.5413
44 | 70 | 135 | 6.6144
44 | 71 | 135 | 6.6876
44 | 72 | 135 | 6.7607
44 | 73 | 135 | 6.8338
44 | 74 | 135 | 6.9069
44 | 75 | 135 | 6.98
44 | 76 | 135 | 7.0037
44 | 77 | 135 | 7.0275
44 | 78 | 135 | 7.0512
44 | 79 | 135 | 7.0749
44 | 80 | 135 | 7.0987
44 | 81 | 135 | 7.1224
44 | 82 | 135 | 7.1461
44 | 83 | 135 | 7.1699
44 | 84 | 135 | 7.1936
44 | 85 | 135 | 7.2173
44 | 86 | 135 | 7.2411
44 | 87 | 135 | 7.2648
44 | 88 | 135 | 7.2885
44 | 89 | 135 | 7.3123
44 | 90 | 135 | 7.336
44 | 91 | 135 | 7.3597
44 | 92 | 135 | 7.3835
44 | 93 | 135 | 7.4072
44 | 94 | 135 | 7.4309
44 | 95 | 135 | 7.4547
44 | 96 | 135 | 7.4784
44 | 97 | 135 | 7.5021
44 | 98 | 135 | 7.5259
44 | 99 | 135 | 7.5496
44 | 100 | 135 | 7.5733
44 | 101 | 135 | 7.6099
44 | 102 | 135 | 7.6464
44 | 103 | 135 | 7.6829
44 | 104 | 135 | 7.7195
44 | 105 | 135 | 7.756
44 | 106 | 135 | 7.7925
44 | 107 | 135 | 7.8291
44 | 108 | 135 | 7.8656
44 | 109 | 135 | 7.9021
44 | 110 | 135 | 7.9387
44 | 111 | 135 | 7.9752
44 | 112 | 135 | 8.0117
44 | 113 | 135 | 8.0483
44 | 114 | 135 | 8.0848
44 | 115 | 135 | 8.1213
44 | 116 | 135 | 8.1579
44 | 117 | 135 | 8.1944
44 | 118 | 135 | 8.2309
44 | 119 | 135 | 8.2675
44 | 120 | 135 | 8.304
44 | 121 | 135 | 8.3405
44 | 122 | 135 | 8.3771
44 | 123 | 135 | 8.4136
44 | 124 | 135 | 8.4501
44 | 125 | 135 | 8.4867
44 | 126 | 135 | 8.5347
44 | 127 | 135 | 8.5827
44 | 128 | 135 | 8.6307
44 | 129 | 135 | 8.6787
44 | 130 | 135 | 8.7267
44 | 131 | 135 | 8.7747
44 | 132 | 135 | 8.8227
44 | 133 | 135 | 8.8707
44 | 134 | 135 | 8.9187
44 | 135 | 135 | 8.9667
44 | 136 | 135 | 9.0147
44 | 137 | 135 | 9.0627
44 | 138 | 135 | 9.1107
44 | 139 | 135 | 9.1587
44 | 140 | 135 | 9.2067
44 | 141 | 135 | 9.2547
44 | 142 | 135 | 9.3027
44 | 143 | 135 | 9.3507
44 | 144 | 135 | 9.3987
44 | 145 | 135 | 9.4467
44 | 146 | 135 | 9.4947
44 | 147 | 135 | 9.5427
44 | 148 | 135 | 9.5907
44 | 149 | 135 | 9.6387
44 | 150 | 135 | 9.6867
45 | 45 | 135 | 4.8
45 | 46 | 135 | 4.8733
45 | 47 | 135 | 4.9467
45 | 48 | 135 | 5.02
45 | 49 | 135 | 5.0933
45 | 50 | 135 | 5.1667
45 | 51 | 135 | 5.24
45 | 52 | 135 | 5.3133
45 | 53 | 135 | 5.3867
45 | 54 | 135 | 5.46
45 | 55 | 135 | 5.5333
45 | 56 | 135 | 5.6067
45 | 57 | 135 | 5.68
45 | 58 | 135 | 5.7533
45 | 59 | 135 | 5.8267
45 | 60 | 135 | 5.9
45 | 61 | 135 | 5.9733
45 | 62 | 135 | 6.0467
45 | 63 | 135 | 6.12
45 | 64 | 135 | 6.1933
45 | 65 | 135 | 6.2667
45 | 66 | 135 | 6.34
45 | 67 | 135 | 6.4133
45 | 68 | 135 | 6.4867
45 | 69 | 135 | 6.56
45 | 70 | 135 | 6.6333
45 | 71 | 135 | 6.7067
45 | 72 | 135 | 6.78
45 | 73 | 135 | 6.8533
45 | 74 | 135 | 6.9267
45 | 75 | 135 | 7
45 | 76 | 135 | 7.024
45 | 77 | 135 | 7.048
45 | 78 | 135 | 7.072
45 | 79 | 135 | 7.096
45 | 80 | 135 | 7.12
45 | 81 | 135 | 7.144
45 | 82 | 135 | 7.168
45 | 83 | 135 | 7.192
45 | 84 | 135 | 7.216
45 | 85 | 135 | 7.24
45 | 86 | 135 | 7.264
45 | 87 | 135 | 7.288
45 | 88 | 135 | 7.312
45 | 89 | 135 | 7.336
45 | 90 | 135 | 7.36
45 | 91 | 135 | 7.384
45 | 92 | 135 | 7.408
45 | 93 | 135 | 7.432
45 | 94 | 135 | 7.456
45 | 95 | 135 | 7.48
45 | 96 | 135 | 7.504
45 | 97 | 135 | 7.528
45 | 98 | 135 | 7.552
45 | 99 | 135 | 7.576
45 | 100 | 135 | 7.6
45 | 101 | 135 | 7.636
45 | 102 | 135 | 7.672
45 | 103 | 135 | 7.708
45 | 104 | 135 | 7.744
45 | 105 | 135 | 7.78
45 | 106 | 135 | 7.816
45 | 107 | 135 | 7.852
45 | 108 | 135 | 7.888
45 | 109 | 135 | 7.924
45 | 110 | 135 | 7.96
45 | 111 | 135 | 7.996
45 | 112 | 135 | 8.032
45 | 113 | 135 | 8.068
45 | 114 | 135 | 8.104
45 | 115 | 135 | 8.14
45 | 116 | 135 | 8.176
45 | 117 | 135 | 8.212
45 | 118 | 135 | 8.248
45 | 119 | 135 | 8.284
45 | 120 | 135 | 8.32
45 | 121 | 135 | 8.356
45 | 122 | 135 | 8.392
45 | 123 | 135 | 8.428
45 | 124 | 135 | 8.464
45 | 125 | 135 | 8.5
45 | 126 | 135 | 8.548
45 | 127 | 135 | 8.596
45 | 128 | 135 | 8.644
45 | 129 | 135 | 8.692
45 | 130 | 135 | 8.74
45 | 131 | 135 | 8.788
45 | 132 | 135 | 8.836
45 | 133 | 135 | 8.884
45 | 134 | 135 | 8.932
45 | 135 | 135 | 8.98
45 | 136 | 135 | 9.028
45 | 137 | 135 | 9.076
45 | 138 | 135 | 9.124
45 | 139 | 135 | 9.172
45 | 140 | 135 | 9.22
45 | 141 | 135 | 9.268
45 | 142 | 135 | 9.316
45 | 143 | 135 | 9.364
45 | 144 | 135 | 9.412
45 | 145 | 135 | 9.46
45 | 146 | 135 | 9.508
45 | 147 | 135 | 9.556
45 | 148 | 135 | 9.604
45 | 149 | 135 | 9.652
45 | 150 | 135 | 9.7
46 | 45 | 135 | 4.8
46 | 46 | 135 | 4.8738
46 | 47 | 135 | 4.9476
46 | 48 | 135 | 5.0213
46 | 49 | 135 | 5.0951
46 | 50 | 135 | 5.1689
46 | 51 | 135 | 5.2427
46 | 52 | 135 | 5.3164
46 | 53 | 135 | 5.3902
46 | 54 | 135 | 5.464
46 | 55 | 135 | 5.5378
46 | 56 | 135 | 5.6116
46 | 57 | 135 | 5.6853
46 | 58 | 135 | 5.7591
46 | 59 | 135 | 5.8329
46 | 60 | 135 | 5.9067
46 | 61 | 135 | 5.9804
46 | 62 | 135 | 6.0542
46 | 63 | 135 | 6.128
46 | 64 | 135 | 6.2018
46 | 65 | 135 | 6.2756
46 | 66 | 135 | 6.3493
46 | 67 | 135 | 6.4231
46 | 68 | 135 | 6.4969
46 | 69 | 135 | 6.5707
46 | 70 | 135 | 6.6444
46 | 71 | 135 | 6.7182
46 | 72 | 135 | 6.792
46 | 73 | 135 | 6.8658
46 | 74 | 135 | 6.9396
46 | 75 | 135 | 7.0133
46 | 76 | 135 | 7.0373
46 | 77 | 135 | 7.0613
46 | 78 | 135 | 7.0853
46 | 79 | 135 | 7.1093
46 | 80 | 135 | 7.1333
46 | 81 | 135 | 7.1573
46 | 82 | 135 | 7.1813
46 | 83 | 135 | 7.2053
46 | 84 | 135 | 7.2293
46 | 85 | 135 | 7.2533
46 | 86 | 135 | 7.2773
46 | 87 | 135 | 7.3013
46 | 88 | 135 | 7.3253
46 | 89 | 135 | 7.3493
46 | 90 | 135 | 7.3733
46 | 91 | 135 | 7.3973
46 | 92 | 135 | 7.4213
46 | 93 | 135 | 7.4453
46 | 94 | 135 | 7.4693
46 | 95 | 135 | 7.4933
46 | 96 | 135 | 7.5173
46 | 97 | 135 | 7.5413
46 | 98 | 135 | 7.5653
46 | 99 | 135 | 7.5893
46 | 100 | 135 | 7.6133
46 | 101 | 135 | 7.6491
46 | 102 | 135 | 7.6848
46 | 103 | 135 | 7.7205
46 | 104 | 135 | 7.7563
46 | 105 | 135 | 7.792
46 | 106 | 135 | 7.8277
46 | 107 | 135 | 7.8635
46 | 108 | 135 | 7.8992
46 | 109 | 135 | 7.9349
46 | 110 | 135 | 7.9707
46 | 111 | 135 | 8.0064
46 | 112 | 135 | 8.0421
46 | 113 | 135 | 8.0779
46 | 114 | 135 | 8.1136
46 | 115 | 135 | 8.1493
46 | 116 | 135 | 8.1851
46 | 117 | 135 | 8.2208
46 | 118 | 135 | 8.2565
46 | 119 | 135 | 8.2923
46 | 120 | 135 | 8.328
46 | 121 | 135 | 8.3637
46 | 122 | 135 | 8.3995
46 | 123 | 135 | 8.4352
46 | 124 | 135 | 8.4709
46 | 125 | 135 | 8.5067
46 | 126 | 135 | 8.5547
46 | 127 | 135 | 8.6027
46 | 128 | 135 | 8.6507
46 | 129 | 135 | 8.6987
46 | 130 | 135 | 8.7467
46 | 131 | 135 | 8.7947
46 | 132 | 135 | 8.8427
46 | 133 | 135 | 8.8907
46 | 134 | 135 | 8.9387
46 | 135 | 135 | 8.9867
46 | 136 | 135 | 9.0347
46 | 137 | 135 | 9.0827
46 | 138 | 135 | 9.1307
46 | 139 | 135 | 9.1787
46 | 140 | 135 | 9.2267
46 | 141 | 135 | 9.2747
46 | 142 | 135 | 9.3227
46 | 143 | 135 | 9.3707
46 | 144 | 135 | 9.4187
46 | 145 | 135 | 9.4667
46 | 146 | 135 | 9.5147
46 | 147 | 135 | 9.5627
46 | 148 | 135 | 9.6107
46 | 149 | 135 | 9.6587
46 | 150 | 135 | 9.7067
47 | 45 | 135 | 4.8
47 | 46 | 135 | 4.8742
47 | 47 | 135 | 4.9484
47 | 48 | 135 | 5.0227
47 | 49 | 135 | 5.0969
47 | 50 | 135 | 5.1711
47 | 51 | 135 | 5.2453
47 | 52 | 135 | 5.3196
47 | 53 | 135 | 5.3938
47 | 54 | 135 | 5.468
47 | 55 | 135 | 5.5422
47 | 56 | 135 | 5.6164
47 | 57 | 135 | 5.6907
47 | 58 | 135 | 5.7649
47 | 59 | 135 | 5.8391
47 | 60 | 135 | 5.9133
47 | 61 | 135 | 5.9876
47 | 62 | 135 | 6.0618
47 | 63 | 135 | 6.136
47 | 64 | 135 | 6.2102
47 | 65 | 135 | 6.2844
47 | 66 | 135 | 6.3587
47 | 67 | 135 | 6.4329
47 | 68 | 135 | 6.5071
47 | 69 | 135 | 6.5813
47 | 70 | 135 | 6.6556
47 | 71 | 135 | 6.7298
47 | 72 | 135 | 6.804
47 | 73 | 135 | 6.8782
47 | 74 | 135 | 6.9524
47 | 75 | 135 | 7.0267
47 | 76 | 135 | 7.0507
47 | 77 | 135 | 7.0747
47 | 78 | 135 | 7.0987
47 | 79 | 135 | 7.1227
47 | 80 | 135 | 7.1467
47 | 81 | 135 | 7.1707
47 | 82 | 135 | 7.1947
47 | 83 | 135 | 7.2187
47 | 84 | 135 | 7.2427
47 | 85 | 135 | 7.2667
47 | 86 | 135 | 7.2907
47 | 87 | 135 | 7.3147
47 | 88 | 135 | 7.3387
47 | 89 | 135 | 7.3627
47 | 90 | 135 | 7.3867
47 | 91 | 135 | 7.4107
47 | 92 | 135 | 7.4347
47 | 93 | 135 | 7.4587
47 | 94 | 135 | 7.4827
47 | 95 | 135 | 7.5067
47 | 96 | 135 | 7.5307
47 | 97 | 135 | 7.5547
47 | 98 | 135 | 7.5787
47 | 99 | 135 | 7.6027
47 | 100 | 135 | 7.6267
47 | 101 | 135 | 7.6621
47 | 102 | 135 | 7.6976
47 | 103 | 135 | 7.7331
47 | 104 | 135 | 7.7685
47 | 105 | 135 | 7.804
47 | 106 | 135 | 7.8395
47 | 107 | 135 | 7.8749
47 | 108 | 135 | 7.9104
47 | 109 | 135 | 7.9459
47 | 110 | 135 | 7.9813
47 | 111 | 135 | 8.0168
47 | 112 | 135 | 8.0523
47 | 113 | 135 | 8.0877
47 | 114 | 135 | 8.1232
47 | 115 | 135 | 8.1587
47 | 116 | 135 | 8.1941
47 | 117 | 135 | 8.2296
47 | 118 | 135 | 8.2651
47 | 119 | 135 | 8.3005
47 | 120 | 135 | 8.336
47 | 121 | 135 | 8.3715
47 | 122 | 135 | 8.4069
47 | 123 | 135 | 8.4424
47 | 124 | 135 | 8.4779
47 | 125 | 135 | 8.5133
47 | 126 | 135 | 8.5613
47 | 127 | 135 | 8.6093
47 | 128 | 135 | 8.6573
47 | 129 | 135 | 8.7053
47 | 130 | 135 | 8.7533
47 | 131 | 135 | 8.8013
47 | 132 | 135 | 8.8493
47 | 133 | 135 | 8.8973
47 | 134 | 135 | 8.9453
47 | 135 | 135 | 8.9933
47 | 136 | 135 | 9.0413
47 | 137 | 135 | 9.0893
47 | 138 | 135 | 9.1373
47 | 139 | 135 | 9.1853
47 | 140 | 135 | 9.2333
47 | 141 | 135 | 9.2813
47 | 142 | 135 | 9.3293
47 | 143 | 135 | 9.3773
47 | 144 | 135 | 9.4253
47 | 145 | 135 | 9.4733
47 | 146 | 135 | 9.5213
47 | 147 | 135 | 9.5693
47 | 148 | 135 | 9.6173
47 | 149 | 135 | 9.6653
47 | 150 | 135 | 9.7133
48 | 45 | 135 | 4.8
48 | 46 | 135 | 4.8747
48 | 47 | 135 | 4.9493
48 | 48 | 135 | 5.024
48 | 49 | 135 | 5.0987
48 | 50 | 135 | 5.1733
48 | 51 | 135 | 5.248
48 | 52 | 135 | 5.3227
48 | 53 | 135 | 5.3973
48 | 54 | 135 | 5.472
48 | 55 | 135 | 5.5467
48 | 56 | 135 | 5.6213
48 | 57 | 135 | 5.696
48 | 58 | 135 | 5.7707
48 | 59 | 135 | 5.8453
48 | 60 | 135 | 5.92
48 | 61 | 135 | 5.9947
48 | 62 | 135 | 6.0693
48 | 63 | 135 | 6.144
48 | 64 | 135 | 6.2187
48 | 65 | 135 | 6.2933
48 | 66 | 135 | 6.368
48 | 67 | 135 | 6.4427
48 | 68 | 135 | 6.5173
48 | 69 | 135 | 6.592
48 | 70 | 135 | 6.6667
48 | 71 | 135 | 6.7413
48 | 72 | 135 | 6.816
48 | 73 | 135 | 6.8907
48 | 74 | 135 | 6.9653
48 | 75 | 135 | 7.04
48 | 76 | 135 | 7.064
48 | 77 | 135 | 7.088
48 | 78 | 135 | 7.112
48 | 79 | 135 | 7.136
48 | 80 | 135 | 7.16
48 | 81 | 135 | 7.184
48 | 82 | 135 | 7.208
48 | 83 | 135 | 7.232
48 | 84 | 135 | 7.256
48 | 85 | 135 | 7.28
48 | 86 | 135 | 7.304
48 | 87 | 135 | 7.328
48 | 88 | 135 | 7.352
48 | 89 | 135 | 7.376
48 | 90 | 135 | 7.4
48 | 91 | 135 | 7.424
48 | 92 | 135 | 7.448
48 | 93 | 135 | 7.472
48 | 94 | 135 | 7.496
48 | 95 | 135 | 7.52
48 | 96 | 135 | 7.544
48 | 97 | 135 | 7.568
48 | 98 | 135 | 7.592
48 | 99 | 135 | 7.616
48 | 100 | 135 | 7.64
48 | 101 | 135 | 7.6752
48 | 102 | 135 | 7.7104
48 | 103 | 135 | 7.7456
48 | 104 | 135 | 7.7808
48 | 105 | 135 | 7.816
48 | 106 | 135 | 7.8512
48 | 107 | 135 | 7.8864
48 | 108 | 135 | 7.9216
48 | 109 | 135 | 7.9568
48 | 110 | 135 | 7.992
48 | 111 | 135 | 8.0272
48 | 112 | 135 | 8.0624
48 | 113 | 135 | 8.0976
48 | 114 | 135 | 8.1328
48 | 115 | 135 | 8.168
48 | 116 | 135 | 8.2032
48 | 117 | 135 | 8.2384
48 | 118 | 135 | 8.2736
48 | 119 | 135 | 8.3088
48 | 120 | 135 | 8.344
48 | 121 | 135 | 8.3792
48 | 122 | 135 | 8.4144
48 | 123 | 135 | 8.4496
48 | 124 | 135 | 8.4848
48 | 125 | 135 | 8.52
48 | 126 | 135 | 8.568
48 | 127 | 135 | 8.616
48 | 128 | 135 | 8.664
48 | 129 | 135 | 8.712
48 | 130 | 135 | 8.76
48 | 131 | 135 | 8.808
48 | 132 | 135 | 8.856
48 | 133 | 135 | 8.904
48 | 134 | 135 | 8.952
48 | 135 | 135 | 9
48 | 136 | 135 | 9.048
48 | 137 | 135 | 9.096
48 | 138 | 135 | 9.144
48 | 139 | 135 | 9.192
48 | 140 | 135 | 9.24
48 | 141 | 135 | 9.288
48 | 142 | 135 | 9.336
48 | 143 | 135 | 9.384
48 | 144 | 135 | 9.432
48 | 145 | 135 | 9.48
48 | 146 | 135 | 9.528
48 | 147 | 135 | 9.576
48 | 148 | 135 | 9.624
48 | 149 | 135 | 9.672
48 | 150 | 135 | 9.72
49 | 45 | 135 | 4.8
49 | 46 | 135 | 4.8751
49 | 47 | 135 | 4.9502
49 | 48 | 135 | 5.0253
49 | 49 | 135 | 5.1004
49 | 50 | 135 | 5.1756
49 | 51 | 135 | 5.2507
49 | 52 | 135 | 5.3258
49 | 53 | 135 | 5.4009
49 | 54 | 135 | 5.476
49 | 55 | 135 | 5.5511
49 | 56 | 135 | 5.6262
49 | 57 | 135 | 5.7013
49 | 58 | 135 | 5.7764
49 | 59 | 135 | 5.8516
49 | 60 | 135 | 5.9267
49 | 61 | 135 | 6.0018
49 | 62 | 135 | 6.0769
49 | 63 | 135 | 6.152
49 | 64 | 135 | 6.2271
49 | 65 | 135 | 6.3022
49 | 66 | 135 | 6.3773
49 | 67 | 135 | 6.4524
49 | 68 | 135 | 6.5276
49 | 69 | 135 | 6.6027
49 | 70 | 135 | 6.6778
49 | 71 | 135 | 6.7529
49 | 72 | 135 | 6.828
49 | 73 | 135 | 6.9031
49 | 74 | 135 | 6.9782
49 | 75 | 135 | 7.0533
49 | 76 | 135 | 7.0773
49 | 77 | 135 | 7.1013
49 | 78 | 135 | 7.1253
49 | 79 | 135 | 7.1493
49 | 80 | 135 | 7.1733
49 | 81 | 135 | 7.1973
49 | 82 | 135 | 7.2213
49 | 83 | 135 | 7.2453
49 | 84 | 135 | 7.2693
49 | 85 | 135 | 7.2933
49 | 86 | 135 | 7.3173
49 | 87 | 135 | 7.3413
49 | 88 | 135 | 7.3653
49 | 89 | 135 | 7.3893
49 | 90 | 135 | 7.4133
49 | 91 | 135 | 7.4373
49 | 92 | 135 | 7.4613
49 | 93 | 135 | 7.4853
49 | 94 | 135 | 7.5093
49 | 95 | 135 | 7.5333
49 | 96 | 135 | 7.5573
49 | 97 | 135 | 7.5813
49 | 98 | 135 | 7.6053
49 | 99 | 135 | 7.6293
49 | 100 | 135 | 7.6533
49 | 101 | 135 | 7.6883
49 | 102 | 135 | 7.7232
49 | 103 | 135 | 7.7581
49 | 104 | 135 | 7.7931
49 | 105 | 135 | 7.828
49 | 106 | 135 | 7.8629
49 | 107 | 135 | 7.8979
49 | 108 | 135 | 7.9328
49 | 109 | 135 | 7.9677
49 | 110 | 135 | 8.0027
49 | 111 | 135 | 8.0376
49 | 112 | 135 | 8.0725
49 | 113 | 135 | 8.1075
49 | 114 | 135 | 8.1424
49 | 115 | 135 | 8.1773
49 | 116 | 135 | 8.2123
49 | 117 | 135 | 8.2472
49 | 118 | 135 | 8.2821
49 | 119 | 135 | 8.3171
49 | 120 | 135 | 8.352
49 | 121 | 135 | 8.3869
49 | 122 | 135 | 8.4219
49 | 123 | 135 | 8.4568
49 | 124 | 135 | 8.4917
49 | 125 | 135 | 8.5267
49 | 126 | 135 | 8.5747
49 | 127 | 135 | 8.6227
49 | 128 | 135 | 8.6707
49 | 129 | 135 | 8.7187
49 | 130 | 135 | 8.7667
49 | 131 | 135 | 8.8147
49 | 132 | 135 | 8.8627
49 | 133 | 135 | 8.9107
49 | 134 | 135 | 8.9587
49 | 135 | 135 | 9.0067
49 | 136 | 135 | 9.0547
49 | 137 | 135 | 9.1027
49 | 138 | 135 | 9.1507
49 | 139 | 135 | 9.1987
49 | 140 | 135 | 9.2467
49 | 141 | 135 | 9.2947
49 | 142 | 135 | 9.3427
49 | 143 | 135 | 9.3907
49 | 144 | 135 | 9.4387
49 | 145 | 135 | 9.4867
49 | 146 | 135 | 9.5347
49 | 147 | 135 | 9.5827
49 | 148 | 135 | 9.6307
49 | 149 | 135 | 9.6787
49 | 150 | 135 | 9.7267
50 | 45 | 135 | 4.8
50 | 46 | 135 | 4.8756
50 | 47 | 135 | 4.9511
50 | 48 | 135 | 5.0267
50 | 49 | 135 | 5.1022
50 | 50 | 135 | 5.1778
50 | 51 | 135 | 5.2533
50 | 52 | 135 | 5.3289
50 | 53 | 135 | 5.4044
50 | 54 | 135 | 5.48
50 | 55 | 135 | 5.5556
50 | 56 | 135 | 5.6311
50 | 57 | 135 | 5.7067
50 | 58 | 135 | 5.7822
50 | 59 | 135 | 5.8578
50 | 60 | 135 | 5.9333
50 | 61 | 135 | 6.0089
50 | 62 | 135 | 6.0844
50 | 63 | 135 | 6.16
50 | 64 | 135 | 6.2356
50 | 65 | 135 | 6.3111
50 | 66 | 135 | 6.3867
50 | 67 | 135 | 6.4622
50 | 68 | 135 | 6.5378
50 | 69 | 135 | 6.6133
50 | 70 | 135 | 6.6889
50 | 71 | 135 | 6.7644
50 | 72 | 135 | 6.84
50 | 73 | 135 | 6.9156
50 | 74 | 135 | 6.9911
50 | 75 | 135 | 7.0667
50 | 76 | 135 | 7.0907
50 | 77 | 135 | 7.1147
50 | 78 | 135 | 7.1387
50 | 79 | 135 | 7.1627
50 | 80 | 135 | 7.1867
50 | 81 | 135 | 7.2107
50 | 82 | 135 | 7.2347
50 | 83 | 135 | 7.2587
50 | 84 | 135 | 7.2827
50 | 85 | 135 | 7.3067
50 | 86 | 135 | 7.3307
50 | 87 | 135 | 7.3547
50 | 88 | 135 | 7.3787
50 | 89 | 135 | 7.4027
50 | 90 | 135 | 7.4267
50 | 91 | 135 | 7.4507
50 | 92 | 135 | 7.4747
50 | 93 | 135 | 7.4987
50 | 94 | 135 | 7.5227
50 | 95 | 135 | 7.5467
50 | 96 | 135 | 7.5707
50 | 97 | 135 | 7.5947
50 | 98 | 135 | 7.6187
50 | 99 | 135 | 7.6427
50 | 100 | 135 | 7.6667
50 | 101 | 135 | 7.7013
50 | 102 | 135 | 7.736
50 | 103 | 135 | 7.7707
50 | 104 | 135 | 7.8053
50 | 105 | 135 | 7.84
50 | 106 | 135 | 7.8747
50 | 107 | 135 | 7.9093
50 | 108 | 135 | 7.944
50 | 109 | 135 | 7.9787
50 | 110 | 135 | 8.0133
50 | 111 | 135 | 8.048
50 | 112 | 135 | 8.0827
50 | 113 | 135 | 8.1173
50 | 114 | 135 | 8.152
50 | 115 | 135 | 8.1867
50 | 116 | 135 | 8.2213
50 | 117 | 135 | 8.256
50 | 118 | 135 | 8.2907
50 | 119 | 135 | 8.3253
50 | 120 | 135 | 8.36
50 | 121 | 135 | 8.3947
50 | 122 | 135 | 8.4293
50 | 123 | 135 | 8.464
50 | 124 | 135 | 8.4987
50 | 125 | 135 | 8.5333
50 | 126 | 135 | 8.5813
50 | 127 | 135 | 8.6293
50 | 128 | 135 | 8.6773
50 | 129 | 135 | 8.7253
50 | 130 | 135 | 8.7733
50 | 131 | 135 | 8.8213
50 | 132 | 135 | 8.8693
50 | 133 | 135 | 8.9173
50 | 134 | 135 | 8.9653
50 | 135 | 135 | 9.0133
50 | 136 | 135 | 9.0613
50 | 137 | 135 | 9.1093
50 | 138 | 135 | 9.1573
50 | 139 | 135 | 9.2053
50 | 140 | 135 | 9.2533
50 | 141 | 135 | 9.3013
50 | 142 | 135 | 9.3493
50 | 143 | 135 | 9.3973
50 | 144 | 135 | 9.4453
50 | 145 | 135 | 9.4933
50 | 146 | 135 | 9.5413
50 | 147 | 135 | 9.5893
50 | 148 | 135 | 9.6373
50 | 149 | 135 | 9.6853
50 | 150 | 135 | 9.7333
51 | 45 | 135 | 4.8
51 | 46 | 135 | 4.876
51 | 47 | 135 | 4.952
51 | 48 | 135 | 5.028
51 | 49 | 135 | 5.104
51 | 50 | 135 | 5.18
51 | 51 | 135 | 5.256
51 | 52 | 135 | 5.332
51 | 53 | 135 | 5.408
51 | 54 | 135 | 5.484
51 | 55 | 135 | 5.56
51 | 56 | 135 | 5.636
51 | 57 | 135 | 5.712
51 | 58 | 135 | 5.788
51 | 59 | 135 | 5.864
51 | 60 | 135 | 5.94
51 | 61 | 135 | 6.016
51 | 62 | 135 | 6.092
51 | 63 | 135 | 6.168
51 | 64 | 135 | 6.244
51 | 65 | 135 | 6.32
51 | 66 | 135 | 6.396
51 | 67 | 135 | 6.472
51 | 68 | 135 | 6.548
51 | 69 | 135 | 6.624
51 | 70 | 135 | 6.7
51 | 71 | 135 | 6.776
51 | 72 | 135 | 6.852
51 | 73 | 135 | 6.928
51 | 74 | 135 | 7.004
51 | 75 | 135 | 7.08
51 | 76 | 135 | 7.104
51 | 77 | 135 | 7.128
51 | 78 | 135 | 7.152
51 | 79 | 135 | 7.176
51 | 80 | 135 | 7.2
51 | 81 | 135 | 7.224
51 | 82 | 135 | 7.248
51 | 83 | 135 | 7.272
51 | 84 | 135 | 7.296
51 | 85 | 135 | 7.32
51 | 86 | 135 | 7.344
51 | 87 | 135 | 7.368
51 | 88 | 135 | 7.392
51 | 89 | 135 | 7.416
51 | 90 | 135 | 7.44
51 | 91 | 135 | 7.464
51 | 92 | 135 | 7.488
51 | 93 | 135 | 7.512
51 | 94 | 135 | 7.536
51 | 95 | 135 | 7.56
51 | 96 | 135 | 7.584
51 | 97 | 135 | 7.608
51 | 98 | 135 | 7.632
51 | 99 | 135 | 7.656
51 | 100 | 135 | 7.68
51 | 101 | 135 | 7.7144
51 | 102 | 135 | 7.7488
51 | 103 | 135 | 7.7832
51 | 104 | 135 | 7.8176
51 | 105 | 135 | 7.852
51 | 106 | 135 | 7.8864
51 | 107 | 135 | 7.9208
51 | 108 | 135 | 7.9552
51 | 109 | 135 | 7.9896
51 | 110 | 135 | 8.024
51 | 111 | 135 | 8.0584
51 | 112 | 135 | 8.0928
51 | 113 | 135 | 8.1272
51 | 114 | 135 | 8.1616
51 | 115 | 135 | 8.196
51 | 116 | 135 | 8.2304
51 | 117 | 135 | 8.2648
51 | 118 | 135 | 8.2992
51 | 119 | 135 | 8.3336
51 | 120 | 135 | 8.368
51 | 121 | 135 | 8.4024
51 | 122 | 135 | 8.4368
51 | 123 | 135 | 8.4712
51 | 124 | 135 | 8.5056
51 | 125 | 135 | 8.54
51 | 126 | 135 | 8.588
51 | 127 | 135 | 8.636
51 | 128 | 135 | 8.684
51 | 129 | 135 | 8.732
51 | 130 | 135 | 8.78
51 | 131 | 135 | 8.828
51 | 132 | 135 | 8.876
51 | 133 | 135 | 8.924
51 | 134 | 135 | 8.972
51 | 135 | 135 | 9.02
51 | 136 | 135 | 9.068
51 | 137 | 135 | 9.116
51 | 138 | 135 | 9.164
51 | 139 | 135 | 9.212
51 | 140 | 135 | 9.26
51 | 141 | 135 | 9.308
51 | 142 | 135 | 9.356
51 | 143 | 135 | 9.404
51 | 144 | 135 | 9.452
51 | 145 | 135 | 9.5
51 | 146 | 135 | 9.548
51 | 147 | 135 | 9.596
51 | 148 | 135 | 9.644
51 | 149 | 135 | 9.692
51 | 150 | 135 | 9.74
52 | 45 | 135 | 4.8
52 | 46 | 135 | 4.8764
52 | 47 | 135 | 4.9529
52 | 48 | 135 | 5.0293
52 | 49 | 135 | 5.1058
52 | 50 | 135 | 5.1822
52 | 51 | 135 | 5.2587
52 | 52 | 135 | 5.3351
52 | 53 | 135 | 5.4116
52 | 54 | 135 | 5.488
52 | 55 | 135 | 5.5644
52 | 56 | 135 | 5.6409
52 | 57 | 135 | 5.7173
52 | 58 | 135 | 5.7938
52 | 59 | 135 | 5.8702
52 | 60 | 135 | 5.9467
52 | 61 | 135 | 6.0231
52 | 62 | 135 | 6.0996
52 | 63 | 135 | 6.176
52 | 64 | 135 | 6.2524
52 | 65 | 135 | 6.3289
52 | 66 | 135 | 6.4053
52 | 67 | 135 | 6.4818
52 | 68 | 135 | 6.5582
52 | 69 | 135 | 6.6347
52 | 70 | 135 | 6.7111
52 | 71 | 135 | 6.7876
52 | 72 | 135 | 6.864
52 | 73 | 135 | 6.9404
52 | 74 | 135 | 7.0169
52 | 75 | 135 | 7.0933
52 | 76 | 135 | 7.1173
52 | 77 | 135 | 7.1413
52 | 78 | 135 | 7.1653
52 | 79 | 135 | 7.1893
52 | 80 | 135 | 7.2133
52 | 81 | 135 | 7.2373
52 | 82 | 135 | 7.2613
52 | 83 | 135 | 7.2853
52 | 84 | 135 | 7.3093
52 | 85 | 135 | 7.3333
52 | 86 | 135 | 7.3573
52 | 87 | 135 | 7.3813
52 | 88 | 135 | 7.4053
52 | 89 | 135 | 7.4293
52 | 90 | 135 | 7.4533
52 | 91 | 135 | 7.4773
52 | 92 | 135 | 7.5013
52 | 93 | 135 | 7.5253
52 | 94 | 135 | 7.5493
52 | 95 | 135 | 7.5733
52 | 96 | 135 | 7.5973
52 | 97 | 135 | 7.6213
52 | 98 | 135 | 7.6453
52 | 99 | 135 | 7.6693
52 | 100 | 135 | 7.6933
52 | 101 | 135 | 7.7275
52 | 102 | 135 | 7.7616
52 | 103 | 135 | 7.7957
52 | 104 | 135 | 7.8299
52 | 105 | 135 | 7.864
52 | 106 | 135 | 7.8981
52 | 107 | 135 | 7.9323
52 | 108 | 135 | 7.9664
52 | 109 | 135 | 8.0005
52 | 110 | 135 | 8.0347
52 | 111 | 135 | 8.0688
52 | 112 | 135 | 8.1029
52 | 113 | 135 | 8.1371
52 | 114 | 135 | 8.1712
52 | 115 | 135 | 8.2053
52 | 116 | 135 | 8.2395
52 | 117 | 135 | 8.2736
52 | 118 | 135 | 8.3077
52 | 119 | 135 | 8.3419
52 | 120 | 135 | 8.376
52 | 121 | 135 | 8.4101
52 | 122 | 135 | 8.4443
52 | 123 | 135 | 8.4784
52 | 124 | 135 | 8.5125
52 | 125 | 135 | 8.5467
52 | 126 | 135 | 8.5947
52 | 127 | 135 | 8.6427
52 | 128 | 135 | 8.6907
52 | 129 | 135 | 8.7387
52 | 130 | 135 | 8.7867
52 | 131 | 135 | 8.8347
52 | 132 | 135 | 8.8827
52 | 133 | 135 | 8.9307
52 | 134 | 135 | 8.9787
52 | 135 | 135 | 9.0267
52 | 136 | 135 | 9.0747
52 | 137 | 135 | 9.1227
52 | 138 | 135 | 9.1707
52 | 139 | 135 | 9.2187
52 | 140 | 135 | 9.2667
52 | 141 | 135 | 9.3147
52 | 142 | 135 | 9.3627
52 | 143 | 135 | 9.4107
52 | 144 | 135 | 9.4587
52 | 145 | 135 | 9.5067
52 | 146 | 135 | 9.5547
52 | 147 | 135 | 9.6027
52 | 148 | 135 | 9.6507
52 | 149 | 135 | 9.6987
52 | 150 | 135 | 9.7467
53 | 45 | 135 | 4.8
53 | 46 | 135 | 4.8769
53 | 47 | 135 | 4.9538
53 | 48 | 135 | 5.0307
53 | 49 | 135 | 5.1076
53 | 50 | 135 | 5.1844
53 | 51 | 135 | 5.2613
53 | 52 | 135 | 5.3382
53 | 53 | 135 | 5.4151
53 | 54 | 135 | 5.492
53 | 55 | 135 | 5.5689
53 | 56 | 135 | 5.6458
53 | 57 | 135 | 5.7227
53 | 58 | 135 | 5.7996
53 | 59 | 135 | 5.8764
53 | 60 | 135 | 5.9533
53 | 61 | 135 | 6.0302
53 | 62 | 135 | 6.1071
53 | 63 | 135 | 6.184
53 | 64 | 135 | 6.2609
53 | 65 | 135 | 6.3378
53 | 66 | 135 | 6.4147
53 | 67 | 135 | 6.4916
53 | 68 | 135 | 6.5684
53 | 69 | 135 | 6.6453
53 | 70 | 135 | 6.7222
53 | 71 | 135 | 6.7991
53 | 72 | 135 | 6.876
53 | 73 | 135 | 6.9529
53 | 74 | 135 | 7.0298
53 | 75 | 135 | 7.1067
53 | 76 | 135 | 7.1307
53 | 77 | 135 | 7.1547
53 | 78 | 135 | 7.1787
53 | 79 | 135 | 7.2027
53 | 80 | 135 | 7.2267
53 | 81 | 135 | 7.2507
53 | 82 | 135 | 7.2747
53 | 83 | 135 | 7.2987
53 | 84 | 135 | 7.3227
53 | 85 | 135 | 7.3467
53 | 86 | 135 | 7.3707
53 | 87 | 135 | 7.3947
53 | 88 | 135 | 7.4187
53 | 89 | 135 | 7.4427
53 | 90 | 135 | 7.4667
53 | 91 | 135 | 7.4907
53 | 92 | 135 | 7.5147
53 | 93 | 135 | 7.5387
53 | 94 | 135 | 7.5627
53 | 95 | 135 | 7.5867
53 | 96 | 135 | 7.6107
53 | 97 | 135 | 7.6347
53 | 98 | 135 | 7.6587
53 | 99 | 135 | 7.6827
53 | 100 | 135 | 7.7067
53 | 101 | 135 | 7.7405
53 | 102 | 135 | 7.7744
53 | 103 | 135 | 7.8083
53 | 104 | 135 | 7.8421
53 | 105 | 135 | 7.876
53 | 106 | 135 | 7.9099
53 | 107 | 135 | 7.9437
53 | 108 | 135 | 7.9776
53 | 109 | 135 | 8.0115
53 | 110 | 135 | 8.0453
53 | 111 | 135 | 8.0792
53 | 112 | 135 | 8.1131
53 | 113 | 135 | 8.1469
53 | 114 | 135 | 8.1808
53 | 115 | 135 | 8.2147
53 | 116 | 135 | 8.2485
53 | 117 | 135 | 8.2824
53 | 118 | 135 | 8.3163
53 | 119 | 135 | 8.3501
53 | 120 | 135 | 8.384
53 | 121 | 135 | 8.4179
53 | 122 | 135 | 8.4517
53 | 123 | 135 | 8.4856
53 | 124 | 135 | 8.5195
53 | 125 | 135 | 8.5533
53 | 126 | 135 | 8.6013
53 | 127 | 135 | 8.6493
53 | 128 | 135 | 8.6973
53 | 129 | 135 | 8.7453
53 | 130 | 135 | 8.7933
53 | 131 | 135 | 8.8413
53 | 132 | 135 | 8.8893
53 | 133 | 135 | 8.9373
53 | 134 | 135 | 8.9853
53 | 135 | 135 | 9.0333
53 | 136 | 135 | 9.0813
53 | 137 | 135 | 9.1293
53 | 138 | 135 | 9.1773
53 | 139 | 135 | 9.2253
53 | 140 | 135 | 9.2733
53 | 141 | 135 | 9.3213
53 | 142 | 135 | 9.3693
53 | 143 | 135 | 9.4173
53 | 144 | 135 | 9.4653
53 | 145 | 135 | 9.5133
53 | 146 | 135 | 9.5613
53 | 147 | 135 | 9.6093
53 | 148 | 135 | 9.6573
53 | 149 | 135 | 9.7053
53 | 150 | 135 | 9.7533
54 | 45 | 135 | 4.8
54 | 46 | 135 | 4.8773
54 | 47 | 135 | 4.9547
54 | 48 | 135 | 5.032
54 | 49 | 135 | 5.1093
54 | 50 | 135 | 5.1867
54 | 51 | 135 | 5.264
54 | 52 | 135 | 5.3413
54 | 53 | 135 | 5.4187
54 | 54 | 135 | 5.496
54 | 55 | 135 | 5.5733
54 | 56 | 135 | 5.6507
54 | 57 | 135 | 5.728
54 | 58 | 135 | 5.8053
54 | 59 | 135 | 5.8827
54 | 60 | 135 | 5.96
54 | 61 | 135 | 6.0373
54 | 62 | 135 | 6.1147
54 | 63 | 135 | 6.192
54 | 64 | 135 | 6.2693
54 | 65 | 135 | 6.3467
54 | 66 | 135 | 6.424
54 | 67 | 135 | 6.5013
54 | 68 | 135 | 6.5787
54 | 69 | 135 | 6.656
54 | 70 | 135 | 6.7333
54 | 71 | 135 | 6.8107
54 | 72 | 135 | 6.888
54 | 73 | 135 | 6.9653
54 | 74 | 135 | 7.0427
54 | 75 | 135 | 7.12
54 | 76 | 135 | 7.144
54 | 77 | 135 | 7.168
54 | 78 | 135 | 7.192
54 | 79 | 135 | 7.216
54 | 80 | 135 | 7.24
54 | 81 | 135 | 7.264
54 | 82 | 135 | 7.288
54 | 83 | 135 | 7.312
54 | 84 | 135 | 7.336
54 | 85 | 135 | 7.36
54 | 86 | 135 | 7.384
54 | 87 | 135 | 7.408
54 | 88 | 135 | 7.432
54 | 89 | 135 | 7.456
54 | 90 | 135 | 7.48
54 | 91 | 135 | 7.504
54 | 92 | 135 | 7.528
54 | 93 | 135 | 7.552
54 | 94 | 135 | 7.576
54 | 95 | 135 | 7.6
54 | 96 | 135 | 7.624
54 | 97 | 135 | 7.648
54 | 98 | 135 | 7.672
54 | 99 | 135 | 7.696
54 | 100 | 135 | 7.72
54 | 101 | 135 | 7.7536
54 | 102 | 135 | 7.7872
54 | 103 | 135 | 7.8208
54 | 104 | 135 | 7.8544
54 | 105 | 135 | 7.888
54 | 106 | 135 | 7.9216
54 | 107 | 135 | 7.9552
54 | 108 | 135 | 7.9888
54 | 109 | 135 | 8.0224
54 | 110 | 135 | 8.056
54 | 111 | 135 | 8.0896
54 | 112 | 135 | 8.1232
54 | 113 | 135 | 8.1568
54 | 114 | 135 | 8.1904
54 | 115 | 135 | 8.224
54 | 116 | 135 | 8.2576
54 | 117 | 135 | 8.2912
54 | 118 | 135 | 8.3248
54 | 119 | 135 | 8.3584
54 | 120 | 135 | 8.392
54 | 121 | 135 | 8.4256
54 | 122 | 135 | 8.4592
54 | 123 | 135 | 8.4928
54 | 124 | 135 | 8.5264
54 | 125 | 135 | 8.56
54 | 126 | 135 | 8.608
54 | 127 | 135 | 8.656
54 | 128 | 135 | 8.704
54 | 129 | 135 | 8.752
54 | 130 | 135 | 8.8
54 | 131 | 135 | 8.848
54 | 132 | 135 | 8.896
54 | 133 | 135 | 8.944
54 | 134 | 135 | 8.992
54 | 135 | 135 | 9.04
54 | 136 | 135 | 9.088
54 | 137 | 135 | 9.136
54 | 138 | 135 | 9.184
54 | 139 | 135 | 9.232
54 | 140 | 135 | 9.28
54 | 141 | 135 | 9.328
54 | 142 | 135 | 9.376
54 | 143 | 135 | 9.424
54 | 144 | 135 | 9.472
54 | 145 | 135 | 9.52
54 | 146 | 135 | 9.568
54 | 147 | 135 | 9.616
54 | 148 | 135 | 9.664
54 | 149 | 135 | 9.712
54 | 150 | 135 | 9.76
55 | 45 | 135 | 4.8
55 | 46 | 135 | 4.8778
55 | 47 | 135 | 4.9556
55 | 48 | 135 | 5.0333
55 | 49 | 135 | 5.1111
55 | 50 | 135 | 5.1889
55 | 51 | 135 | 5.2667
55 | 52 | 135 | 5.3444
55 | 53 | 135 | 5.4222
55 | 54 | 135 | 5.5
55 | 55 | 135 | 5.5778
55 | 56 | 135 | 5.6556
55 | 57 | 135 | 5.7333
55 | 58 | 135 | 5.8111
55 | 59 | 135 | 5.8889
55 | 60 | 135 | 5.9667
55 | 61 | 135 | 6.0444
55 | 62 | 135 | 6.1222
55 | 63 | 135 | 6.2
55 | 64 | 135 | 6.2778
55 | 65 | 135 | 6.3556
55 | 66 | 135 | 6.4333
55 | 67 | 135 | 6.5111
55 | 68 | 135 | 6.5889
55 | 69 | 135 | 6.6667
55 | 70 | 135 | 6.7444
55 | 71 | 135 | 6.8222
55 | 72 | 135 | 6.9
55 | 73 | 135 | 6.9778
55 | 74 | 135 | 7.0556
55 | 75 | 135 | 7.1333
55 | 76 | 135 | 7.1573
55 | 77 | 135 | 7.1813
55 | 78 | 135 | 7.2053
55 | 79 | 135 | 7.2293
55 | 80 | 135 | 7.2533
55 | 81 | 135 | 7.2773
55 | 82 | 135 | 7.3013
55 | 83 | 135 | 7.3253
55 | 84 | 135 | 7.3493
55 | 85 | 135 | 7.3733
55 | 86 | 135 | 7.3973
55 | 87 | 135 | 7.4213
55 | 88 | 135 | 7.4453
55 | 89 | 135 | 7.4693
55 | 90 | 135 | 7.4933
55 | 91 | 135 | 7.5173
55 | 92 | 135 | 7.5413
55 | 93 | 135 | 7.5653
55 | 94 | 135 | 7.5893
55 | 95 | 135 | 7.6133
55 | 96 | 135 | 7.6373
55 | 97 | 135 | 7.6613
55 | 98 | 135 | 7.6853
55 | 99 | 135 | 7.7093
55 | 100 | 135 | 7.7333
55 | 101 | 135 | 7.7667
55 | 102 | 135 | 7.8
55 | 103 | 135 | 7.8333
55 | 104 | 135 | 7.8667
55 | 105 | 135 | 7.9
55 | 106 | 135 | 7.9333
55 | 107 | 135 | 7.9667
55 | 108 | 135 | 8
55 | 109 | 135 | 8.0333
55 | 110 | 135 | 8.0667
55 | 111 | 135 | 8.1
55 | 112 | 135 | 8.1333
55 | 113 | 135 | 8.1667
55 | 114 | 135 | 8.2
55 | 115 | 135 | 8.2333
55 | 116 | 135 | 8.2667
55 | 117 | 135 | 8.3
55 | 118 | 135 | 8.3333
55 | 119 | 135 | 8.3667
55 | 120 | 135 | 8.4
55 | 121 | 135 | 8.4333
55 | 122 | 135 | 8.4667
55 | 123 | 135 | 8.5
55 | 124 | 135 | 8.5333
55 | 125 | 135 | 8.5667
55 | 126 | 135 | 8.6147
55 | 127 | 135 | 8.6627
55 | 128 | 135 | 8.7107
55 | 129 | 135 | 8.7587
55 | 130 | 135 | 8.8067
55 | 131 | 135 | 8.8547
55 | 132 | 135 | 8.9027
55 | 133 | 135 | 8.9507
55 | 134 | 135 | 8.9987
55 | 135 | 135 | 9.0467
55 | 136 | 135 | 9.0947
55 | 137 | 135 | 9.1427
55 | 138 | 135 | 9.1907
55 | 139 | 135 | 9.2387
55 | 140 | 135 | 9.2867
55 | 141 | 135 | 9.3347
55 | 142 | 135 | 9.3827
55 | 143 | 135 | 9.4307
55 | 144 | 135 | 9.4787
55 | 145 | 135 | 9.5267
55 | 146 | 135 | 9.5747
55 | 147 | 135 | 9.6227
55 | 148 | 135 | 9.6707
55 | 149 | 135 | 9.7187
55 | 150 | 135 | 9.7667
56 | 45 | 135 | 4.8
56 | 46 | 135 | 4.8782
56 | 47 | 135 | 4.9564
56 | 48 | 135 | 5.0347
56 | 49 | 135 | 5.1129
56 | 50 | 135 | 5.1911
56 | 51 | 135 | 5.2693
56 | 52 | 135 | 5.3476
56 | 53 | 135 | 5.4258
56 | 54 | 135 | 5.504
56 | 55 | 135 | 5.5822
56 | 56 | 135 | 5.6604
56 | 57 | 135 | 5.7387
56 | 58 | 135 | 5.8169
56 | 59 | 135 | 5.8951
56 | 60 | 135 | 5.9733
56 | 61 | 135 | 6.0516
56 | 62 | 135 | 6.1298
56 | 63 | 135 | 6.208
56 | 64 | 135 | 6.2862
56 | 65 | 135 | 6.3644
56 | 66 | 135 | 6.4427
56 | 67 | 135 | 6.5209
56 | 68 | 135 | 6.5991
56 | 69 | 135 | 6.6773
56 | 70 | 135 | 6.7556
56 | 71 | 135 | 6.8338
56 | 72 | 135 | 6.912
56 | 73 | 135 | 6.9902
56 | 74 | 135 | 7.0684
56 | 75 | 135 | 7.1467
56 | 76 | 135 | 7.1707
56 | 77 | 135 | 7.1947
56 | 78 | 135 | 7.2187
56 | 79 | 135 | 7.2427
56 | 80 | 135 | 7.2667
56 | 81 | 135 | 7.2907
56 | 82 | 135 | 7.3147
56 | 83 | 135 | 7.3387
56 | 84 | 135 | 7.3627
56 | 85 | 135 | 7.3867
56 | 86 | 135 | 7.4107
56 | 87 | 135 | 7.4347
56 | 88 | 135 | 7.4587
56 | 89 | 135 | 7.4827
56 | 90 | 135 | 7.5067
56 | 91 | 135 | 7.5307
56 | 92 | 135 | 7.5547
56 | 93 | 135 | 7.5787
56 | 94 | 135 | 7.6027
56 | 95 | 135 | 7.6267
56 | 96 | 135 | 7.6507
56 | 97 | 135 | 7.6747
56 | 98 | 135 | 7.6987
56 | 99 | 135 | 7.7227
56 | 100 | 135 | 7.7467
56 | 101 | 135 | 7.7797
56 | 102 | 135 | 7.8128
56 | 103 | 135 | 7.8459
56 | 104 | 135 | 7.8789
56 | 105 | 135 | 7.912
56 | 106 | 135 | 7.9451
56 | 107 | 135 | 7.9781
56 | 108 | 135 | 8.0112
56 | 109 | 135 | 8.0443
56 | 110 | 135 | 8.0773
56 | 111 | 135 | 8.1104
56 | 112 | 135 | 8.1435
56 | 113 | 135 | 8.1765
56 | 114 | 135 | 8.2096
56 | 115 | 135 | 8.2427
56 | 116 | 135 | 8.2757
56 | 117 | 135 | 8.3088
56 | 118 | 135 | 8.3419
56 | 119 | 135 | 8.3749
56 | 120 | 135 | 8.408
56 | 121 | 135 | 8.4411
56 | 122 | 135 | 8.4741
56 | 123 | 135 | 8.5072
56 | 124 | 135 | 8.5403
56 | 125 | 135 | 8.5733
56 | 126 | 135 | 8.6213
56 | 127 | 135 | 8.6693
56 | 128 | 135 | 8.7173
56 | 129 | 135 | 8.7653
56 | 130 | 135 | 8.8133
56 | 131 | 135 | 8.8613
56 | 132 | 135 | 8.9093
56 | 133 | 135 | 8.9573
56 | 134 | 135 | 9.0053
56 | 135 | 135 | 9.0533
56 | 136 | 135 | 9.1013
56 | 137 | 135 | 9.1493
56 | 138 | 135 | 9.1973
56 | 139 | 135 | 9.2453
56 | 140 | 135 | 9.2933
56 | 141 | 135 | 9.3413
56 | 142 | 135 | 9.3893
56 | 143 | 135 | 9.4373
56 | 144 | 135 | 9.4853
56 | 145 | 135 | 9.5333
56 | 146 | 135 | 9.5813
56 | 147 | 135 | 9.6293
56 | 148 | 135 | 9.6773
56 | 149 | 135 | 9.7253
56 | 150 | 135 | 9.7733
57 | 45 | 135 | 4.8
57 | 46 | 135 | 4.8787
57 | 47 | 135 | 4.9573
57 | 48 | 135 | 5.036
57 | 49 | 135 | 5.1147
57 | 50 | 135 | 5.1933
57 | 51 | 135 | 5.272
57 | 52 | 135 | 5.3507
57 | 53 | 135 | 5.4293
57 | 54 | 135 | 5.508
57 | 55 | 135 | 5.5867
57 | 56 | 135 | 5.6653
57 | 57 | 135 | 5.744
57 | 58 | 135 | 5.8227
57 | 59 | 135 | 5.9013
57 | 60 | 135 | 5.98
57 | 61 | 135 | 6.0587
57 | 62 | 135 | 6.1373
57 | 63 | 135 | 6.216
57 | 64 | 135 | 6.2947
57 | 65 | 135 | 6.3733
57 | 66 | 135 | 6.452
57 | 67 | 135 | 6.5307
57 | 68 | 135 | 6.6093
57 | 69 | 135 | 6.688
57 | 70 | 135 | 6.7667
57 | 71 | 135 | 6.8453
57 | 72 | 135 | 6.924
57 | 73 | 135 | 7.0027
57 | 74 | 135 | 7.0813
57 | 75 | 135 | 7.16
57 | 76 | 135 | 7.184
57 | 77 | 135 | 7.208
57 | 78 | 135 | 7.232
57 | 79 | 135 | 7.256
57 | 80 | 135 | 7.28
57 | 81 | 135 | 7.304
57 | 82 | 135 | 7.328
57 | 83 | 135 | 7.352
57 | 84 | 135 | 7.376
57 | 85 | 135 | 7.4
57 | 86 | 135 | 7.424
57 | 87 | 135 | 7.448
57 | 88 | 135 | 7.472
57 | 89 | 135 | 7.496
57 | 90 | 135 | 7.52
57 | 91 | 135 | 7.544
57 | 92 | 135 | 7.568
57 | 93 | 135 | 7.592
57 | 94 | 135 | 7.616
57 | 95 | 135 | 7.64
57 | 96 | 135 | 7.664
57 | 97 | 135 | 7.688
57 | 98 | 135 | 7.712
57 | 99 | 135 | 7.736
57 | 100 | 135 | 7.76
57 | 101 | 135 | 7.7928
57 | 102 | 135 | 7.8256
57 | 103 | 135 | 7.8584
57 | 104 | 135 | 7.8912
57 | 105 | 135 | 7.924
57 | 106 | 135 | 7.9568
57 | 107 | 135 | 7.9896
57 | 108 | 135 | 8.0224
57 | 109 | 135 | 8.0552
57 | 110 | 135 | 8.088
57 | 111 | 135 | 8.1208
57 | 112 | 135 | 8.1536
57 | 113 | 135 | 8.1864
57 | 114 | 135 | 8.2192
57 | 115 | 135 | 8.252
57 | 116 | 135 | 8.2848
57 | 117 | 135 | 8.3176
57 | 118 | 135 | 8.3504
57 | 119 | 135 | 8.3832
57 | 120 | 135 | 8.416
57 | 121 | 135 | 8.4488
57 | 122 | 135 | 8.4816
57 | 123 | 135 | 8.5144
57 | 124 | 135 | 8.5472
57 | 125 | 135 | 8.58
57 | 126 | 135 | 8.628
57 | 127 | 135 | 8.676
57 | 128 | 135 | 8.724
57 | 129 | 135 | 8.772
57 | 130 | 135 | 8.82
57 | 131 | 135 | 8.868
57 | 132 | 135 | 8.916
57 | 133 | 135 | 8.964
57 | 134 | 135 | 9.012
57 | 135 | 135 | 9.06
57 | 136 | 135 | 9.108
57 | 137 | 135 | 9.156
57 | 138 | 135 | 9.204
57 | 139 | 135 | 9.252
57 | 140 | 135 | 9.3
57 | 141 | 135 | 9.348
57 | 142 | 135 | 9.396
57 | 143 | 135 | 9.444
57 | 144 | 135 | 9.492
57 | 145 | 135 | 9.54
57 | 146 | 135 | 9.588
57 | 147 | 135 | 9.636
57 | 148 | 135 | 9.684
57 | 149 | 135 | 9.732
57 | 150 | 135 | 9.78
58 | 45 | 135 | 4.8
58 | 46 | 135 | 4.8791
58 | 47 | 135 | 4.9582
58 | 48 | 135 | 5.0373
58 | 49 | 135 | 5.1164
58 | 50 | 135 | 5.1956
58 | 51 | 135 | 5.2747
58 | 52 | 135 | 5.3538
58 | 53 | 135 | 5.4329
58 | 54 | 135 | 5.512
58 | 55 | 135 | 5.5911
58 | 56 | 135 | 5.6702
58 | 57 | 135 | 5.7493
58 | 58 | 135 | 5.8284
58 | 59 | 135 | 5.9076
58 | 60 | 135 | 5.9867
58 | 61 | 135 | 6.0658
58 | 62 | 135 | 6.1449
58 | 63 | 135 | 6.224
58 | 64 | 135 | 6.3031
58 | 65 | 135 | 6.3822
58 | 66 | 135 | 6.4613
58 | 67 | 135 | 6.5404
58 | 68 | 135 | 6.6196
58 | 69 | 135 | 6.6987
58 | 70 | 135 | 6.7778
58 | 71 | 135 | 6.8569
58 | 72 | 135 | 6.936
58 | 73 | 135 | 7.0151
58 | 74 | 135 | 7.0942
58 | 75 | 135 | 7.1733
58 | 76 | 135 | 7.1973
58 | 77 | 135 | 7.2213
58 | 78 | 135 | 7.2453
58 | 79 | 135 | 7.2693
58 | 80 | 135 | 7.2933
58 | 81 | 135 | 7.3173
58 | 82 | 135 | 7.3413
58 | 83 | 135 | 7.3653
58 | 84 | 135 | 7.3893
58 | 85 | 135 | 7.4133
58 | 86 | 135 | 7.4373
58 | 87 | 135 | 7.4613
58 | 88 | 135 | 7.4853
58 | 89 | 135 | 7.5093
58 | 90 | 135 | 7.5333
58 | 91 | 135 | 7.5573
58 | 92 | 135 | 7.5813
58 | 93 | 135 | 7.6053
58 | 94 | 135 | 7.6293
58 | 95 | 135 | 7.6533
58 | 96 | 135 | 7.6773
58 | 97 | 135 | 7.7013
58 | 98 | 135 | 7.7253
58 | 99 | 135 | 7.7493
58 | 100 | 135 | 7.7733
58 | 101 | 135 | 7.8059
58 | 102 | 135 | 7.8384
58 | 103 | 135 | 7.8709
58 | 104 | 135 | 7.9035
58 | 105 | 135 | 7.936
58 | 106 | 135 | 7.9685
58 | 107 | 135 | 8.0011
58 | 108 | 135 | 8.0336
58 | 109 | 135 | 8.0661
58 | 110 | 135 | 8.0987
58 | 111 | 135 | 8.1312
58 | 112 | 135 | 8.1637
58 | 113 | 135 | 8.1963
58 | 114 | 135 | 8.2288
58 | 115 | 135 | 8.2613
58 | 116 | 135 | 8.2939
58 | 117 | 135 | 8.3264
58 | 118 | 135 | 8.3589
58 | 119 | 135 | 8.3915
58 | 120 | 135 | 8.424
58 | 121 | 135 | 8.4565
58 | 122 | 135 | 8.4891
58 | 123 | 135 | 8.5216
58 | 124 | 135 | 8.5541
58 | 125 | 135 | 8.5867
58 | 126 | 135 | 8.6347
58 | 127 | 135 | 8.6827
58 | 128 | 135 | 8.7307
58 | 129 | 135 | 8.7787
58 | 130 | 135 | 8.8267
58 | 131 | 135 | 8.8747
58 | 132 | 135 | 8.9227
58 | 133 | 135 | 8.9707
58 | 134 | 135 | 9.0187
58 | 135 | 135 | 9.0667
58 | 136 | 135 | 9.1147
58 | 137 | 135 | 9.1627
58 | 138 | 135 | 9.2107
58 | 139 | 135 | 9.2587
58 | 140 | 135 | 9.3067
58 | 141 | 135 | 9.3547
58 | 142 | 135 | 9.4027
58 | 143 | 135 | 9.4507
58 | 144 | 135 | 9.4987
58 | 145 | 135 | 9.5467
58 | 146 | 135 | 9.5947
58 | 147 | 135 | 9.6427
58 | 148 | 135 | 9.6907
58 | 149 | 135 | 9.7387
58 | 150 | 135 | 9.7867
59 | 45 | 135 | 4.8
59 | 46 | 135 | 4.8796
59 | 47 | 135 | 4.9591
59 | 48 | 135 | 5.0387
59 | 49 | 135 | 5.1182
59 | 50 | 135 | 5.1978
59 | 51 | 135 | 5.2773
59 | 52 | 135 | 5.3569
59 | 53 | 135 | 5.4364
59 | 54 | 135 | 5.516
59 | 55 | 135 | 5.5956
59 | 56 | 135 | 5.6751
59 | 57 | 135 | 5.7547
59 | 58 | 135 | 5.8342
59 | 59 | 135 | 5.9138
59 | 60 | 135 | 5.9933
59 | 61 | 135 | 6.0729
59 | 62 | 135 | 6.1524
59 | 63 | 135 | 6.232
59 | 64 | 135 | 6.3116
59 | 65 | 135 | 6.3911
59 | 66 | 135 | 6.4707
59 | 67 | 135 | 6.5502
59 | 68 | 135 | 6.6298
59 | 69 | 135 | 6.7093
59 | 70 | 135 | 6.7889
59 | 71 | 135 | 6.8684
59 | 72 | 135 | 6.948
59 | 73 | 135 | 7.0276
59 | 74 | 135 | 7.1071
59 | 75 | 135 | 7.1867
59 | 76 | 135 | 7.2107
59 | 77 | 135 | 7.2347
59 | 78 | 135 | 7.2587
59 | 79 | 135 | 7.2827
59 | 80 | 135 | 7.3067
59 | 81 | 135 | 7.3307
59 | 82 | 135 | 7.3547
59 | 83 | 135 | 7.3787
59 | 84 | 135 | 7.4027
59 | 85 | 135 | 7.4267
59 | 86 | 135 | 7.4507
59 | 87 | 135 | 7.4747
59 | 88 | 135 | 7.4987
59 | 89 | 135 | 7.5227
59 | 90 | 135 | 7.5467
59 | 91 | 135 | 7.5707
59 | 92 | 135 | 7.5947
59 | 93 | 135 | 7.6187
59 | 94 | 135 | 7.6427
59 | 95 | 135 | 7.6667
59 | 96 | 135 | 7.6907
59 | 97 | 135 | 7.7147
59 | 98 | 135 | 7.7387
59 | 99 | 135 | 7.7627
59 | 100 | 135 | 7.7867
59 | 101 | 135 | 7.8189
59 | 102 | 135 | 7.8512
59 | 103 | 135 | 7.8835
59 | 104 | 135 | 7.9157
59 | 105 | 135 | 7.948
59 | 106 | 135 | 7.9803
59 | 107 | 135 | 8.0125
59 | 108 | 135 | 8.0448
59 | 109 | 135 | 8.0771
59 | 110 | 135 | 8.1093
59 | 111 | 135 | 8.1416
59 | 112 | 135 | 8.1739
59 | 113 | 135 | 8.2061
59 | 114 | 135 | 8.2384
59 | 115 | 135 | 8.2707
59 | 116 | 135 | 8.3029
59 | 117 | 135 | 8.3352
59 | 118 | 135 | 8.3675
59 | 119 | 135 | 8.3997
59 | 120 | 135 | 8.432
59 | 121 | 135 | 8.4643
59 | 122 | 135 | 8.4965
59 | 123 | 135 | 8.5288
59 | 124 | 135 | 8.5611
59 | 125 | 135 | 8.5933
59 | 126 | 135 | 8.6413
59 | 127 | 135 | 8.6893
59 | 128 | 135 | 8.7373
59 | 129 | 135 | 8.7853
59 | 130 | 135 | 8.8333
59 | 131 | 135 | 8.8813
59 | 132 | 135 | 8.9293
59 | 133 | 135 | 8.9773
59 | 134 | 135 | 9.0253
59 | 135 | 135 | 9.0733
59 | 136 | 135 | 9.1213
59 | 137 | 135 | 9.1693
59 | 138 | 135 | 9.2173
59 | 139 | 135 | 9.2653
59 | 140 | 135 | 9.3133
59 | 141 | 135 | 9.3613
59 | 142 | 135 | 9.4093
59 | 143 | 135 | 9.4573
59 | 144 | 135 | 9.5053
59 | 145 | 135 | 9.5533
59 | 146 | 135 | 9.6013
59 | 147 | 135 | 9.6493
59 | 148 | 135 | 9.6973
59 | 149 | 135 | 9.7453
59 | 150 | 135 | 9.7933
60 | 45 | 135 | 4.8
60 | 46 | 135 | 4.88
60 | 47 | 135 | 4.96
60 | 48 | 135 | 5.04
60 | 49 | 135 | 5.12
60 | 50 | 135 | 5.2
60 | 51 | 135 | 5.28
60 | 52 | 135 | 5.36
60 | 53 | 135 | 5.44
60 | 54 | 135 | 5.52
60 | 55 | 135 | 5.6
60 | 56 | 135 | 5.68
60 | 57 | 135 | 5.76
60 | 58 | 135 | 5.84
60 | 59 | 135 | 5.92
60 | 60 | 135 | 6
60 | 61 | 135 | 6.08
60 | 62 | 135 | 6.16
60 | 63 | 135 | 6.24
60 | 64 | 135 | 6.32
60 | 65 | 135 | 6.4
60 | 66 | 135 | 6.48
60 | 67 | 135 | 6.56
60 | 68 | 135 | 6.64
60 | 69 | 135 | 6.72
60 | 70 | 135 | 6.8
60 | 71 | 135 | 6.88
60 | 72 | 135 | 6.96
60 | 73 | 135 | 7.04
60 | 74 | 135 | 7.12
60 | 75 | 135 | 7.2
60 | 76 | 135 | 7.224
60 | 77 | 135 | 7.248
60 | 78 | 135 | 7.272
60 | 79 | 135 | 7.296
60 | 80 | 135 | 7.32
60 | 81 | 135 | 7.344
60 | 82 | 135 | 7.368
60 | 83 | 135 | 7.392
60 | 84 | 135 | 7.416
60 | 85 | 135 | 7.44
60 | 86 | 135 | 7.464
60 | 87 | 135 | 7.488
60 | 88 | 135 | 7.512
60 | 89 | 135 | 7.536
60 | 90 | 135 | 7.56
60 | 91 | 135 | 7.584
60 | 92 | 135 | 7.608
60 | 93 | 135 | 7.632
60 | 94 | 135 | 7.656
60 | 95 | 135 | 7.68
60 | 96 | 135 | 7.704
60 | 97 | 135 | 7.728
60 | 98 | 135 | 7.752
60 | 99 | 135 | 7.776
60 | 100 | 135 | 7.8
60 | 101 | 135 | 7.832
60 | 102 | 135 | 7.864
60 | 103 | 135 | 7.896
60 | 104 | 135 | 7.928
60 | 105 | 135 | 7.96
60 | 106 | 135 | 7.992
60 | 107 | 135 | 8.024
60 | 108 | 135 | 8.056
60 | 109 | 135 | 8.088
60 | 110 | 135 | 8.12
60 | 111 | 135 | 8.152
60 | 112 | 135 | 8.184
60 | 113 | 135 | 8.216
60 | 114 | 135 | 8.248
60 | 115 | 135 | 8.28
60 | 116 | 135 | 8.312
60 | 117 | 135 | 8.344
60 | 118 | 135 | 8.376
60 | 119 | 135 | 8.408
60 | 120 | 135 | 8.44
60 | 121 | 135 | 8.472
60 | 122 | 135 | 8.504
60 | 123 | 135 | 8.536
60 | 124 | 135 | 8.568
60 | 125 | 135 | 8.6
60 | 126 | 135 | 8.648
60 | 127 | 135 | 8.696
60 | 128 | 135 | 8.744
60 | 129 | 135 | 8.792
60 | 130 | 135 | 8.84
60 | 131 | 135 | 8.888
60 | 132 | 135 | 8.936
60 | 133 | 135 | 8.984
60 | 134 | 135 | 9.032
60 | 135 | 135 | 9.08
60 | 136 | 135 | 9.128
60 | 137 | 135 | 9.176
60 | 138 | 135 | 9.224
60 | 139 | 135 | 9.272
60 | 140 | 135 | 9.32
60 | 141 | 135 | 9.368
60 | 142 | 135 | 9.416
60 | 143 | 135 | 9.464
60 | 144 | 135 | 9.512
60 | 145 | 135 | 9.56
60 | 146 | 135 | 9.608
60 | 147 | 135 | 9.656
60 | 148 | 135 | 9.704
60 | 149 | 135 | 9.752
60 | 150 | 135 | 9.8
61 | 45 | 135 | 4.8067
61 | 46 | 135 | 4.8867
61 | 47 | 135 | 4.9667
61 | 48 | 135 | 5.0467
61 | 49 | 135 | 5.1267
61 | 50 | 135 | 5.2067
61 | 51 | 135 | 5.2867
61 | 52 | 135 | 5.3667
61 | 53 | 135 | 5.4467
61 | 54 | 135 | 5.5267
61 | 55 | 135 | 5.6067
61 | 56 | 135 | 5.6867
61 | 57 | 135 | 5.7667
61 | 58 | 135 | 5.8467
61 | 59 | 135 | 5.9267
61 | 60 | 135 | 6.0067
61 | 61 | 135 | 6.0867
61 | 62 | 135 | 6.1667
61 | 63 | 135 | 6.2467
61 | 64 | 135 | 6.3267
61 | 65 | 135 | 6.4067
61 | 66 | 135 | 6.4867
61 | 67 | 135 | 6.5667
61 | 68 | 135 | 6.6467
61 | 69 | 135 | 6.7267
61 | 70 | 135 | 6.8067
61 | 71 | 135 | 6.8867
61 | 72 | 135 | 6.9667
61 | 73 | 135 | 7.0467
61 | 74 | 135 | 7.1267
61 | 75 | 135 | 7.2067
61 | 76 | 135 | 7.2309
61 | 77 | 135 | 7.2552
61 | 78 | 135 | 7.2795
61 | 79 | 135 | 7.3037
61 | 80 | 135 | 7.328
61 | 81 | 135 | 7.3523
61 | 82 | 135 | 7.3765
61 | 83 | 135 | 7.4008
61 | 84 | 135 | 7.4251
61 | 85 | 135 | 7.4493
61 | 86 | 135 | 7.4736
61 | 87 | 135 | 7.4979
61 | 88 | 135 | 7.5221
61 | 89 | 135 | 7.5464
61 | 90 | 135 | 7.5707
61 | 91 | 135 | 7.5949
61 | 92 | 135 | 7.6192
61 | 93 | 135 | 7.6435
61 | 94 | 135 | 7.6677
61 | 95 | 135 | 7.692
61 | 96 | 135 | 7.7163
61 | 97 | 135 | 7.7405
61 | 98 | 135 | 7.7648
61 | 99 | 135 | 7.7891
61 | 100 | 135 | 7.8133
61 | 101 | 135 | 7.8456
61 | 102 | 135 | 7.8779
61 | 103 | 135 | 7.9101
61 | 104 | 135 | 7.9424
61 | 105 | 135 | 7.9747
61 | 106 | 135 | 8.0069
61 | 107 | 135 | 8.0392
61 | 108 | 135 | 8.0715
61 | 109 | 135 | 8.1037
61 | 110 | 135 | 8.136
61 | 111 | 135 | 8.1683
61 | 112 | 135 | 8.2005
61 | 113 | 135 | 8.2328
61 | 114 | 135 | 8.2651
61 | 115 | 135 | 8.2973
61 | 116 | 135 | 8.3296
61 | 117 | 135 | 8.3619
61 | 118 | 135 | 8.3941
61 | 119 | 135 | 8.4264
61 | 120 | 135 | 8.4587
61 | 121 | 135 | 8.4909
61 | 122 | 135 | 8.5232
61 | 123 | 135 | 8.5555
61 | 124 | 135 | 8.5877
61 | 125 | 135 | 8.62
61 | 126 | 135 | 8.668
61 | 127 | 135 | 8.716
61 | 128 | 135 | 8.764
61 | 129 | 135 | 8.812
61 | 130 | 135 | 8.86
61 | 131 | 135 | 8.908
61 | 132 | 135 | 8.956
61 | 133 | 135 | 9.004
61 | 134 | 135 | 9.052
61 | 135 | 135 | 9.1
61 | 136 | 135 | 9.148
61 | 137 | 135 | 9.196
61 | 138 | 135 | 9.244
61 | 139 | 135 | 9.292
61 | 140 | 135 | 9.34
61 | 141 | 135 | 9.388
61 | 142 | 135 | 9.436
61 | 143 | 135 | 9.484
61 | 144 | 135 | 9.532
61 | 145 | 135 | 9.58
61 | 146 | 135 | 9.628
61 | 147 | 135 | 9.676
61 | 148 | 135 | 9.724
61 | 149 | 135 | 9.772
61 | 150 | 135 | 9.82
62 | 45 | 135 | 4.8133
62 | 46 | 135 | 4.8933
62 | 47 | 135 | 4.9733
62 | 48 | 135 | 5.0533
62 | 49 | 135 | 5.1333
62 | 50 | 135 | 5.2133
62 | 51 | 135 | 5.2933
62 | 52 | 135 | 5.3733
62 | 53 | 135 | 5.4533
62 | 54 | 135 | 5.5333
62 | 55 | 135 | 5.6133
62 | 56 | 135 | 5.6933
62 | 57 | 135 | 5.7733
62 | 58 | 135 | 5.8533
62 | 59 | 135 | 5.9333
62 | 60 | 135 | 6.0133
62 | 61 | 135 | 6.0933
62 | 62 | 135 | 6.1733
62 | 63 | 135 | 6.2533
62 | 64 | 135 | 6.3333
62 | 65 | 135 | 6.4133
62 | 66 | 135 | 6.4933
62 | 67 | 135 | 6.5733
62 | 68 | 135 | 6.6533
62 | 69 | 135 | 6.7333
62 | 70 | 135 | 6.8133
62 | 71 | 135 | 6.8933
62 | 72 | 135 | 6.9733
62 | 73 | 135 | 7.0533
62 | 74 | 135 | 7.1333
62 | 75 | 135 | 7.2133
62 | 76 | 135 | 7.2379
62 | 77 | 135 | 7.2624
62 | 78 | 135 | 7.2869
62 | 79 | 135 | 7.3115
62 | 80 | 135 | 7.336
62 | 81 | 135 | 7.3605
62 | 82 | 135 | 7.3851
62 | 83 | 135 | 7.4096
62 | 84 | 135 | 7.4341
62 | 85 | 135 | 7.4587
62 | 86 | 135 | 7.4832
62 | 87 | 135 | 7.5077
62 | 88 | 135 | 7.5323
62 | 89 | 135 | 7.5568
62 | 90 | 135 | 7.5813
62 | 91 | 135 | 7.6059
62 | 92 | 135 | 7.6304
62 | 93 | 135 | 7.6549
62 | 94 | 135 | 7.6795
62 | 95 | 135 | 7.704
62 | 96 | 135 | 7.7285
62 | 97 | 135 | 7.7531
62 | 98 | 135 | 7.7776
62 | 99 | 135 | 7.8021
62 | 100 | 135 | 7.8267
62 | 101 | 135 | 7.8592
62 | 102 | 135 | 7.8917
62 | 103 | 135 | 7.9243
62 | 104 | 135 | 7.9568
62 | 105 | 135 | 7.9893
62 | 106 | 135 | 8.0219
62 | 107 | 135 | 8.0544
62 | 108 | 135 | 8.0869
62 | 109 | 135 | 8.1195
62 | 110 | 135 | 8.152
62 | 111 | 135 | 8.1845
62 | 112 | 135 | 8.2171
62 | 113 | 135 | 8.2496
62 | 114 | 135 | 8.2821
62 | 115 | 135 | 8.3147
62 | 116 | 135 | 8.3472
62 | 117 | 135 | 8.3797
62 | 118 | 135 | 8.4123
62 | 119 | 135 | 8.4448
62 | 120 | 135 | 8.4773
62 | 121 | 135 | 8.5099
62 | 122 | 135 | 8.5424
62 | 123 | 135 | 8.5749
62 | 124 | 135 | 8.6075
62 | 125 | 135 | 8.64
62 | 126 | 135 | 8.688
62 | 127 | 135 | 8.736
62 | 128 | 135 | 8.784
62 | 129 | 135 | 8.832
62 | 130 | 135 | 8.88
62 | 131 | 135 | 8.928
62 | 132 | 135 | 8.976
62 | 133 | 135 | 9.024
62 | 134 | 135 | 9.072
62 | 135 | 135 | 9.12
62 | 136 | 135 | 9.168
62 | 137 | 135 | 9.216
62 | 138 | 135 | 9.264
62 | 139 | 135 | 9.312
62 | 140 | 135 | 9.36
62 | 141 | 135 | 9.408
62 | 142 | 135 | 9.456
62 | 143 | 135 | 9.504
62 | 144 | 135 | 9.552
62 | 145 | 135 | 9.6
62 | 146 | 135 | 9.648
62 | 147 | 135 | 9.696
62 | 148 | 135 | 9.744
62 | 149 | 135 | 9.792
62 | 150 | 135 | 9.84
63 | 45 | 135 | 4.82
63 | 46 | 135 | 4.9
63 | 47 | 135 | 4.98
63 | 48 | 135 | 5.06
63 | 49 | 135 | 5.14
63 | 50 | 135 | 5.22
63 | 51 | 135 | 5.3
63 | 52 | 135 | 5.38
63 | 53 | 135 | 5.46
63 | 54 | 135 | 5.54
63 | 55 | 135 | 5.62
63 | 56 | 135 | 5.7
63 | 57 | 135 | 5.78
63 | 58 | 135 | 5.86
63 | 59 | 135 | 5.94
63 | 60 | 135 | 6.02
63 | 61 | 135 | 6.1
63 | 62 | 135 | 6.18
63 | 63 | 135 | 6.26
63 | 64 | 135 | 6.34
63 | 65 | 135 | 6.42
63 | 66 | 135 | 6.5
63 | 67 | 135 | 6.58
63 | 68 | 135 | 6.66
63 | 69 | 135 | 6.74
63 | 70 | 135 | 6.82
63 | 71 | 135 | 6.9
63 | 72 | 135 | 6.98
63 | 73 | 135 | 7.06
63 | 74 | 135 | 7.14
63 | 75 | 135 | 7.22
63 | 76 | 135 | 7.2448
63 | 77 | 135 | 7.2696
63 | 78 | 135 | 7.2944
63 | 79 | 135 | 7.3192
63 | 80 | 135 | 7.344
63 | 81 | 135 | 7.3688
63 | 82 | 135 | 7.3936
63 | 83 | 135 | 7.4184
63 | 84 | 135 | 7.4432
63 | 85 | 135 | 7.468
63 | 86 | 135 | 7.4928
63 | 87 | 135 | 7.5176
63 | 88 | 135 | 7.5424
63 | 89 | 135 | 7.5672
63 | 90 | 135 | 7.592
63 | 91 | 135 | 7.6168
63 | 92 | 135 | 7.6416
63 | 93 | 135 | 7.6664
63 | 94 | 135 | 7.6912
63 | 95 | 135 | 7.716
63 | 96 | 135 | 7.7408
63 | 97 | 135 | 7.7656
63 | 98 | 135 | 7.7904
63 | 99 | 135 | 7.8152
63 | 100 | 135 | 7.84
63 | 101 | 135 | 7.8728
63 | 102 | 135 | 7.9056
63 | 103 | 135 | 7.9384
63 | 104 | 135 | 7.9712
63 | 105 | 135 | 8.004
63 | 106 | 135 | 8.0368
63 | 107 | 135 | 8.0696
63 | 108 | 135 | 8.1024
63 | 109 | 135 | 8.1352
63 | 110 | 135 | 8.168
63 | 111 | 135 | 8.2008
63 | 112 | 135 | 8.2336
63 | 113 | 135 | 8.2664
63 | 114 | 135 | 8.2992
63 | 115 | 135 | 8.332
63 | 116 | 135 | 8.3648
63 | 117 | 135 | 8.3976
63 | 118 | 135 | 8.4304
63 | 119 | 135 | 8.4632
63 | 120 | 135 | 8.496
63 | 121 | 135 | 8.5288
63 | 122 | 135 | 8.5616
63 | 123 | 135 | 8.5944
63 | 124 | 135 | 8.6272
63 | 125 | 135 | 8.66
63 | 126 | 135 | 8.708
63 | 127 | 135 | 8.756
63 | 128 | 135 | 8.804
63 | 129 | 135 | 8.852
63 | 130 | 135 | 8.9
63 | 131 | 135 | 8.948
63 | 132 | 135 | 8.996
63 | 133 | 135 | 9.044
63 | 134 | 135 | 9.092
63 | 135 | 135 | 9.14
63 | 136 | 135 | 9.188
63 | 137 | 135 | 9.236
63 | 138 | 135 | 9.284
63 | 139 | 135 | 9.332
63 | 140 | 135 | 9.38
63 | 141 | 135 | 9.428
63 | 142 | 135 | 9.476
63 | 143 | 135 | 9.524
63 | 144 | 135 | 9.572
63 | 145 | 135 | 9.62
63 | 146 | 135 | 9.668
63 | 147 | 135 | 9.716
63 | 148 | 135 | 9.764
63 | 149 | 135 | 9.812
63 | 150 | 135 | 9.86
64 | 45 | 135 | 4.8267
64 | 46 | 135 | 4.9067
64 | 47 | 135 | 4.9867
64 | 48 | 135 | 5.0667
64 | 49 | 135 | 5.1467
64 | 50 | 135 | 5.2267
64 | 51 | 135 | 5.3067
64 | 52 | 135 | 5.3867
64 | 53 | 135 | 5.4667
64 | 54 | 135 | 5.5467
64 | 55 | 135 | 5.6267
64 | 56 | 135 | 5.7067
64 | 57 | 135 | 5.7867
64 | 58 | 135 | 5.8667
64 | 59 | 135 | 5.9467
64 | 60 | 135 | 6.0267
64 | 61 | 135 | 6.1067
64 | 62 | 135 | 6.1867
64 | 63 | 135 | 6.2667
64 | 64 | 135 | 6.3467
64 | 65 | 135 | 6.4267
64 | 66 | 135 | 6.5067
64 | 67 | 135 | 6.5867
64 | 68 | 135 | 6.6667
64 | 69 | 135 | 6.7467
64 | 70 | 135 | 6.8267
64 | 71 | 135 | 6.9067
64 | 72 | 135 | 6.9867
64 | 73 | 135 | 7.0667
64 | 74 | 135 | 7.1467
64 | 75 | 135 | 7.2267
64 | 76 | 135 | 7.2517
64 | 77 | 135 | 7.2768
64 | 78 | 135 | 7.3019
64 | 79 | 135 | 7.3269
64 | 80 | 135 | 7.352
64 | 81 | 135 | 7.3771
64 | 82 | 135 | 7.4021
64 | 83 | 135 | 7.4272
64 | 84 | 135 | 7.4523
64 | 85 | 135 | 7.4773
64 | 86 | 135 | 7.5024
64 | 87 | 135 | 7.5275
64 | 88 | 135 | 7.5525
64 | 89 | 135 | 7.5776
64 | 90 | 135 | 7.6027
64 | 91 | 135 | 7.6277
64 | 92 | 135 | 7.6528
64 | 93 | 135 | 7.6779
64 | 94 | 135 | 7.7029
64 | 95 | 135 | 7.728
64 | 96 | 135 | 7.7531
64 | 97 | 135 | 7.7781
64 | 98 | 135 | 7.8032
64 | 99 | 135 | 7.8283
64 | 100 | 135 | 7.8533
64 | 101 | 135 | 7.8864
64 | 102 | 135 | 7.9195
64 | 103 | 135 | 7.9525
64 | 104 | 135 | 7.9856
64 | 105 | 135 | 8.0187
64 | 106 | 135 | 8.0517
64 | 107 | 135 | 8.0848
64 | 108 | 135 | 8.1179
64 | 109 | 135 | 8.1509
64 | 110 | 135 | 8.184
64 | 111 | 135 | 8.2171
64 | 112 | 135 | 8.2501
64 | 113 | 135 | 8.2832
64 | 114 | 135 | 8.3163
64 | 115 | 135 | 8.3493
64 | 116 | 135 | 8.3824
64 | 117 | 135 | 8.4155
64 | 118 | 135 | 8.4485
64 | 119 | 135 | 8.4816
64 | 120 | 135 | 8.5147
64 | 121 | 135 | 8.5477
64 | 122 | 135 | 8.5808
64 | 123 | 135 | 8.6139
64 | 124 | 135 | 8.6469
64 | 125 | 135 | 8.68
64 | 126 | 135 | 8.728
64 | 127 | 135 | 8.776
64 | 128 | 135 | 8.824
64 | 129 | 135 | 8.872
64 | 130 | 135 | 8.92
64 | 131 | 135 | 8.968
64 | 132 | 135 | 9.016
64 | 133 | 135 | 9.064
64 | 134 | 135 | 9.112
64 | 135 | 135 | 9.16
64 | 136 | 135 | 9.208
64 | 137 | 135 | 9.256
64 | 138 | 135 | 9.304
64 | 139 | 135 | 9.352
64 | 140 | 135 | 9.4
64 | 141 | 135 | 9.448
64 | 142 | 135 | 9.496
64 | 143 | 135 | 9.544
64 | 144 | 135 | 9.592
64 | 145 | 135 | 9.64
64 | 146 | 135 | 9.688
64 | 147 | 135 | 9.736
64 | 148 | 135 | 9.784
64 | 149 | 135 | 9.832
64 | 150 | 135 | 9.88
65 | 45 | 135 | 4.8333
65 | 46 | 135 | 4.9133
65 | 47 | 135 | 4.9933
65 | 48 | 135 | 5.0733
65 | 49 | 135 | 5.1533
65 | 50 | 135 | 5.2333
65 | 51 | 135 | 5.3133
65 | 52 | 135 | 5.3933
65 | 53 | 135 | 5.4733
65 | 54 | 135 | 5.5533
65 | 55 | 135 | 5.6333
65 | 56 | 135 | 5.7133
65 | 57 | 135 | 5.7933
65 | 58 | 135 | 5.8733
65 | 59 | 135 | 5.9533
65 | 60 | 135 | 6.0333
65 | 61 | 135 | 6.1133
65 | 62 | 135 | 6.1933
65 | 63 | 135 | 6.2733
65 | 64 | 135 | 6.3533
65 | 65 | 135 | 6.4333
65 | 66 | 135 | 6.5133
65 | 67 | 135 | 6.5933
65 | 68 | 135 | 6.6733
65 | 69 | 135 | 6.7533
65 | 70 | 135 | 6.8333
65 | 71 | 135 | 6.9133
65 | 72 | 135 | 6.9933
65 | 73 | 135 | 7.0733
65 | 74 | 135 | 7.1533
65 | 75 | 135 | 7.2333
65 | 76 | 135 | 7.2587
65 | 77 | 135 | 7.284
65 | 78 | 135 | 7.3093
65 | 79 | 135 | 7.3347
65 | 80 | 135 | 7.36
65 | 81 | 135 | 7.3853
65 | 82 | 135 | 7.4107
65 | 83 | 135 | 7.436
65 | 84 | 135 | 7.4613
65 | 85 | 135 | 7.4867
65 | 86 | 135 | 7.512
65 | 87 | 135 | 7.5373
65 | 88 | 135 | 7.5627
65 | 89 | 135 | 7.588
65 | 90 | 135 | 7.6133
65 | 91 | 135 | 7.6387
65 | 92 | 135 | 7.664
65 | 93 | 135 | 7.6893
65 | 94 | 135 | 7.7147
65 | 95 | 135 | 7.74
65 | 96 | 135 | 7.7653
65 | 97 | 135 | 7.7907
65 | 98 | 135 | 7.816
65 | 99 | 135 | 7.8413
65 | 100 | 135 | 7.8667
65 | 101 | 135 | 7.9
65 | 102 | 135 | 7.9333
65 | 103 | 135 | 7.9667
65 | 104 | 135 | 8
65 | 105 | 135 | 8.0333
65 | 106 | 135 | 8.0667
65 | 107 | 135 | 8.1
65 | 108 | 135 | 8.1333
65 | 109 | 135 | 8.1667
65 | 110 | 135 | 8.2
65 | 111 | 135 | 8.2333
65 | 112 | 135 | 8.2667
65 | 113 | 135 | 8.3
65 | 114 | 135 | 8.3333
65 | 115 | 135 | 8.3667
65 | 116 | 135 | 8.4
65 | 117 | 135 | 8.4333
65 | 118 | 135 | 8.4667
65 | 119 | 135 | 8.5
65 | 120 | 135 | 8.5333
65 | 121 | 135 | 8.5667
65 | 122 | 135 | 8.6
65 | 123 | 135 | 8.6333
65 | 124 | 135 | 8.6667
65 | 125 | 135 | 8.7
65 | 126 | 135 | 8.748
65 | 127 | 135 | 8.796
65 | 128 | 135 | 8.844
65 | 129 | 135 | 8.892
65 | 130 | 135 | 8.94
65 | 131 | 135 | 8.988
65 | 132 | 135 | 9.036
65 | 133 | 135 | 9.084
65 | 134 | 135 | 9.132
65 | 135 | 135 | 9.18
65 | 136 | 135 | 9.228
65 | 137 | 135 | 9.276
65 | 138 | 135 | 9.324
65 | 139 | 135 | 9.372
65 | 140 | 135 | 9.42
65 | 141 | 135 | 9.468
65 | 142 | 135 | 9.516
65 | 143 | 135 | 9.564
65 | 144 | 135 | 9.612
65 | 145 | 135 | 9.66
65 | 146 | 135 | 9.708
65 | 147 | 135 | 9.756
65 | 148 | 135 | 9.804
65 | 149 | 135 | 9.852
65 | 150 | 135 | 9.9
66 | 45 | 135 | 4.84
66 | 46 | 135 | 4.92
66 | 47 | 135 | 5
66 | 48 | 135 | 5.08
66 | 49 | 135 | 5.16
66 | 50 | 135 | 5.24
66 | 51 | 135 | 5.32
66 | 52 | 135 | 5.4
66 | 53 | 135 | 5.48
66 | 54 | 135 | 5.56
66 | 55 | 135 | 5.64
66 | 56 | 135 | 5.72
66 | 57 | 135 | 5.8
66 | 58 | 135 | 5.88
66 | 59 | 135 | 5.96
66 | 60 | 135 | 6.04
66 | 61 | 135 | 6.12
66 | 62 | 135 | 6.2
66 | 63 | 135 | 6.28
66 | 64 | 135 | 6.36
66 | 65 | 135 | 6.44
66 | 66 | 135 | 6.52
66 | 67 | 135 | 6.6
66 | 68 | 135 | 6.68
66 | 69 | 135 | 6.76
66 | 70 | 135 | 6.84
66 | 71 | 135 | 6.92
66 | 72 | 135 | 7
66 | 73 | 135 | 7.08
66 | 74 | 135 | 7.16
66 | 75 | 135 | 7.24
66 | 76 | 135 | 7.2656
66 | 77 | 135 | 7.2912
66 | 78 | 135 | 7.3168
66 | 79 | 135 | 7.3424
66 | 80 | 135 | 7.368
66 | 81 | 135 | 7.3936
66 | 82 | 135 | 7.4192
66 | 83 | 135 | 7.4448
66 | 84 | 135 | 7.4704
66 | 85 | 135 | 7.496
66 | 86 | 135 | 7.5216
66 | 87 | 135 | 7.5472
66 | 88 | 135 | 7.5728
66 | 89 | 135 | 7.5984
66 | 90 | 135 | 7.624
66 | 91 | 135 | 7.6496
66 | 92 | 135 | 7.6752
66 | 93 | 135 | 7.7008
66 | 94 | 135 | 7.7264
66 | 95 | 135 | 7.752
66 | 96 | 135 | 7.7776
66 | 97 | 135 | 7.8032
66 | 98 | 135 | 7.8288
66 | 99 | 135 | 7.8544
66 | 100 | 135 | 7.88
66 | 101 | 135 | 7.9136
66 | 102 | 135 | 7.9472
66 | 103 | 135 | 7.9808
66 | 104 | 135 | 8.0144
66 | 105 | 135 | 8.048
66 | 106 | 135 | 8.0816
66 | 107 | 135 | 8.1152
66 | 108 | 135 | 8.1488
66 | 109 | 135 | 8.1824
66 | 110 | 135 | 8.216
66 | 111 | 135 | 8.2496
66 | 112 | 135 | 8.2832
66 | 113 | 135 | 8.3168
66 | 114 | 135 | 8.3504
66 | 115 | 135 | 8.384
66 | 116 | 135 | 8.4176
66 | 117 | 135 | 8.4512
66 | 118 | 135 | 8.4848
66 | 119 | 135 | 8.5184
66 | 120 | 135 | 8.552
66 | 121 | 135 | 8.5856
66 | 122 | 135 | 8.6192
66 | 123 | 135 | 8.6528
66 | 124 | 135 | 8.6864
66 | 125 | 135 | 8.72
66 | 126 | 135 | 8.768
66 | 127 | 135 | 8.816
66 | 128 | 135 | 8.864
66 | 129 | 135 | 8.912
66 | 130 | 135 | 8.96
66 | 131 | 135 | 9.008
66 | 132 | 135 | 9.056
66 | 133 | 135 | 9.104
66 | 134 | 135 | 9.152
66 | 135 | 135 | 9.2
66 | 136 | 135 | 9.248
66 | 137 | 135 | 9.296
66 | 138 | 135 | 9.344
66 | 139 | 135 | 9.392
66 | 140 | 135 | 9.44
66 | 141 | 135 | 9.488
66 | 142 | 135 | 9.536
66 | 143 | 135 | 9.584
66 | 144 | 135 | 9.632
66 | 145 | 135 | 9.68
66 | 146 | 135 | 9.728
66 | 147 | 135 | 9.776
66 | 148 | 135 | 9.824
66 | 149 | 135 | 9.872
66 | 150 | 135 | 9.92
67 | 45 | 135 | 4.8467
67 | 46 | 135 | 4.9267
67 | 47 | 135 | 5.0067
67 | 48 | 135 | 5.0867
67 | 49 | 135 | 5.1667
67 | 50 | 135 | 5.2467
67 | 51 | 135 | 5.3267
67 | 52 | 135 | 5.4067
67 | 53 | 135 | 5.4867
67 | 54 | 135 | 5.5667
67 | 55 | 135 | 5.6467
67 | 56 | 135 | 5.7267
67 | 57 | 135 | 5.8067
67 | 58 | 135 | 5.8867
67 | 59 | 135 | 5.9667
67 | 60 | 135 | 6.0467
67 | 61 | 135 | 6.1267
67 | 62 | 135 | 6.2067
67 | 63 | 135 | 6.2867
67 | 64 | 135 | 6.3667
67 | 65 | 135 | 6.4467
67 | 66 | 135 | 6.5267
67 | 67 | 135 | 6.6067
67 | 68 | 135 | 6.6867
67 | 69 | 135 | 6.7667
67 | 70 | 135 | 6.8467
67 | 71 | 135 | 6.9267
67 | 72 | 135 | 7.0067
67 | 73 | 135 | 7.0867
67 | 74 | 135 | 7.1667
67 | 75 | 135 | 7.2467
67 | 76 | 135 | 7.2725
67 | 77 | 135 | 7.2984
67 | 78 | 135 | 7.3243
67 | 79 | 135 | 7.3501
67 | 80 | 135 | 7.376
67 | 81 | 135 | 7.4019
67 | 82 | 135 | 7.4277
67 | 83 | 135 | 7.4536
67 | 84 | 135 | 7.4795
67 | 85 | 135 | 7.5053
67 | 86 | 135 | 7.5312
67 | 87 | 135 | 7.5571
67 | 88 | 135 | 7.5829
67 | 89 | 135 | 7.6088
67 | 90 | 135 | 7.6347
67 | 91 | 135 | 7.6605
67 | 92 | 135 | 7.6864
67 | 93 | 135 | 7.7123
67 | 94 | 135 | 7.7381
67 | 95 | 135 | 7.764
67 | 96 | 135 | 7.7899
67 | 97 | 135 | 7.8157
67 | 98 | 135 | 7.8416
67 | 99 | 135 | 7.8675
67 | 100 | 135 | 7.8933
67 | 101 | 135 | 7.9272
67 | 102 | 135 | 7.9611
67 | 103 | 135 | 7.9949
67 | 104 | 135 | 8.0288
67 | 105 | 135 | 8.0627
67 | 106 | 135 | 8.0965
67 | 107 | 135 | 8.1304
67 | 108 | 135 | 8.1643
67 | 109 | 135 | 8.1981
67 | 110 | 135 | 8.232
67 | 111 | 135 | 8.2659
67 | 112 | 135 | 8.2997
67 | 113 | 135 | 8.3336
67 | 114 | 135 | 8.3675
67 | 115 | 135 | 8.4013
67 | 116 | 135 | 8.4352
67 | 117 | 135 | 8.4691
67 | 118 | 135 | 8.5029
67 | 119 | 135 | 8.5368
67 | 120 | 135 | 8.5707
67 | 121 | 135 | 8.6045
67 | 122 | 135 | 8.6384
67 | 123 | 135 | 8.6723
67 | 124 | 135 | 8.7061
67 | 125 | 135 | 8.74
67 | 126 | 135 | 8.788
67 | 127 | 135 | 8.836
67 | 128 | 135 | 8.884
67 | 129 | 135 | 8.932
67 | 130 | 135 | 8.98
67 | 131 | 135 | 9.028
67 | 132 | 135 | 9.076
67 | 133 | 135 | 9.124
67 | 134 | 135 | 9.172
67 | 135 | 135 | 9.22
67 | 136 | 135 | 9.268
67 | 137 | 135 | 9.316
67 | 138 | 135 | 9.364
67 | 139 | 135 | 9.412
67 | 140 | 135 | 9.46
67 | 141 | 135 | 9.508
67 | 142 | 135 | 9.556
67 | 143 | 135 | 9.604
67 | 144 | 135 | 9.652
67 | 145 | 135 | 9.7
67 | 146 | 135 | 9.748
67 | 147 | 135 | 9.796
67 | 148 | 135 | 9.844
67 | 149 | 135 | 9.892
67 | 150 | 135 | 9.94
68 | 45 | 135 | 4.8533
68 | 46 | 135 | 4.9333
68 | 47 | 135 | 5.0133
68 | 48 | 135 | 5.0933
68 | 49 | 135 | 5.1733
68 | 50 | 135 | 5.2533
68 | 51 | 135 | 5.3333
68 | 52 | 135 | 5.4133
68 | 53 | 135 | 5.4933
68 | 54 | 135 | 5.5733
68 | 55 | 135 | 5.6533
68 | 56 | 135 | 5.7333
68 | 57 | 135 | 5.8133
68 | 58 | 135 | 5.8933
68 | 59 | 135 | 5.9733
68 | 60 | 135 | 6.0533
68 | 61 | 135 | 6.1333
68 | 62 | 135 | 6.2133
68 | 63 | 135 | 6.2933
68 | 64 | 135 | 6.3733
68 | 65 | 135 | 6.4533
68 | 66 | 135 | 6.5333
68 | 67 | 135 | 6.6133
68 | 68 | 135 | 6.6933
68 | 69 | 135 | 6.7733
68 | 70 | 135 | 6.8533
68 | 71 | 135 | 6.9333
68 | 72 | 135 | 7.0133
68 | 73 | 135 | 7.0933
68 | 74 | 135 | 7.1733
68 | 75 | 135 | 7.2533
68 | 76 | 135 | 7.2795
68 | 77 | 135 | 7.3056
68 | 78 | 135 | 7.3317
68 | 79 | 135 | 7.3579
68 | 80 | 135 | 7.384
68 | 81 | 135 | 7.4101
68 | 82 | 135 | 7.4363
68 | 83 | 135 | 7.4624
68 | 84 | 135 | 7.4885
68 | 85 | 135 | 7.5147
68 | 86 | 135 | 7.5408
68 | 87 | 135 | 7.5669
68 | 88 | 135 | 7.5931
68 | 89 | 135 | 7.6192
68 | 90 | 135 | 7.6453
68 | 91 | 135 | 7.6715
68 | 92 | 135 | 7.6976
68 | 93 | 135 | 7.7237
68 | 94 | 135 | 7.7499
68 | 95 | 135 | 7.776
68 | 96 | 135 | 7.8021
68 | 97 | 135 | 7.8283
68 | 98 | 135 | 7.8544
68 | 99 | 135 | 7.8805
68 | 100 | 135 | 7.9067
68 | 101 | 135 | 7.9408
68 | 102 | 135 | 7.9749
68 | 103 | 135 | 8.0091
68 | 104 | 135 | 8.0432
68 | 105 | 135 | 8.0773
68 | 106 | 135 | 8.1115
68 | 107 | 135 | 8.1456
68 | 108 | 135 | 8.1797
68 | 109 | 135 | 8.2139
68 | 110 | 135 | 8.248
68 | 111 | 135 | 8.2821
68 | 112 | 135 | 8.3163
68 | 113 | 135 | 8.3504
68 | 114 | 135 | 8.3845
68 | 115 | 135 | 8.4187
68 | 116 | 135 | 8.4528
68 | 117 | 135 | 8.4869
68 | 118 | 135 | 8.5211
68 | 119 | 135 | 8.5552
68 | 120 | 135 | 8.5893
68 | 121 | 135 | 8.6235
68 | 122 | 135 | 8.6576
68 | 123 | 135 | 8.6917
68 | 124 | 135 | 8.7259
68 | 125 | 135 | 8.76
68 | 126 | 135 | 8.808
68 | 127 | 135 | 8.856
68 | 128 | 135 | 8.904
68 | 129 | 135 | 8.952
68 | 130 | 135 | 9
68 | 131 | 135 | 9.048
68 | 132 | 135 | 9.096
68 | 133 | 135 | 9.144
68 | 134 | 135 | 9.192
68 | 135 | 135 | 9.24
68 | 136 | 135 | 9.288
68 | 137 | 135 | 9.336
68 | 138 | 135 | 9.384
68 | 139 | 135 | 9.432
68 | 140 | 135 | 9.48
68 | 141 | 135 | 9.528
68 | 142 | 135 | 9.576
68 | 143 | 135 | 9.624
68 | 144 | 135 | 9.672
68 | 145 | 135 | 9.72
68 | 146 | 135 | 9.768
68 | 147 | 135 | 9.816
68 | 148 | 135 | 9.864
68 | 149 | 135 | 9.912
68 | 150 | 135 | 9.96
69 | 45 | 135 | 4.86
69 | 46 | 135 | 4.94
69 | 47 | 135 | 5.02
69 | 48 | 135 | 5.1
69 | 49 | 135 | 5.18
69 | 50 | 135 | 5.26
69 | 51 | 135 | 5.34
69 | 52 | 135 | 5.42
69 | 53 | 135 | 5.5
69 | 54 | 135 | 5.58
69 | 55 | 135 | 5.66
69 | 56 | 135 | 5.74
69 | 57 | 135 | 5.82
69 | 58 | 135 | 5.9
69 | 59 | 135 | 5.98
69 | 60 | 135 | 6.06
69 | 61 | 135 | 6.14
69 | 62 | 135 | 6.22
69 | 63 | 135 | 6.3
69 | 64 | 135 | 6.38
69 | 65 | 135 | 6.46
69 | 66 | 135 | 6.54
69 | 67 | 135 | 6.62
69 | 68 | 135 | 6.7
69 | 69 | 135 | 6.78
69 | 70 | 135 | 6.86
69 | 71 | 135 | 6.94
69 | 72 | 135 | 7.02
69 | 73 | 135 | 7.1
69 | 74 | 135 | 7.18
69 | 75 | 135 | 7.26
69 | 76 | 135 | 7.2864
69 | 77 | 135 | 7.3128
69 | 78 | 135 | 7.3392
69 | 79 | 135 | 7.3656
69 | 80 | 135 | 7.392
69 | 81 | 135 | 7.4184
69 | 82 | 135 | 7.4448
69 | 83 | 135 | 7.4712
69 | 84 | 135 | 7.4976
69 | 85 | 135 | 7.524
69 | 86 | 135 | 7.5504
69 | 87 | 135 | 7.5768
69 | 88 | 135 | 7.6032
69 | 89 | 135 | 7.6296
69 | 90 | 135 | 7.656
69 | 91 | 135 | 7.6824
69 | 92 | 135 | 7.7088
69 | 93 | 135 | 7.7352
69 | 94 | 135 | 7.7616
69 | 95 | 135 | 7.788
69 | 96 | 135 | 7.8144
69 | 97 | 135 | 7.8408
69 | 98 | 135 | 7.8672
69 | 99 | 135 | 7.8936
69 | 100 | 135 | 7.92
69 | 101 | 135 | 7.9544
69 | 102 | 135 | 7.9888
69 | 103 | 135 | 8.0232
69 | 104 | 135 | 8.0576
69 | 105 | 135 | 8.092
69 | 106 | 135 | 8.1264
69 | 107 | 135 | 8.1608
69 | 108 | 135 | 8.1952
69 | 109 | 135 | 8.2296
69 | 110 | 135 | 8.264
69 | 111 | 135 | 8.2984
69 | 112 | 135 | 8.3328
69 | 113 | 135 | 8.3672
69 | 114 | 135 | 8.4016
69 | 115 | 135 | 8.436
69 | 116 | 135 | 8.4704
69 | 117 | 135 | 8.5048
69 | 118 | 135 | 8.5392
69 | 119 | 135 | 8.5736
69 | 120 | 135 | 8.608
69 | 121 | 135 | 8.6424
69 | 122 | 135 | 8.6768
69 | 123 | 135 | 8.7112
69 | 124 | 135 | 8.7456
69 | 125 | 135 | 8.78
69 | 126 | 135 | 8.828
69 | 127 | 135 | 8.876
69 | 128 | 135 | 8.924
69 | 129 | 135 | 8.972
69 | 130 | 135 | 9.02
69 | 131 | 135 | 9.068
69 | 132 | 135 | 9.116
69 | 133 | 135 | 9.164
69 | 134 | 135 | 9.212
69 | 135 | 135 | 9.26
69 | 136 | 135 | 9.308
69 | 137 | 135 | 9.356
69 | 138 | 135 | 9.404
69 | 139 | 135 | 9.452
69 | 140 | 135 | 9.5
69 | 141 | 135 | 9.548
69 | 142 | 135 | 9.596
69 | 143 | 135 | 9.644
69 | 144 | 135 | 9.692
69 | 145 | 135 | 9.74
69 | 146 | 135 | 9.788
69 | 147 | 135 | 9.836
69 | 148 | 135 | 9.884
69 | 149 | 135 | 9.932
69 | 150 | 135 | 9.98
70 | 45 | 135 | 4.8667
70 | 46 | 135 | 4.9467
70 | 47 | 135 | 5.0267
70 | 48 | 135 | 5.1067
70 | 49 | 135 | 5.1867
70 | 50 | 135 | 5.2667
70 | 51 | 135 | 5.3467
70 | 52 | 135 | 5.4267
70 | 53 | 135 | 5.5067
70 | 54 | 135 | 5.5867
70 | 55 | 135 | 5.6667
70 | 56 | 135 | 5.7467
70 | 57 | 135 | 5.8267
70 | 58 | 135 | 5.9067
70 | 59 | 135 | 5.9867
70 | 60 | 135 | 6.0667
70 | 61 | 135 | 6.1467
70 | 62 | 135 | 6.2267
70 | 63 | 135 | 6.3067
70 | 64 | 135 | 6.3867
70 | 65 | 135 | 6.4667
70 | 66 | 135 | 6.5467
70 | 67 | 135 | 6.6267
70 | 68 | 135 | 6.7067
70 | 69 | 135 | 6.7867
70 | 70 | 135 | 6.8667
70 | 71 | 135 | 6.9467
70 | 72 | 135 | 7.0267
70 | 73 | 135 | 7.1067
70 | 74 | 135 | 7.1867
70 | 75 | 135 | 7.2667
70 | 76 | 135 | 7.2933
70 | 77 | 135 | 7.32
70 | 78 | 135 | 7.3467
70 | 79 | 135 | 7.3733
70 | 80 | 135 | 7.4
70 | 81 | 135 | 7.4267
70 | 82 | 135 | 7.4533
70 | 83 | 135 | 7.48
70 | 84 | 135 | 7.5067
70 | 85 | 135 | 7.5333
70 | 86 | 135 | 7.56
70 | 87 | 135 | 7.5867
70 | 88 | 135 | 7.6133
70 | 89 | 135 | 7.64
70 | 90 | 135 | 7.6667
70 | 91 | 135 | 7.6933
70 | 92 | 135 | 7.72
70 | 93 | 135 | 7.7467
70 | 94 | 135 | 7.7733
70 | 95 | 135 | 7.8
70 | 96 | 135 | 7.8267
70 | 97 | 135 | 7.8533
70 | 98 | 135 | 7.88
70 | 99 | 135 | 7.9067
70 | 100 | 135 | 7.9333
70 | 101 | 135 | 7.968
70 | 102 | 135 | 8.0027
70 | 103 | 135 | 8.0373
70 | 104 | 135 | 8.072
70 | 105 | 135 | 8.1067
70 | 106 | 135 | 8.1413
70 | 107 | 135 | 8.176
70 | 108 | 135 | 8.2107
70 | 109 | 135 | 8.2453
70 | 110 | 135 | 8.28
70 | 111 | 135 | 8.3147
70 | 112 | 135 | 8.3493
70 | 113 | 135 | 8.384
70 | 114 | 135 | 8.4187
70 | 115 | 135 | 8.4533
70 | 116 | 135 | 8.488
70 | 117 | 135 | 8.5227
70 | 118 | 135 | 8.5573
70 | 119 | 135 | 8.592
70 | 120 | 135 | 8.6267
70 | 121 | 135 | 8.6613
70 | 122 | 135 | 8.696
70 | 123 | 135 | 8.7307
70 | 124 | 135 | 8.7653
70 | 125 | 135 | 8.8
70 | 126 | 135 | 8.848
70 | 127 | 135 | 8.896
70 | 128 | 135 | 8.944
70 | 129 | 135 | 8.992
70 | 130 | 135 | 9.04
70 | 131 | 135 | 9.088
70 | 132 | 135 | 9.136
70 | 133 | 135 | 9.184
70 | 134 | 135 | 9.232
70 | 135 | 135 | 9.28
70 | 136 | 135 | 9.328
70 | 137 | 135 | 9.376
70 | 138 | 135 | 9.424
70 | 139 | 135 | 9.472
70 | 140 | 135 | 9.52
70 | 141 | 135 | 9.568
70 | 142 | 135 | 9.616
70 | 143 | 135 | 9.664
70 | 144 | 135 | 9.712
70 | 145 | 135 | 9.76
70 | 146 | 135 | 9.808
70 | 147 | 135 | 9.856
70 | 148 | 135 | 9.904
70 | 149 | 135 | 9.952
70 | 150 | 135 | 10
71 | 45 | 135 | 4.8733
71 | 46 | 135 | 4.9533
71 | 47 | 135 | 5.0333
71 | 48 | 135 | 5.1133
71 | 49 | 135 | 5.1933
71 | 50 | 135 | 5.2733
71 | 51 | 135 | 5.3533
71 | 52 | 135 | 5.4333
71 | 53 | 135 | 5.5133
71 | 54 | 135 | 5.5933
71 | 55 | 135 | 5.6733
71 | 56 | 135 | 5.7533
71 | 57 | 135 | 5.8333
71 | 58 | 135 | 5.9133
71 | 59 | 135 | 5.9933
71 | 60 | 135 | 6.0733
71 | 61 | 135 | 6.1533
71 | 62 | 135 | 6.2333
71 | 63 | 135 | 6.3133
71 | 64 | 135 | 6.3933
71 | 65 | 135 | 6.4733
71 | 66 | 135 | 6.5533
71 | 67 | 135 | 6.6333
71 | 68 | 135 | 6.7133
71 | 69 | 135 | 6.7933
71 | 70 | 135 | 6.8733
71 | 71 | 135 | 6.9533
71 | 72 | 135 | 7.0333
71 | 73 | 135 | 7.1133
71 | 74 | 135 | 7.1933
71 | 75 | 135 | 7.2733
71 | 76 | 135 | 7.3003
71 | 77 | 135 | 7.3272
71 | 78 | 135 | 7.3541
71 | 79 | 135 | 7.3811
71 | 80 | 135 | 7.408
71 | 81 | 135 | 7.4349
71 | 82 | 135 | 7.4619
71 | 83 | 135 | 7.4888
71 | 84 | 135 | 7.5157
71 | 85 | 135 | 7.5427
71 | 86 | 135 | 7.5696
71 | 87 | 135 | 7.5965
71 | 88 | 135 | 7.6235
71 | 89 | 135 | 7.6504
71 | 90 | 135 | 7.6773
71 | 91 | 135 | 7.7043
71 | 92 | 135 | 7.7312
71 | 93 | 135 | 7.7581
71 | 94 | 135 | 7.7851
71 | 95 | 135 | 7.812
71 | 96 | 135 | 7.8389
71 | 97 | 135 | 7.8659
71 | 98 | 135 | 7.8928
71 | 99 | 135 | 7.9197
71 | 100 | 135 | 7.9467
71 | 101 | 135 | 7.9816
71 | 102 | 135 | 8.0165
71 | 103 | 135 | 8.0515
71 | 104 | 135 | 8.0864
71 | 105 | 135 | 8.1213
71 | 106 | 135 | 8.1563
71 | 107 | 135 | 8.1912
71 | 108 | 135 | 8.2261
71 | 109 | 135 | 8.2611
71 | 110 | 135 | 8.296
71 | 111 | 135 | 8.3309
71 | 112 | 135 | 8.3659
71 | 113 | 135 | 8.4008
71 | 114 | 135 | 8.4357
71 | 115 | 135 | 8.4707
71 | 116 | 135 | 8.5056
71 | 117 | 135 | 8.5405
71 | 118 | 135 | 8.5755
71 | 119 | 135 | 8.6104
71 | 120 | 135 | 8.6453
71 | 121 | 135 | 8.6803
71 | 122 | 135 | 8.7152
71 | 123 | 135 | 8.7501
71 | 124 | 135 | 8.7851
71 | 125 | 135 | 8.82
71 | 126 | 135 | 8.868
71 | 127 | 135 | 8.916
71 | 128 | 135 | 8.964
71 | 129 | 135 | 9.012
71 | 130 | 135 | 9.06
71 | 131 | 135 | 9.108
71 | 132 | 135 | 9.156
71 | 133 | 135 | 9.204
71 | 134 | 135 | 9.252
71 | 135 | 135 | 9.3
71 | 136 | 135 | 9.348
71 | 137 | 135 | 9.396
71 | 138 | 135 | 9.444
71 | 139 | 135 | 9.492
71 | 140 | 135 | 9.54
71 | 141 | 135 | 9.588
71 | 142 | 135 | 9.636
71 | 143 | 135 | 9.684
71 | 144 | 135 | 9.732
71 | 145 | 135 | 9.78
71 | 146 | 135 | 9.828
71 | 147 | 135 | 9.876
71 | 148 | 135 | 9.924
71 | 149 | 135 | 9.972
71 | 150 | 135 | 10.02
72 | 45 | 135 | 4.88
72 | 46 | 135 | 4.96
72 | 47 | 135 | 5.04
72 | 48 | 135 | 5.12
72 | 49 | 135 | 5.2
72 | 50 | 135 | 5.28
72 | 51 | 135 | 5.36
72 | 52 | 135 | 5.44
72 | 53 | 135 | 5.52
72 | 54 | 135 | 5.6
72 | 55 | 135 | 5.68
72 | 56 | 135 | 5.76
72 | 57 | 135 | 5.84
72 | 58 | 135 | 5.92
72 | 59 | 135 | 6
72 | 60 | 135 | 6.08
72 | 61 | 135 | 6.16
72 | 62 | 135 | 6.24
72 | 63 | 135 | 6.32
72 | 64 | 135 | 6.4
72 | 65 | 135 | 6.48
72 | 66 | 135 | 6.56
72 | 67 | 135 | 6.64
72 | 68 | 135 | 6.72
72 | 69 | 135 | 6.8
72 | 70 | 135 | 6.88
72 | 71 | 135 | 6.96
72 | 72 | 135 | 7.04
72 | 73 | 135 | 7.12
72 | 74 | 135 | 7.2
72 | 75 | 135 | 7.28
72 | 76 | 135 | 7.3072
72 | 77 | 135 | 7.3344
72 | 78 | 135 | 7.3616
72 | 79 | 135 | 7.3888
72 | 80 | 135 | 7.416
72 | 81 | 135 | 7.4432
72 | 82 | 135 | 7.4704
72 | 83 | 135 | 7.4976
72 | 84 | 135 | 7.5248
72 | 85 | 135 | 7.552
72 | 86 | 135 | 7.5792
72 | 87 | 135 | 7.6064
72 | 88 | 135 | 7.6336
72 | 89 | 135 | 7.6608
72 | 90 | 135 | 7.688
72 | 91 | 135 | 7.7152
72 | 92 | 135 | 7.7424
72 | 93 | 135 | 7.7696
72 | 94 | 135 | 7.7968
72 | 95 | 135 | 7.824
72 | 96 | 135 | 7.8512
72 | 97 | 135 | 7.8784
72 | 98 | 135 | 7.9056
72 | 99 | 135 | 7.9328
72 | 100 | 135 | 7.96
72 | 101 | 135 | 7.9952
72 | 102 | 135 | 8.0304
72 | 103 | 135 | 8.0656
72 | 104 | 135 | 8.1008
72 | 105 | 135 | 8.136
72 | 106 | 135 | 8.1712
72 | 107 | 135 | 8.2064
72 | 108 | 135 | 8.2416
72 | 109 | 135 | 8.2768
72 | 110 | 135 | 8.312
72 | 111 | 135 | 8.3472
72 | 112 | 135 | 8.3824
72 | 113 | 135 | 8.4176
72 | 114 | 135 | 8.4528
72 | 115 | 135 | 8.488
72 | 116 | 135 | 8.5232
72 | 117 | 135 | 8.5584
72 | 118 | 135 | 8.5936
72 | 119 | 135 | 8.6288
72 | 120 | 135 | 8.664
72 | 121 | 135 | 8.6992
72 | 122 | 135 | 8.7344
72 | 123 | 135 | 8.7696
72 | 124 | 135 | 8.8048
72 | 125 | 135 | 8.84
72 | 126 | 135 | 8.888
72 | 127 | 135 | 8.936
72 | 128 | 135 | 8.984
72 | 129 | 135 | 9.032
72 | 130 | 135 | 9.08
72 | 131 | 135 | 9.128
72 | 132 | 135 | 9.176
72 | 133 | 135 | 9.224
72 | 134 | 135 | 9.272
72 | 135 | 135 | 9.32
72 | 136 | 135 | 9.368
72 | 137 | 135 | 9.416
72 | 138 | 135 | 9.464
72 | 139 | 135 | 9.512
72 | 140 | 135 | 9.56
72 | 141 | 135 | 9.608
72 | 142 | 135 | 9.656
72 | 143 | 135 | 9.704
72 | 144 | 135 | 9.752
72 | 145 | 135 | 9.8
72 | 146 | 135 | 9.848
72 | 147 | 135 | 9.896
72 | 148 | 135 | 9.944
72 | 149 | 135 | 9.992
72 | 150 | 135 | 10.04
73 | 45 | 135 | 4.8867
73 | 46 | 135 | 4.9667
73 | 47 | 135 | 5.0467
73 | 48 | 135 | 5.1267
73 | 49 | 135 | 5.2067
73 | 50 | 135 | 5.2867
73 | 51 | 135 | 5.3667
73 | 52 | 135 | 5.4467
73 | 53 | 135 | 5.5267
73 | 54 | 135 | 5.6067
73 | 55 | 135 | 5.6867
73 | 56 | 135 | 5.7667
73 | 57 | 135 | 5.8467
73 | 58 | 135 | 5.9267
73 | 59 | 135 | 6.0067
73 | 60 | 135 | 6.0867
73 | 61 | 135 | 6.1667
73 | 62 | 135 | 6.2467
73 | 63 | 135 | 6.3267
73 | 64 | 135 | 6.4067
73 | 65 | 135 | 6.4867
73 | 66 | 135 | 6.5667
73 | 67 | 135 | 6.6467
73 | 68 | 135 | 6.7267
73 | 69 | 135 | 6.8067
73 | 70 | 135 | 6.8867
73 | 71 | 135 | 6.9667
73 | 72 | 135 | 7.0467
73 | 73 | 135 | 7.1267
73 | 74 | 135 | 7.2067
73 | 75 | 135 | 7.2867
73 | 76 | 135 | 7.3141
73 | 77 | 135 | 7.3416
73 | 78 | 135 | 7.3691
73 | 79 | 135 | 7.3965
73 | 80 | 135 | 7.424
73 | 81 | 135 | 7.4515
73 | 82 | 135 | 7.4789
73 | 83 | 135 | 7.5064
73 | 84 | 135 | 7.5339
73 | 85 | 135 | 7.5613
73 | 86 | 135 | 7.5888
73 | 87 | 135 | 7.6163
73 | 88 | 135 | 7.6437
73 | 89 | 135 | 7.6712
73 | 90 | 135 | 7.6987
73 | 91 | 135 | 7.7261
73 | 92 | 135 | 7.7536
73 | 93 | 135 | 7.7811
73 | 94 | 135 | 7.8085
73 | 95 | 135 | 7.836
73 | 96 | 135 | 7.8635
73 | 97 | 135 | 7.8909
73 | 98 | 135 | 7.9184
73 | 99 | 135 | 7.9459
73 | 100 | 135 | 7.9733
73 | 101 | 135 | 8.0088
73 | 102 | 135 | 8.0443
73 | 103 | 135 | 8.0797
73 | 104 | 135 | 8.1152
73 | 105 | 135 | 8.1507
73 | 106 | 135 | 8.1861
73 | 107 | 135 | 8.2216
73 | 108 | 135 | 8.2571
73 | 109 | 135 | 8.2925
73 | 110 | 135 | 8.328
73 | 111 | 135 | 8.3635
73 | 112 | 135 | 8.3989
73 | 113 | 135 | 8.4344
73 | 114 | 135 | 8.4699
73 | 115 | 135 | 8.5053
73 | 116 | 135 | 8.5408
73 | 117 | 135 | 8.5763
73 | 118 | 135 | 8.6117
73 | 119 | 135 | 8.6472
73 | 120 | 135 | 8.6827
73 | 121 | 135 | 8.7181
73 | 122 | 135 | 8.7536
73 | 123 | 135 | 8.7891
73 | 124 | 135 | 8.8245
73 | 125 | 135 | 8.86
73 | 126 | 135 | 8.908
73 | 127 | 135 | 8.956
73 | 128 | 135 | 9.004
73 | 129 | 135 | 9.052
73 | 130 | 135 | 9.1
73 | 131 | 135 | 9.148
73 | 132 | 135 | 9.196
73 | 133 | 135 | 9.244
73 | 134 | 135 | 9.292
73 | 135 | 135 | 9.34
73 | 136 | 135 | 9.388
73 | 137 | 135 | 9.436
73 | 138 | 135 | 9.484
73 | 139 | 135 | 9.532
73 | 140 | 135 | 9.58
73 | 141 | 135 | 9.628
73 | 142 | 135 | 9.676
73 | 143 | 135 | 9.724
73 | 144 | 135 | 9.772
73 | 145 | 135 | 9.82
73 | 146 | 135 | 9.868
73 | 147 | 135 | 9.916
73 | 148 | 135 | 9.964
73 | 149 | 135 | 10.012
73 | 150 | 135 | 10.06
74 | 45 | 135 | 4.8933
74 | 46 | 135 | 4.9733
74 | 47 | 135 | 5.0533
74 | 48 | 135 | 5.1333
74 | 49 | 135 | 5.2133
74 | 50 | 135 | 5.2933
74 | 51 | 135 | 5.3733
74 | 52 | 135 | 5.4533
74 | 53 | 135 | 5.5333
74 | 54 | 135 | 5.6133
74 | 55 | 135 | 5.6933
74 | 56 | 135 | 5.7733
74 | 57 | 135 | 5.8533
74 | 58 | 135 | 5.9333
74 | 59 | 135 | 6.0133
74 | 60 | 135 | 6.0933
74 | 61 | 135 | 6.1733
74 | 62 | 135 | 6.2533
74 | 63 | 135 | 6.3333
74 | 64 | 135 | 6.4133
74 | 65 | 135 | 6.4933
74 | 66 | 135 | 6.5733
74 | 67 | 135 | 6.6533
74 | 68 | 135 | 6.7333
74 | 69 | 135 | 6.8133
74 | 70 | 135 | 6.8933
74 | 71 | 135 | 6.9733
74 | 72 | 135 | 7.0533
74 | 73 | 135 | 7.1333
74 | 74 | 135 | 7.2133
74 | 75 | 135 | 7.2933
74 | 76 | 135 | 7.3211
74 | 77 | 135 | 7.3488
74 | 78 | 135 | 7.3765
74 | 79 | 135 | 7.4043
74 | 80 | 135 | 7.432
74 | 81 | 135 | 7.4597
74 | 82 | 135 | 7.4875
74 | 83 | 135 | 7.5152
74 | 84 | 135 | 7.5429
74 | 85 | 135 | 7.5707
74 | 86 | 135 | 7.5984
74 | 87 | 135 | 7.6261
74 | 88 | 135 | 7.6539
74 | 89 | 135 | 7.6816
74 | 90 | 135 | 7.7093
74 | 91 | 135 | 7.7371
74 | 92 | 135 | 7.7648
74 | 93 | 135 | 7.7925
74 | 94 | 135 | 7.8203
74 | 95 | 135 | 7.848
74 | 96 | 135 | 7.8757
74 | 97 | 135 | 7.9035
74 | 98 | 135 | 7.9312
74 | 99 | 135 | 7.9589
74 | 100 | 135 | 7.9867
74 | 101 | 135 | 8.0224
74 | 102 | 135 | 8.0581
74 | 103 | 135 | 8.0939
74 | 104 | 135 | 8.1296
74 | 105 | 135 | 8.1653
74 | 106 | 135 | 8.2011
74 | 107 | 135 | 8.2368
74 | 108 | 135 | 8.2725
74 | 109 | 135 | 8.3083
74 | 110 | 135 | 8.344
74 | 111 | 135 | 8.3797
74 | 112 | 135 | 8.4155
74 | 113 | 135 | 8.4512
74 | 114 | 135 | 8.4869
74 | 115 | 135 | 8.5227
74 | 116 | 135 | 8.5584
74 | 117 | 135 | 8.5941
74 | 118 | 135 | 8.6299
74 | 119 | 135 | 8.6656
74 | 120 | 135 | 8.7013
74 | 121 | 135 | 8.7371
74 | 122 | 135 | 8.7728
74 | 123 | 135 | 8.8085
74 | 124 | 135 | 8.8443
74 | 125 | 135 | 8.88
74 | 126 | 135 | 8.928
74 | 127 | 135 | 8.976
74 | 128 | 135 | 9.024
74 | 129 | 135 | 9.072
74 | 130 | 135 | 9.12
74 | 131 | 135 | 9.168
74 | 132 | 135 | 9.216
74 | 133 | 135 | 9.264
74 | 134 | 135 | 9.312
74 | 135 | 135 | 9.36
74 | 136 | 135 | 9.408
74 | 137 | 135 | 9.456
74 | 138 | 135 | 9.504
74 | 139 | 135 | 9.552
74 | 140 | 135 | 9.6
74 | 141 | 135 | 9.648
74 | 142 | 135 | 9.696
74 | 143 | 135 | 9.744
74 | 144 | 135 | 9.792
74 | 145 | 135 | 9.84
74 | 146 | 135 | 9.888
74 | 147 | 135 | 9.936
74 | 148 | 135 | 9.984
74 | 149 | 135 | 10.032
74 | 150 | 135 | 10.08
75 | 45 | 135 | 4.9
75 | 46 | 135 | 4.98
75 | 47 | 135 | 5.06
75 | 48 | 135 | 5.14
75 | 49 | 135 | 5.22
75 | 50 | 135 | 5.3
75 | 51 | 135 | 5.38
75 | 52 | 135 | 5.46
75 | 53 | 135 | 5.54
75 | 54 | 135 | 5.62
75 | 55 | 135 | 5.7
75 | 56 | 135 | 5.78
75 | 57 | 135 | 5.86
75 | 58 | 135 | 5.94
75 | 59 | 135 | 6.02
75 | 60 | 135 | 6.1
75 | 61 | 135 | 6.18
75 | 62 | 135 | 6.26
75 | 63 | 135 | 6.34
75 | 64 | 135 | 6.42
75 | 65 | 135 | 6.5
75 | 66 | 135 | 6.58
75 | 67 | 135 | 6.66
75 | 68 | 135 | 6.74
75 | 69 | 135 | 6.82
75 | 70 | 135 | 6.9
75 | 71 | 135 | 6.98
75 | 72 | 135 | 7.06
75 | 73 | 135 | 7.14
75 | 74 | 135 | 7.22
75 | 75 | 135 | 7.3
75 | 76 | 135 | 7.328
75 | 77 | 135 | 7.356
75 | 78 | 135 | 7.384
75 | 79 | 135 | 7.412
75 | 80 | 135 | 7.44
75 | 81 | 135 | 7.468
75 | 82 | 135 | 7.496
75 | 83 | 135 | 7.524
75 | 84 | 135 | 7.552
75 | 85 | 135 | 7.58
75 | 86 | 135 | 7.608
75 | 87 | 135 | 7.636
75 | 88 | 135 | 7.664
75 | 89 | 135 | 7.692
75 | 90 | 135 | 7.72
75 | 91 | 135 | 7.748
75 | 92 | 135 | 7.776
75 | 93 | 135 | 7.804
75 | 94 | 135 | 7.832
75 | 95 | 135 | 7.86
75 | 96 | 135 | 7.888
75 | 97 | 135 | 7.916
75 | 98 | 135 | 7.944
75 | 99 | 135 | 7.972
75 | 100 | 135 | 8
75 | 101 | 135 | 8.036
75 | 102 | 135 | 8.072
75 | 103 | 135 | 8.108
75 | 104 | 135 | 8.144
75 | 105 | 135 | 8.18
75 | 106 | 135 | 8.216
75 | 107 | 135 | 8.252
75 | 108 | 135 | 8.288
75 | 109 | 135 | 8.324
75 | 110 | 135 | 8.36
75 | 111 | 135 | 8.396
75 | 112 | 135 | 8.432
75 | 113 | 135 | 8.468
75 | 114 | 135 | 8.504
75 | 115 | 135 | 8.54
75 | 116 | 135 | 8.576
75 | 117 | 135 | 8.612
75 | 118 | 135 | 8.648
75 | 119 | 135 | 8.684
75 | 120 | 135 | 8.72
75 | 121 | 135 | 8.756
75 | 122 | 135 | 8.792
75 | 123 | 135 | 8.828
75 | 124 | 135 | 8.864
75 | 125 | 135 | 8.9
75 | 126 | 135 | 8.948
75 | 127 | 135 | 8.996
75 | 128 | 135 | 9.044
75 | 129 | 135 | 9.092
75 | 130 | 135 | 9.14
75 | 131 | 135 | 9.188
75 | 132 | 135 | 9.236
75 | 133 | 135 | 9.284
75 | 134 | 135 | 9.332
75 | 135 | 135 | 9.38
75 | 136 | 135 | 9.428
75 | 137 | 135 | 9.476
75 | 138 | 135 | 9.524
75 | 139 | 135 | 9.572
75 | 140 | 135 | 9.62
75 | 141 | 135 | 9.668
75 | 142 | 135 | 9.716
75 | 143 | 135 | 9.764
75 | 144 | 135 | 9.812
75 | 145 | 135 | 9.86
75 | 146 | 135 | 9.908
75 | 147 | 135 | 9.956
75 | 148 | 135 | 10.004
75 | 149 | 135 | 10.052
75 | 150 | 135 | 10.1

## Data Sheet 1 (hidden)
Absolute | Boiling Point | Specific Volume (steam) | Density (steam) | Specific Enthalpy of Liquid Water |  | Specific Enthalpy of Steam |  | Latent heat of Vaporization |  | Specific Heat
Pressure |  |  |  | (sensible heat) |  | (total heat)
(bar) | (oC) | (m3/kg) | (kg/m3) | (kJ/kg) | (kcal/kg) | (kJ/kg) | (kcal/kg) | (kJ/kg) | (kcal/kg) | (kJ/kg K)
0.02 | 17.51 | 67.006 | 0.015 | 73.45 | 17.54 | 2533.64 | 605.15 | 2460.19 | 587.61 | 1.8644
0.03 | 24.1 | 45.667 | 0.022 | 101 | 24.12 | 2545.64 | 608.02 | 2444.65 | 583.89 | 1.8694
0.04 | 28.98 | 34.802 | 0.029 | 121.41 | 29 | 2554.51 | 610.13 | 2433.1 | 581.14 | 1.8736
0.05 | 32.9 | 28.194 | 0.035 | 137.77 | 32.91 | 2561.59 | 611.83 | 2423.82 | 578.92 | 1.8774
0.06 | 36.18 | 23.741 | 0.042 | 151.5 | 36.19 | 2567.51 | 613.24 | 2416.01 | 577.05 | 1.8808
0.07 | 39.02 | 20.531 | 0.049 | 163.38 | 39.02 | 2572.62 | 614.46 | 2409.24 | 575.44 | 1.884
0.08 | 41.53 | 18.105 | 0.055 | 173.87 | 41.53 | 2577.11 | 615.53 | 2403.25 | 574.01 | 1.8871
0.09 | 43.79 | 16.204 | 0.062 | 183.28 | 43.78 | 2581.14 | 616.49 | 2397.85 | 572.72 | 1.8899
0.1 | 45.83 | 14.675 | 0.068 | 191.84 | 45.82 | 2584.78 | 617.36 | 2392.94 | 571.54 | 1.8927
0.2 | 60.09 | 7.65 | 0.131 | 251.46 | 60.06 | 2609.86 | 623.35 | 2358.4 | 563.3 | 1.9156
0.3 | 69.13 | 5.229 | 0.191 | 289.31 | 69.1 | 2625.43 | 627.07 | 2336.13 | 557.97 | 1.9343
0.4 | 75.89 | 3.993 | 0.25 | 317.65 | 75.87 | 2636.88 | 629.81 | 2319.23 | 553.94 | 1.9506
0.5 | 81.35 | 3.24 | 0.309 | 340.57 | 81.34 | 2645.99 | 631.98 | 2305.42 | 550.64 | 1.9654
0.6 | 85.95 | 2.732 | 0.366 | 359.93 | 85.97 | 2653.57 | 633.79 | 2293.64 | 547.83 | 1.979
0.7 | 89.96 | 2.365 | 0.423 | 376.77 | 89.99 | 2660.07 | 635.35 | 2283.3 | 545.36 | 1.9919
0.8 | 93.51 | 2.087 | 0.479 | 391.73 | 93.56 | 2665.77 | 636.71 | 2274.05 | 543.15 | 2.004
0.9 | 96.71 | 1.869 | 0.535 | 405.21 | 96.78 | 2670.85 | 637.92 | 2265.65 | 541.14 | 2.0156
11) | 99.63 | 1.694 | 0.59 | 417.51 | 99.72 | 2675.43 | 639.02 | 2257.92 | 539.3 | 2.0267
1.1 | 102.32 | 1.549 | 0.645 | 428.84 | 102.43 | 2679.61 | 640.01 | 2250.76 | 537.59 | 2.0373
1.2 | 104.81 | 1.428 | 0.7 | 439.36 | 104.94 | 2683.44 | 640.93 | 2244.08 | 535.99 | 2.0476
1.3 | 107.13 | 1.325 | 0.755 | 449.19 | 107.29 | 2686.98 | 641.77 | 2237.79 | 534.49 | 2.0576
1.4 | 109.32 | 1.236 | 0.809 | 458.42 | 109.49 | 2690.28 | 642.56 | 2231.86 | 533.07 | 2.0673
1.5 | 111.37 | 1.159 | 0.863 | 467.13 | 111.57 | 2693.36 | 643.3 | 2226.23 | 531.73 | 2.0768
1.6 | 113.32 | 1.091 | 0.916 | 475.38 | 113.54 | 2696.25 | 643.99 | 2220.87 | 530.45 | 2.086
1.7 | 115.17 | 1.031 | 0.97 | 483.22 | 115.42 | 2698.97 | 644.64 | 2215.75 | 529.22 | 2.095
1.8 | 116.93 | 0.977 | 1.023 | 490.7 | 117.2 | 2701.54 | 645.25 | 2210.84 | 528.05 | 2.1037
1.9 | 118.62 | 0.929 | 1.076 | 497.85 | 118.91 | 2703.98 | 645.83 | 2206.13 | 526.92 | 2.1124
2 | 120.23 | 0.885 | 1.129 | 504.71 | 120.55 | 2706.29 | 646.39 | 2201.59 | 525.84 | 2.1208
2.2 | 123.27 | 0.81 | 1.235 | 517.63 | 123.63 | 2710.6 | 647.42 | 2192.98 | 523.78 | 2.1372
2.4 | 126.09 | 0.746 | 1.34 | 529.64 | 126.5 | 2714.55 | 648.36 | 2184.91 | 521.86 | 2.1531
2.6 | 128.73 | 0.693 | 1.444 | 540.88 | 129.19 | 2718.17 | 649.22 | 2177.3 | 520.04 | 2.1685
2.8 | 131.2 | 0.646 | 1.548 | 551.45 | 131.71 | 2721.54 | 650.03 | 2170.08 | 518.32 | 2.1835
3 | 133.54 | 0.606 | 1.651 | 561.44 | 134.1 | 2724.66 | 650.77 | 2163.22 | 516.68 | 2.1981
3.5 | 138.87 | 0.524 | 1.908 | 584.28 | 139.55 | 2731.63 | 652.44 | 2147.35 | 512.89 | 2.2331
4 | 143.63 | 0.462 | 2.163 | 604.68 | 144.43 | 2737.63 | 653.87 | 2132.95 | 509.45 | 2.2664
4.5 | 147.92 | 0.414 | 2.417 | 623.17 | 148.84 | 2742.88 | 655.13 | 2119.71 | 506.29 | 2.2983
5 | 151.85 | 0.375 | 2.669 | 640.12 | 152.89 | 2747.54 | 656.24 | 2107.42 | 503.35 | 2.3289
5.5 | 155.47 | 0.342 | 2.92 | 655.81 | 156.64 | 2751.7 | 657.23 | 2095.9 | 500.6 | 2.3585
6 | 158.84 | 0.315 | 3.17 | 670.43 | 160.13 | 2755.46 | 658.13 | 2085.03 | 498 | 2.3873
6.5 | 161.99 | 0.292 | 3.419 | 684.14 | 163.4 | 2758.87 | 658.94 | 2074.73 | 495.54 | 2.4152
7 | 164.96 | 0.273 | 3.667 | 697.07 | 166.49 | 2761.98 | 659.69 | 2064.92 | 493.2 | 2.4424
7.5 | 167.76 | 0.255 | 3.915 | 709.3 | 169.41 | 2764.84 | 660.37 | 2055.53 | 490.96 | 2.469
8 | 170.42 | 0.24 | 4.162 | 720.94 | 172.19 | 2767.46 | 661 | 2046.53 | 488.8 | 2.4951
8.5 | 172.94 | 0.227 | 4.409 | 732.03 | 174.84 | 2769.89 | 661.58 | 2037.86 | 486.73 | 2.5206
9 | 175.36 | 0.215 | 4.655 | 742.64 | 177.38 | 2772.13 | 662.11 | 2029.49 | 484.74 | 2.5456
9.5 | 177.67 | 0.204 | 4.901 | 752.82 | 179.81 | 2774.22 | 662.61 | 2021.4 | 482.8 | 2.5702
10 | 179.88 | 0.194 | 5.147 | 762.6 | 182.14 | 2776.16 | 663.07 | 2013.56 | 480.93 | 2.5944
11 | 184.06 | 0.177 | 5.638 | 781.11 | 186.57 | 2779.66 | 663.91 | 1998.55 | 477.35 | 2.6418
12 | 187.96 | 0.163 | 6.127 | 798.42 | 190.7 | 2782.73 | 664.64 | 1984.31 | 473.94 | 2.6878
13 | 191.6 | 0.151 | 6.617 | 814.68 | 194.58 | 2785.42 | 665.29 | 1970.73 | 470.7 | 2.7327
14 | 195.04 | 0.141 | 7.106 | 830.05 | 198.26 | 2787.79 | 665.85 | 1957.73 | 467.6 | 2.7767
15 | 198.28 | 0.132 | 7.596 | 844.64 | 201.74 | 2789.88 | 666.35 | 1945.24 | 464.61 | 2.8197
16 | 201.37 | 0.124 | 8.085 | 858.54 | 205.06 | 2791.73 | 666.79 | 1933.19 | 461.74 | 2.862
17 | 204.3 | 0.117 | 8.575 | 871.82 | 208.23 | 2793.37 | 667.18 | 1921.55 | 458.95 | 2.9036
18 | 207.11 | 0.11 | 9.065 | 884.55 | 211.27 | 2794.81 | 667.53 | 1910.27 | 456.26 | 2.9445
19 | 209.79 | 0.105 | 9.556 | 896.78 | 214.19 | 2796.09 | 667.83 | 1899.31 | 453.64 | 2.9849
20 | 212.37 | 0.1 | 10.047 | 908.56 | 217.01 | 2797.21 | 668.1 | 1888.65 | 451.1 | 3.0248
21 | 214.85 | 0.095 | 10.539 | 919.93 | 219.72 | 2798.18 | 668.33 | 1878.25 | 448.61 | 3.0643
22 | 217.24 | 0.091 | 11.032 | 930.92 | 222.35 | 2799.03 | 668.54 | 1868.11 | 446.19 | 3.1034
23 | 219.55 | 0.087 | 11.525 | 941.57 | 224.89 | 2799.77 | 668.71 | 1858.2 | 443.82 | 3.1421
24 | 221.78 | 0.083 | 12.02 | 951.9 | 227.36 | 2800.39 | 668.86 | 1848.49 | 441.5 | 3.1805
25 | 223.94 | 0.08 | 12.515 | 961.93 | 229.75 | 2800.91 | 668.99 | 1838.98 | 439.23 | 3.2187
26 | 226.03 | 0.077 | 13.012 | 971.69 | 232.08 | 2801.35 | 669.09 | 1829.66 | 437.01 | 3.2567
27 | 228.06 | 0.074 | 13.509 | 981.19 | 234.35 | 2801.69 | 669.17 | 1820.5 | 434.82 | 3.2944
28 | 230.04 | 0.071 | 14.008 | 990.46 | 236.57 | 2801.96 | 669.24 | 1811.5 | 432.67 | 3.332
29 | 231.96 | 0.069 | 14.508 | 999.5 | 238.73 | 2802.15 | 669.28 | 1802.65 | 430.56 | 3.3695
30 | 233.84 | 0.067 | 15.009 | 1008.33 | 240.84 | 2802.27 | 669.31 | 1793.94 | 428.48 | 3.4069